## Read Me
Mass Save Heat Pump Qualified Products List (HPQPL) | [7 empty] | Data pulled | 2026-02-05
IMPORTANT NOTICE
1. AHRI has replaced the "Heating Capacity (H1Full) - Single or High Stage (47F), btuh" field with the "Heating Capacity (47F), btuh (Appendix M1)" field. This data update has resulted in systems that once qualified to no longer qualify. These systems will be eligible for a rebate if installed on or before March 31, 2026, but will no longer be eligible for a rebate beginning April 1, 2026. These systems are marked with "No - DS" in column B. 2. The industry is moving away from R410A refrigerants to A2L refrigerants, like R-454B and R-32, to comply with the EPA’s transition rule. Key terms to understand the transition: System: A grouping of HVAC components, otherwise known as split systems (ex: IDUs paired with ODUs). Product: A self-contained unit, otherwise known as a packaged heat pump (ex: evaporator coil, condenser, and compressor all located in one cabinet). As of January 1, 2026, the EPA ruling prohibits the installation of new residential and light commercial heat pump Systems with GWPs >700. Systems using R410 refrigerants have been removed from the Heat Pump Qualified Product List. For more information on the A2L transition, view the “Introduction to A2L Refrigerants” course on the Mass Save Heating and Cooling Learning Center. Please also independently confirm that installed system(s) do not use R410 refrigerant, to remain compliant with the EPA A2L Transition order. Please note, new residential and light commercial heat pump variable refrigerant flow Systems that are 65,000 BTU/h or greater can be installed prior to January 1, 2027. To clarify this on the Mass Save Heat Pump Qualified Product List (HPQPL), the “Commercial Air Source VRF” tab, column B “Date No Longer Eligible”, all rows will read “1/1/2027.” Additionally, self-contained heat pump Products with GWPs >700 that are fully assembled and charged at the factory can be installed prior to January 1, 2028. R410A Products are marked with a "1/1/2028" in column B “Date No Longer Eligible”.
Installation Type | Equipment Type | Equipment Capacity1 |  | Efficiency Ratings
|  | Tons | Btu/Hr | EER2 | IEER3 | COP4 @ 47°F | COP4 @ 17°F
Residential and Commercial | Air Source Heat Pumps (ASHP) | < 5.4 | < 65,000 | See ASHPs < 5.4 Tons table below
Commercial |  | ≥ 5.4 and < 11.33 | ≥ 65,000 and < 135,000 | 11.1 | 15.4 | 3.5 | 2.25
|  | ≥ 11.33 and < 20 | ≥ 135,000 and < 240,000 | 10.7 | 14.6 | 3.4 | 2.05
|  | ≥ 20 and ≤ 150 | ≥ 240,000 and ≤ 1,800,000 | 9.6 | 13 | 3.3 | 2.05
Residential | Air to Water Heat Pumps (AWHP) | See AWHP criteria listed below
Residential | Ground Source Heat Pumps (GSHP) | ENERGY STAR Certified (see tab)
Commercial | Ground Source Heat Pumps - Closed Loop (GSHP-C), GLHP | ≤ 150 | ≤ 1,800,000 | 17.1 | --- | 3.6 | ---
| Ground Source Heat Pumps - Open Loop (GSHP-O), GWHP | ≤ 150 | ≤ 1,800,000 | 21.1 | --- | 4.1 | ---
1 Btu / Hr based on AHRI rated cooling capacity @ 95°F; Tons are calculated as Btu / Hr divided by 12,000 Btu / Hr 2 Energy Efficiency Ratio 3 Integrated Energy Efficiency Ratio 4 Coefficient of Performance
Equipment Type | Equipment Capacity1 |  | Efficiency Ratings
| Tons | Btu/Hr | EER² (1230-2021) Listed "Active" | EER² (1230-2014) | IEER3 | COP4 @ 47°F | COP4 @ 17°F
Air Source Variable Refriegerant Flow Heat Pumps (VRF) | ≥ 5.4 and < 11.33 | ≥ 65,000 and < 135,000 | 10.3 | 11.1 | 18.9 | 3.4 | 2.25
| ≥ 11.33 and < 20 | ≥ 135,000 and < 240,000 | 9.9 | 10.7 | 18 | 3.25 | 2.07
| ≥ 20 and ≤ 150 | ≥ 240,000 and ≤ 1,800,000 | 9.1 | 9.6 | 16.4 | 3.25 | 2.07
1 Btu / Hr based on AHRI rated cooling capacity @ 95°F; Tons are calculated as Btu / Hr divided by 12,000 Btu / Hr 2 Energy Efficiency Ratio 3 Integrated Energy Efficiency Ratio 4 Coefficient of Performance
Air Source Heat Pumps (ASHPs) < 5.4 Tons
Equipment |  |  | Efficiency Ratings 1
|  |  | HSPF2 2 | SEER2 3 | HCR4 @5°F | COP5 @5°F
Ductless | Mini-Split | Single-Zone | 8.5 | 15.2 | 70% | 1.75
Ductless | Mini-Split | Multi-Zone
Ducted | Mini-Split | Single-Zone | 8.1 | 15.2 | 70% | 1.75
Ducted | Mini-Split | Multi-Zone
Ducted | Central | --
Single Packaged Roof Top Units (Commercial Only) |  |  | 7.2 | 15.2 | 10.6 EER2⁶
Ducted | High Velocity | -- | 7 | 12.5 | 70% | 1.5
1 Aligns with ENERGY STAR 6.1 Cold-Climate Specification, except Ducted High Velocity Heat Pumps 2 Heating Season Performance Factor 3 Seasonal Energy Efficiency Ratio 4 Heating Capacity Ratio, calculated as heating capacity at the specified temperature divided by heating capacity @ 47°F 5 Coefficient of Performance 6 Energy Efficiency Ratio
The Data Fields below are sourced directly from the AHRI Directory of Cerified Product Performance
AHRI Directory
Air Source Heat Pumps < 5.4 Tons |  |  | Air Source Heat Pumps > 5.4 Tons |  | VRF Heat Pumps |  |  | Ground Source Heat Pumps
AHRI Certified Reference Number |  |  | AHRI Certified Reference Number |  | AHRI Certified Reference Number |  |  | AHRI Certified Reference Number
Brand Name |  |  | Brand Name |  | Brand Name |  |  | Brand Name
AHRI Type |  |  | AHRI Type |  | AHRI Type |  |  | AHRI Type
Indoor Type |  |  | Outdoor Unit Model Number |  | Indoor Type |  |  | Program Type
Outdoor Unit Model Number |  |  | Indoor Unit Model Number |  | System Model Number |  |  | Outdoor Unit Model Number
Indoor Unit Model Number(s) |  |  | Cooling Capacity (95F) |  | Module Model Number 1 |  |  | Indoor Unit Model Number(s)
Furnace Model Number |  |  | EER (95F) |  | Module Model Number 2 |  |  | Full Load GLHP Cooling Capacity (Btuh)
Cooling Capacity (AFull) - Single or High Stage (95F), btuh |  |  | IEER |  | Module Model Number 3 |  |  | Full Load GLHP Cooling EER (Btuh/watt)
SEER2 |  |  | COP at 47°F |  | Cooling Capacity (95F) |  |  | Full Load GLHP Heating COP
EER2 (AFull) - Single or High Stage (95F) |  |  | Heating Capacity at 47°F |  | EER (95F) |  |  | Full Load GLHP Heating Capacity (Btuh)
HSPF2 (Region IV) |  |  | Heating Capacity at 17°F |  | IEER
Heating Capacity (H1Full) - Single or High Stage (47F), btuh |  |  | COP at 17°F |  | High COP (47F)
Heating Capacity at 5°F as calculated by M1 |  |  |  |  | High Heating Capacity (47F)
Heating COP at 5°F as calculated by M1 |  |  |  |  | Low Heating Capacity (17F)
Heating Capacity at 17°F as calculated by M1 |  |  |  |  | Low COP (17F)
Equipment Category | AHRI Types
Ducted | ·HRCU-A-CB = Split System: Heat Pump with Remote Outdoor Unit-Air-Source ·HRCU-A-C =Split System: Heat Pump with Remote Outdoor Unit with No Indoor Fan --Air Source (Ducted) ·HSP-A = Single-Package Heat Pump Air-Source ·HMSV-A-CB = Multi-Split Heat Pump (Ducted, Mixed) ·HMSR-A-CB = Multi-Split Heat Recovery Heat Pump (Ducted, Mixed)
Ductless | ·HRCU-A-CB-O =Mini-Split Heat Pump, with Remote Outdoor Unit Air-Source, Free Delivery ·HMSV-A-CB-O = Multi-Split Heat Pump, Free Delivery (Non-ducted) ·HMSR-A-CB-O = Multi-Split Heat Recovery Heat Pump, Free Delivery (Non-ducted)
Ducted High Velocity | ·SDHV-HRCU-A-CB = Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled
Air to Water Heat Pumps (Residential Only)
Criteria is as follows:
•Minimum COP of 1.7 while delivering 110°F supply water at an outside temperature of 5°F.
•Fully displacing existing hydronic heating
•Maximum 6 tons nominal capacity
Integrated Controls
Integrated controls automatically switch between a heat pump and fossil fuel heating system at a pre-set outdoor temperature.
Eligibility
For residential heat pump rebates: |  | click here
For commercial heat pump rebates |  | click here
To note, effective January 1, 2025, the Consortium for Energy Efficiency (CEE) published updates to the CEE Residential Electric HVAC and Water Heating performance requirements, which serve as the basis of eligibility for federal 25C tax credits. These credits could be subject to change in the future. For tax advice, consult a tax professional.

## High Velocity ASHPs
AHRI Certified Reference Number | Date No Longer Eligible | Equipment Type | Outdoor Unit Brand Name | AHRI Type | Outdoor Unit Model Number | Indoor Unit Brand Name | Indoor Unit Type | Indoor Unit Model Number(s) | Furnace Model Number | Cooling Capacity (AFull) - Single or High Stage (95F), btuh | SEER2 | HSPF2 (Region IV) | Heating Capacity (47F), btuh | Heating Capacity at 5°F as calculated by M1 | Heating Capacity Ratio @ 5°F | Heating COP at 5°F as calculated by M1 | EER (95F) | IEER | COP at 47°F | COP at 17°F | Refrigerant Type | Tonnage | Rebate Type
217048334 | N/A | Central HP < 5.4 tons | BOSCH | SDHV-HRCU-A-CB (Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled) | BOVA-36RTB-M20S | UNICO SYSTEM |  | M3036C*1-B***+M3036B**-EC**+TXV-3T-454 |  | 26400 | 14.1 | 7.4 | 27200 | 19400 | 71.32% | 1.55 | 0 |  |  |  | R-454B | 2.2 | Residential & Commercial
217048386 | N/A | Central HP < 5.4 tons | BOSCH | SDHV-HRCU-A-CB (Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled) | BOVA-60RTB-M20S | UNICO SYSTEM |  | M3642C*1-B***+M3642B**-EC**+TXV-3T-454 |  | 41500 | 14.2 | 7.6 | 42200 | 31000 | 73.46% | 1.65 | 0 |  |  |  | R-454B | 3.4583 | Residential & Commercial
217656828 | N/A | Central HP < 5.4 tons | HISENSE | SDHV-HRCU-A-CB (Small-duct, High-velocity Heat Pump, Split-System, Air-Cooled) | AUWR-3624P | UNICO SYSTEM |  | M3642C*1-BA***+M3642B**-EC**+TXV-4T-454 |  | 32600 | 12.75 | 7.2 | 28600 | 26000 | 90.91% | 1.84 | 0 |  |  |  | R-454B | 2.7167 | Residential & Commercial

## Air to Water HPs (AWHPs)
Last update: 2/4/2026
Manufacturer | System Type | Model Name | Model # | Nominal Capacity in Tons | COP @ A5W110* | Refrigerant**
Apollo | Mono-bloc | Apollo Air-to-Water Heat Pump | AP-EVI-DC-3.5T. | 3.5 | 2.46 | Please independently confirm
Apollo | Mono-bloc | Apollo Air-to-Water Heat Pump | AP-EVI-DC-5T. | 5 | 2.34 | Please independently confirm
Apollo | Mono-bloc | Apollo Air-to-Water Heat Pump | AP-EVI-DC-6T. | 6 | 2.34 | Please independently confirm
Arctic Heat Pumps | Mono-bloc |  | 035ZA/BE-R32 | 2.5 | 2.2 | R32
Arctic Heat Pumps | Mono-bloc |  | 050ZA/BE-R32 | 4 | 2.45 | R32
Arctic Heat Pumps | Mono-bloc |  | 060ZA/BE-R32 | 5 | 2.39 | R32
Arctic Heat Pumps | Mono-bloc |  | 030ZA/BEH2 | 4 | 2.03 | Please independently confirm
Arctic Heat Pumps | Mono-bloc |  | MAHRW030A (BEH2)-R32 | 4 | 1.84 | R32
Arctic Heat Pumps | Mono-bloc | EVI - Cold Climate | 020A | 2.5 | 2.26 | Please independently confirm
Arctic Heat Pumps | Mono-bloc | EVI - Cold Climate | 040A | 4 | 2.18 | Please independently confirm
Arctic Heat Pumps | Mono-bloc | EVI - Cold Climate | 060A | 5 | 2.26 | Please independently confirm
Chiltrix Inc. | R32 Air To Water Heat Pump | CX50 | CX50 | 4.8 | 2.18 | R32
Chiltrix Inc. | Mono-bloc | CX34 | CX34-ODU | 3 | 2 | R32
Chiltrix Inc. | Mono-bloc | CX35 | CX35 | 3.5 | 2.187 | R32
Daikin | Mono-bloc | Altherma 3 H HT | UPRA036DAVJ | 2.9 | 2.2 | R32
Daikin | Mono-bloc | Altherma 3 H HT | UPRA043DAVJ | 2.9 | 2.17 | R32
ECOER | Mono-bloc | Smart Green One | ESMA-060ADP | 5.2 | 2.04 | R32
ECOER | Mono-bloc | Smart Green One | ESBM-060GPP | 5.5 | 2.27 | R32
Ecoforest | Mono-bloc Air to Water Heat Pump | Ecoair | ecoAIR 1-7 PRO (81001/P) | 1 | 2.5 | R290 (propane)
Ecoforest | Mono-bloc Air to Water Heat Pump | Ecoair | ecoAIR 1-9 PRO (81004/P) | 1.3 | 2.31 | R290 (propane)
Ecoforest | Mono-bloc Air to Water Heat Pump | Ecoair | ecoAIR 3-12 PRO (81002/P) | 1.75 | 2.23 | R290 (propane)
Ecoforest | Mono-bloc Air to Water Heat Pump | Ecoair | ecoAIR 3-18 PRO (81005/P2) | 2.75 | 2.42 | R290 (propane)
Ecoforest | Mono-bloc Air to Water Heat Pump | Ecoair | ecoAIR EVI 4-20 (81003) | 3.79 | 2.92 | R290 (propane)
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-1H | 2 | 2.3 | CO2
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-2H | 3 | 2.3 | CO2
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-11 | 2 | 2.3 | CO2
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-12 | 2 | 2.3 | CO2
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-13 | 3 | 2.3 | CO2
Harvest Thermal | Mono-bloc CO2 | Harvest Smart Thermal Battery | PD2B-14 | 4 | 2.3 | CO2
LG | Mono-bloc | LATS AWHP | KPHTC411M | 3.41 | 2.5 | R32
LG | Mono-bloc | LATS AWHP | KPHTC481M | 4 | 2.15 | R32
LG | Mono-bloc | LATS AWHP | KPHTC551M | 4.58 | 2.38 | R32
Lochinvar | Mono-bloc | Lochinvar | RAH040 | 3.42 | 1.9 | R32
Midea | Split | M Thermal Arctic Split | MHA-V12WD2MN8-B2 | 3.5 | 2.11 | R32
Midea | Split | M Thermal Arctic Split | MHA-V14WD2MN8-B2 | 4 | 2.08 | R32
Midea | Split | M Thermal Arctic Split | MHA-V16WD2MN8-B2 | 4.5 | 2.06 | R32
Midea | Split | M Thermal Arctic Split | MHA-V16WD2MN8 / HB–A160CMGN8 | 4 | 2.1 | R32
NTI Boilers Inc. | Mono-bloc | Verta | NHP32-036 | 2.7 | 1.94 | R32
NTI Boilers Inc. | Mono-bloc | Verta | NHP32-060 | 4.7 | 2 | R32
Mitsubishi Electric | Split | ECODAN AIR TO WATER OUTDOOR UNIT | WUZ-SA24NMZ-U1 | 2 | 1.98 | R32
Mitsubishi Electric | Split | ECODAN AIR TO WATER OUTDOOR UNIT | WUZ-SA36NMZ-U1 | 3 | 1.93 | R32
Mitsubishi Electric | Split | ECODAN AIR TO WATER OUTDOOR UNIT | WUZ-SA48NMZ-U1 | 4 | 1.99 | R32
Mitsubishi Electric | Split | Ecodan Hydro Box Indoor Unit | ERSF-NM6E | Depenant on Connected ODU | Dependant on connected IDU | R32
SpacePak | Monobloc | Solstice R32 Series | CC32-18 | 1.7 | 1.54 | R32
SpacePak | Monobloc | Solstice R32 Series | CC32-40 | 2.8 | 2.83 | R32
SpacePak | Monobloc | Solstice R32 Series | CC32-60 | 4.3 | 2.39 | R32
U.S. Boiler Company, LLC | Mono-bloc | Ambient Heat Pump System (HPS) | HPS-5T60-DF | 5 | 1.9 | R32
U.S. Boiler Company, LLC | Mono-bloc | Ambient Heat Pump System (HPS) | HPS-5T60 | 5 | 1.9 | R32
Weil-McLain | Split | ECO HP | ECO HP SPLT ODU 41 | 2.62 | 2.11 | R32
Weil-McLain | Split | ECO HP | ECO HP SPLT ODU 48 | 2.76 | 2.08 | R32
Weil-McLain | Split | ECO HP | ECO HP SPLT ODU 55 | 2.79 | 2.06 | R32
Viessmann | Split | Vitocal 100-AW | AM2V 034043 | 3 | 2.2 | R32
Viessmann | Split | Vitocal 100-AW | AM2V 051078 | 4.3 | 1.9 | R32
* Equivalent value. Equipment automatically reduces outlet water temperature to 110°F when ambient conditions drop to 5°F. ** Please independently confirm that system does not use R410 refrigerant, per the EPA A2L Transition order.

## Commercial Air Source VRF
AHRI Certified Reference Number | Date No Longer Eligible | Outdoor Unit Brand Name | AHRI Type | Module Model Number 1 | Module Model Number 2 | Module Model Number 3 | Module Model Number 4 | Outdoor Unit Model Number | Indoor Type | Full Load Cooling Capacity (Btuh) | EER | IEER | Heating Capacity 47°F (Btuh) | COP 47°F | Heating Capacity 17°F (Btuh) | COP 17°F | Refrigerant Type | Tonnage
209937596 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM72TAM |  |  |  | MXZ-SM72TAM | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 22.85 | 76000 | 4.2 | 56000 | 2.67 | R-410A | 5.75
209445576 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM72TAM |  |  |  | MXZ-SM72TAM | Non-Ducted Indoor Units | 69000 | 12.3 | 24.2 | 76000 | 4.3 | 56000 | 2.7 | R-410A | 5.75
209445577 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM72TAM |  |  |  | MXZ-SM72TAM | Ducted Indoor Units | 69000 | 12 | 21.5 | 76000 | 4.1 | 56000 | 2.65 | R-410A | 5.75
209445578 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM96TAM |  |  |  | MXZ-SM96TAM | Non-Ducted Indoor Units | 92000 | 12 | 23.4 | 103000 | 4 | 76000 | 2.6 | R-410A | 7.6667
209445579 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM96TAM |  |  |  | MXZ-SM96TAM | Ducted Indoor Units | 92000 | 11.8 | 21.2 | 103000 | 3.8 | 76000 | 2.47 | R-410A | 7.6667
209937595 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM96TAM |  |  |  | MXZ-SM96TAM | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.3 | 103000 | 3.9 | 76000 | 2.53 | R-410A | 7.6667
209937594 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM120TAM |  |  |  | MXZ-SM120TAM | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.6 | 22.75 | 129000 | 3.77 | 92000 | 2.43 | R-410A | 9.5
209445580 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM120TAM |  |  |  | MXZ-SM120TAM | Non-Ducted Indoor Units | 114000 | 11.8 | 24.5 | 129000 | 3.9 | 92000 | 2.5 | R-410A | 9.5
209445573 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | MXZ-SM120TAM |  |  |  | MXZ-SM120TAM | Ducted Indoor Units | 114000 | 11.4 | 21 | 129000 | 3.65 | 92000 | 2.37 | R-410A | 9.5
209447005 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM72A1123AA |  |  |  | NTXMSM72A1123AA | Non-Ducted Indoor Units | 69000 | 12.3 | 24.2 | 76000 | 4.3 | 56000 | 2.7 | R-410A | 5.75
209447006 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM72A1123AA |  |  |  | NTXMSM72A1123AA | Ducted Indoor Units | 69000 | 12 | 21.5 | 76000 | 4.1 | 56000 | 2.65 | R-410A | 5.75
209938003 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM72A1123AA |  |  |  | NTXMSM72A1123AA | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 22.85 | 76000 | 4.2 | 56000 | 2.67 | R-410A | 5.75
209447007 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM96A1123AA |  |  |  | NTXMSM96A1123AA | Non-Ducted Indoor Units | 92000 | 12 | 23.4 | 103000 | 4 | 76000 | 2.6 | R-410A | 7.6667
209447008 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM96A1123AA |  |  |  | NTXMSM96A1123AA | Ducted Indoor Units | 92000 | 11.8 | 21.2 | 103000 | 3.8 | 76000 | 2.47 | R-410A | 7.6667
209938002 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM96A1123AA |  |  |  | NTXMSM96A1123AA | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.3 | 103000 | 3.9 | 76000 | 2.53 | R-410A | 7.6667
209938001 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM120A1123AA |  |  |  | NTXMSM120A1123AA | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.6 | 22.75 | 129000 | 3.77 | 92000 | 2.43 | R-410A | 9.5
209445574 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM120A1123AA |  |  |  | NTXMSM120A1123AA | Non-Ducted Indoor Units | 114000 | 11.8 | 24.5 | 129000 | 3.9 | 92000 | 2.5 | R-410A | 9.5
209445575 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | NTXMSM120A1123AA |  |  |  | NTXMSM120A1123AA | Ducted Indoor Units | 114000 | 11.4 | 21 | 129000 | 3.65 | 92000 | 2.37 | R-410A | 9.5
218044847 | N/A | Mitsubishi Electric | HMSV-A-CB | MXZ-SM72TL |  |  |  | MXZ-SM72TL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 23.75 | 76000 | 4.29 | 56000 | 2.76 | R-454B | 5.75
218044838 | N/A | Mitsubishi Electric | HMSV-A-CB | MXZ-SM72TL |  |  |  | MXZ-SM72TL | Non-Ducted Indoor Units | 69000 | 12.7 | 25 | 76000 | 4.38 | 56000 | 2.76 | R-454B | 5.75
218044839 | N/A | Mitsubishi Electric | HMSV-A-CB | MXZ-SM72TL |  |  |  | MXZ-SM72TL | Ducted Indoor Units | 69000 | 12.5 | 22.5 | 76000 | 4.2 | 56000 | 2.76 | R-454B | 5.75
218044840 | N/A | Mitsubishi Electric | HMSV-A-CB | MXZ-SM96TL |  |  |  | MXZ-SM96TL | Non-Ducted Indoor Units | 92000 | 12.2 | 24.2 | 103000 | 4.05 | 76000 | 2.64 | R-454B | 7.6667
218044841 | N/A | Mitsubishi Electric | HMSV-A-CB | MXZ-SM96TL |  |  |  | MXZ-SM96TL | Ducted Indoor Units | 92000 | 12.2 | 22.1 | 103000 | 3.83 | 76000 | 2.59 | R-454B | 7.6667
218044848 | N/A | Mitsubishi Electric | HMSV-A-CB | MXZ-SM96TL |  |  |  | MXZ-SM96TL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.2 | 23.15 | 103000 | 3.94 | 76000 | 2.61 | R-454B | 7.6667
218044849 | N/A | Mitsubishi Electric | HMSV-A-CB | MXZ-SM120TL |  |  |  | MXZ-SM120TL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12 | 23.6 | 123000 | 3.87 | 92000 | 2.49 | R-454B | 9.5
218044842 | N/A | Mitsubishi Electric | HMSV-A-CB | MXZ-SM120TL |  |  |  | MXZ-SM120TL | Non-Ducted Indoor Units | 114000 | 12.2 | 25.3 | 123000 | 3.94 | 92000 | 2.53 | R-454B | 9.5
218044843 | N/A | Mitsubishi Electric | HMSV-A-CB | MXZ-SM120TL |  |  |  | MXZ-SM120TL | Ducted Indoor Units | 114000 | 11.8 | 21.9 | 123000 | 3.81 | 92000 | 2.46 | R-454B | 9.5
218079204 | N/A | Mitsubishi Electric | HMSV-A-CB | PUMY-L72TBMU |  |  |  | PUMY-L72TBMU | Non-Ducted Indoor Units | 69000 | 12.7 | 25 | 76000 | 4.38 | 56000 | 2.76 | R-454B | 5.75
218079205 | N/A | Mitsubishi Electric | HMSV-A-CB | PUMY-L72TBMU |  |  |  | PUMY-L72TBMU | Ducted Indoor Units | 69000 | 12.5 | 22.5 | 76000 | 4.2 | 56000 | 2.76 | R-454B | 5.75
218079206 | N/A | Mitsubishi Electric | HMSV-A-CB | PUMY-L72TBMU |  |  |  | PUMY-L72TBMU | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 23.75 | 76000 | 4.29 | 56000 | 2.76 | R-454B | 5.75
218079207 | N/A | Mitsubishi Electric | HMSV-A-CB | PUMY-L96TBMU |  |  |  | PUMY-L96TBMU | Non-Ducted Indoor Units | 92000 | 12.2 | 24.2 | 103000 | 4.05 | 76000 | 2.64 | R-454B | 7.6667
218079208 | N/A | Mitsubishi Electric | HMSV-A-CB | PUMY-L96TBMU |  |  |  | PUMY-L96TBMU | Ducted Indoor Units | 92000 | 12.2 | 22.1 | 103000 | 3.83 | 76000 | 2.59 | R-454B | 7.6667
218079209 | N/A | Mitsubishi Electric | HMSV-A-CB | PUMY-L96TBMU |  |  |  | PUMY-L96TBMU | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.2 | 23.15 | 103000 | 3.94 | 76000 | 2.61 | R-454B | 7.6667
218079210 | N/A | Mitsubishi Electric | HMSV-A-CB | PUMY-L120TBMU |  |  |  | PUMY-L120TBMU | Non-Ducted Indoor Units | 114000 | 12.2 | 25.3 | 123000 | 3.94 | 92000 | 2.53 | R-454B | 9.5
218079211 | N/A | Mitsubishi Electric | HMSV-A-CB | PUMY-L120TBMU |  |  |  | PUMY-L120TBMU | Ducted Indoor Units | 114000 | 11.8 | 21.9 | 123000 | 3.81 | 92000 | 2.46 | R-454B | 9.5
218079212 | N/A | Mitsubishi Electric | HMSV-A-CB | PUMY-L120TBMU |  |  |  | PUMY-L120TBMU | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12 | 23.6 | 123000 | 3.87 | 92000 | 2.49 | R-454B | 9.5
6687539 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV |  |  |  | AOUA72TLBV | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.06 | 56000 | 2.53 | R-410A | 5.75
207742258 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV |  |  |  | AOUA72TLBV | Ducted Indoor Units | 69000 | 12.3 | 20 | 77000 | 3.64 | 56000 | 2.38 | R-410A | 5.75
6687541 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV |  |  |  | AOUA96TLBV | Non-Ducted Indoor Units | 92000 | 11.7 | 23.6 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
6687542 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV |  |  |  | AOUA96TLBV | Ducted Indoor Units | 92000 | 11.3 | 20.2 | 103000 | 3.6 | 73000 | 2.42 | R-410A | 7.6667
6687543 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV |  |  |  | AOUA120TLBV | Non-Ducted Indoor Units | 114000 | 11.3 | 23.8 | 129000 | 3.61 | 87000 | 2.43 | R-410A | 9.5
7850818 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV |  |  |  | AOUA72TLCV | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.06 | 56000 | 2.53 | R-410A | 5.75
7850820 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV |  |  |  | AOUA96TLCV | Non-Ducted Indoor Units | 92000 | 11.7 | 23.6 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
7850821 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV |  |  |  | AOUA96TLCV | Ducted Indoor Units | 92000 | 11.3 | 20.2 | 103000 | 3.6 | 73000 | 2.42 | R-410A | 7.6667
7850822 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV |  |  |  | AOUA120TLCV | Non-Ducted Indoor Units | 114000 | 11.3 | 23.8 | 129000 | 3.61 | 87000 | 2.43 | R-410A | 9.5
7850838 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV |  |  |  | AOUA72RLCV | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.06 | 56000 | 2.53 | R-410A | 5.75
7850840 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV |  |  |  | AOUA96RLCV | Non-Ducted Indoor Units | 92000 | 11.7 | 23.6 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
7850841 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV |  |  |  | AOUA96RLCV | Ducted Indoor Units | 92000 | 11.3 | 20.2 | 103000 | 3.6 | 73000 | 2.42 | R-410A | 7.6667
7850842 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV |  |  |  | AOUA120RLCV | Non-Ducted Indoor Units | 114000 | 11.3 | 23.8 | 129000 | 3.61 | 87000 | 2.43 | R-410A | 9.5
214825944 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C |  |  |  | TVRF-VQ72WM/C | Ducted Indoor Units | 69000 | 11.4 | 21 | 77000 | 4 | 68000 | 2.25 | R-410A | 5.75
214825941 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C |  |  |  | TVRF-VQ72WM/C | Non-Ducted Indoor Units | 69000 | 11.8 | 23.8 | 77000 | 4.4 | 68000 | 2.25 | R-410A | 5.75
214825945 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ96WM/C |  |  |  | TVRF-VQ96WM/C | Ducted Indoor Units | 92000 | 11.6 | 20.2 | 103000 | 3.9 | 78000 | 2.25 | R-410A | 7.6667
214825946 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ120WM/C |  |  |  | TVRF-VQ120WM/C | Ducted Indoor Units | 114000 | 11 | 19.7 | 129000 | 3.8 | 81000 | 2.25 | R-410A | 9.5
214825938 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHD72K/220V |  |  |  | TVRF-SHD72K/220V | Ducted Indoor Units | 69000 | 11.2 | 20.4 | 77000 | 3.68 | 66000 | 2.25 | R-410A | 5.75
214825949 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHD96K/220V |  |  |  | TVRF-SHD96K/220V | Ducted Indoor Units | 92000 | 11 | 22.2 | 103000 | 3.8 | 75000 | 2.25 | R-410A | 7.6667
214826363 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072DXVGQH |  |  |  | AM072DXVGQH | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
214826372 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072DXVGQH |  |  |  | AM072DXVGQH | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
214826403 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072DXVGQH |  |  |  | AM072DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602723 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4J |  |  |  | VPC072S4M-4J | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602775 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4J |  |  |  | VPC072S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602708 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4J |  |  |  | VPC072S4M-4J | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602710 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J |  |  |  | VPC096S4M-4J | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
216602778 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J |  |  |  | VPC096S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602724 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J |  |  |  | VPC096S4M-4J | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
214826404 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH |  |  |  | AM096DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
214826373 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH |  |  |  | AM096DXVGQH | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
214826364 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH |  |  |  | AM096DXVGQH | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
214826365 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH |  |  |  | AM120DXVGQH | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
214826374 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH |  |  |  | AM120DXVGQH | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
214826405 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH |  |  |  | AM120DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602725 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J |  |  |  | VPC120S4M-4J | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602780 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J |  |  |  | VPC120S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602711 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J |  |  |  | VPC120S4M-4J | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
214826383 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072DXVGQR |  |  |  | AM072DXVGQR | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
214826392 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072DXVGQR |  |  |  | AM072DXVGQR | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602741 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4J |  |  |  | VRC072S4M-4J | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602756 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4J |  |  |  | VRC072S4M-4J | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602758 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J |  |  |  | VRC096S4M-4J | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
216602742 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J |  |  |  | VRC096S4M-4J | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
214826393 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR |  |  |  | AM096DXVGQR | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
214826384 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR |  |  |  | AM096DXVGQR | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
214826385 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR |  |  |  | AM120DXVGQR | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
214826394 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR |  |  |  | AM120DXVGQR | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602744 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J |  |  |  | VRC120S4M-4J | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602759 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J |  |  |  | VRC120S4M-4J | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
213916335 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 10.4 | 21.8 | 77000 | 3.83 | 54000 | 2.45 | R-410A | 5.75
213916331 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Ducted Indoor Units | 69000 | 10.5 | 21.8 | 77000 | 3.62 | 54000 | 2.4 | R-410A | 5.75
213916332 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Non-Ducted Indoor Units | 69000 | 10.3 | 21.8 | 77000 | 4.04 | 54000 | 2.5 | R-410A | 5.75
213895919 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AATJ* |  |  |  | REYQ72AATJ* | Ducted Indoor Units | 69000 | 11.8 | 19 | 69000 | 3.6 | 51000 | 2.4 | R-410A | 5.75
213895937 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AATJ* |  |  |  | REYQ72AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 20 | 69000 | 3.7 | 51000 | 2.35 | R-410A | 5.75
213895897 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AATJ* |  |  |  | REYQ72AATJ* | Non-Ducted Indoor Units | 69000 | 12.2 | 21 | 69000 | 3.8 | 51000 | 2.3 | R-410A | 5.75
213895898 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AATJ* |  |  |  | REYQ96AATJ* | Non-Ducted Indoor Units | 92000 | 11.4 | 22.1 | 92000 | 3.8 | 72000 | 2.3 | R-410A | 7.6667
213895716 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AATJ* |  |  |  | REYQ96AATJ* | Ducted Indoor Units | 92000 | 11.9 | 19.3 | 92000 | 3.6 | 72000 | 2.25 | R-410A | 7.6667
213895938 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AATJ* |  |  |  | REYQ96AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.65 | 20.7 | 92000 | 3.7 | 72000 | 2.27 | R-410A | 7.6667
213896224 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AATJ* |  |  |  | REYQ120AATJ* | Non-Ducted Indoor Units | 114000 | 10.6 | 21.6 | 114000 | 3.5 | 82000 | 2.25 | R-410A | 9.5
213896246 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AATJ* |  |  |  | REYQ120AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.75 | 20.1 | 114000 | 3.5 | 82000 | 2.25 | R-410A | 9.5
213895908 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AAYD* |  |  |  | REYQ72AAYD* | Non-Ducted Indoor Units | 69000 | 12.2 | 21 | 69000 | 3.8 | 51000 | 2.3 | R-410A | 5.75
213895928 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AAYD* |  |  |  | REYQ72AAYD* | Ducted Indoor Units | 69000 | 11.8 | 19 | 69000 | 3.6 | 51000 | 2.4 | R-410A | 5.75
213895947 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72AAYD* |  |  |  | REYQ72AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 20 | 69000 | 3.7 | 51000 | 2.35 | R-410A | 5.75
213895948 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AAYD* |  |  |  | REYQ96AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.65 | 20.7 | 92000 | 3.7 | 72000 | 2.27 | R-410A | 7.6667
213895718 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AAYD* |  |  |  | REYQ96AAYD* | Ducted Indoor Units | 92000 | 11.9 | 19.3 | 92000 | 3.6 | 72000 | 2.25 | R-410A | 7.6667
213895909 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96AAYD* |  |  |  | REYQ96AAYD* | Non-Ducted Indoor Units | 92000 | 11.4 | 22.1 | 92000 | 3.8 | 72000 | 2.3 | R-410A | 7.6667
213896254 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AAYD* |  |  |  | REYQ120AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.75 | 20.1 | 114000 | 3.5 | 82000 | 2.25 | R-410A | 9.5
213896228 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AAYD* |  |  |  | REYQ120AAYD* | Non-Ducted Indoor Units | 114000 | 10.6 | 21.6 | 114000 | 3.5 | 82000 | 2.25 | R-410A | 9.5
213893987 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGFH |  |  |  | AM072BXVGFH | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
213893881 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGFH |  |  |  | AM072BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
213893925 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGFH |  |  |  | AM072BXVGFH | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602343 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4Y |  |  |  | VPC072S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602443 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4Y |  |  |  | VPC072S4M-4Y | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602547 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4Y |  |  |  | VPC072S4M-4Y | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602450 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y |  |  |  | VPC096S4M-4Y | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
216602354 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y |  |  |  | VPC096S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602337 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y |  |  |  | VPC096S4M-4Y | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
213893929 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH |  |  |  | AM096BXVGFH | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893877 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH |  |  |  | AM096BXVGFH | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
213893885 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH |  |  |  | AM096BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893991 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH |  |  |  | AM120BXVGFH | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
213893889 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH |  |  |  | AM120BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
213893933 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH |  |  |  | AM120BXVGFH | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602362 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y |  |  |  | VPC120S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602457 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y |  |  |  | VPC120S4M-4Y | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602553 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y |  |  |  | VPC120S4M-4Y | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
213893927 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGJH |  |  |  | AM072BXVGJH | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
213893883 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGJH |  |  |  | AM072BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
213893989 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVGJH |  |  |  | AM072BXVGJH | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602550 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4G |  |  |  | VPC072S4M-4G | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602447 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4G |  |  |  | VPC072S4M-4G | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602349 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072S4M-4G |  |  |  | VPC072S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602357 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G |  |  |  | VPC096S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602340 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G |  |  |  | VPC096S4M-4G | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
216602454 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G |  |  |  | VPC096S4M-4G | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893879 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH |  |  |  | AM096BXVGJH | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
213893887 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH |  |  |  | AM096BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893931 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH |  |  |  | AM096BXVGJH | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893935 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH |  |  |  | AM120BXVGJH | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
213893891 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH |  |  |  | AM120BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
213893993 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH |  |  |  | AM120BXVGJH | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602557 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G |  |  |  | VPC120S4M-4G | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602366 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G |  |  |  | VPC120S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602461 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G |  |  |  | VPC120S4M-4G | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
213893926 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGFR |  |  |  | AM072BXVGFR | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
213893882 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGFR |  |  |  | AM072BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
213893988 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGFR |  |  |  | AM072BXVGFR | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602549 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4Y |  |  |  | VRC072S4M-4Y | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602446 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4Y |  |  |  | VRC072S4M-4Y | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602795 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4Y |  |  |  | VRC072S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602346 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4Y |  |  |  | VRC072S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
214826411 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGFR |  |  |  | AM072DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
214826412 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR |  |  |  | AM096DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602356 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y |  |  |  | VRC096S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602338 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y |  |  |  | VRC096S4M-4Y | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
216602797 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y |  |  |  | VRC096S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602452 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y |  |  |  | VRC096S4M-4Y | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893878 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR |  |  |  | AM096BXVGFR | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
213893886 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR |  |  |  | AM096BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893930 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR |  |  |  | AM096BXVGFR | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893934 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR |  |  |  | AM120BXVGFR | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
213893890 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR |  |  |  | AM120BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
213893992 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR |  |  |  | AM120BXVGFR | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602555 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y |  |  |  | VRC120S4M-4Y | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602364 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y |  |  |  | VRC120S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602459 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y |  |  |  | VRC120S4M-4Y | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
216602799 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y |  |  |  | VRC120S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
214826413 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR |  |  |  | AM120DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
213893928 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGJR |  |  |  | AM072BXVGJR | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
213893884 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGJR |  |  |  | AM072BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
213893990 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVGJR |  |  |  | AM072BXVGJR | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602552 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4G |  |  |  | VRC072S4M-4G | Non-Ducted Indoor Units | 69000 | 12.2 | 28 | 77000 | 3.93 | 51000 | 2.5 | R-410A | 5.75
216602449 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4G |  |  |  | VRC072S4M-4G | Ducted Indoor Units | 69000 | 11.5 | 23 | 77000 | 3.8 | 51000 | 2.55 | R-410A | 5.75
216602351 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072S4M-4G |  |  |  | VRC072S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 25.5 | 77000 | 3.86 | 51000 | 2.52 | R-410A | 5.75
216602360 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G |  |  |  | VRC096S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
216602342 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G |  |  |  | VRC096S4M-4G | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
216602455 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G |  |  |  | VRC096S4M-4G | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893880 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR |  |  |  | AM096BXVGJR | Non-Ducted Indoor Units | 92000 | 13.1 | 27.9 | 103000 | 4.13 | 67000 | 2.82 | R-410A | 7.6667
213893888 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR |  |  |  | AM096BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 26 | 103000 | 3.98 | 67000 | 2.77 | R-410A | 7.6667
213893932 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR |  |  |  | AM096BXVGJR | Ducted Indoor Units | 92000 | 12.4 | 24.1 | 103000 | 3.83 | 67000 | 2.73 | R-410A | 7.6667
213893936 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR |  |  |  | AM120BXVGJR | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
213893892 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR |  |  |  | AM120BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
213893994 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR |  |  |  | AM120BXVGJR | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602558 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G |  |  |  | VRC120S4M-4G | Non-Ducted Indoor Units | 114000 | 11.8 | 25.3 | 129000 | 3.85 | 84000 | 2.81 | R-410A | 9.5
216602369 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G |  |  |  | VRC120S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.9 | 23.95 | 129000 | 3.82 | 84000 | 2.8 | R-410A | 9.5
216602462 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G |  |  |  | VRC120S4M-4G | Ducted Indoor Units | 114000 | 12 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-410A | 9.5
208812532 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULBV5 |  |  |  | AOUA72ULBV5 | Ducted Indoor Units | 69000 | 12.3 | 21.2 | 77000 | 3.77 | 56000 | 2.45 | R-410A | 5.75
208811482 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULBV5 |  |  |  | AOUA72ULBV5 | Non-Ducted Indoor Units | 69000 | 14.9 | 29 | 77000 | 4.42 | 56000 | 2.65 | R-410A | 5.75
208811483 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULBV5 |  |  |  | AOUA96ULBV5 | Non-Ducted Indoor Units | 92000 | 13.2 | 28 | 103000 | 4 | 73000 | 2.52 | R-410A | 7.6667
208812533 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULBV5 |  |  |  | AOUA96ULBV5 | Ducted Indoor Units | 92000 | 11.7 | 19.9 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
208812534 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 |  |  |  | AOUA120ULBV5 | Ducted Indoor Units | 115000 | 11.3 | 19.8 | 129000 | 3.65 | 87000 | 2.43 | R-410A | 9.5833
208811484 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 |  |  |  | AOUA120ULBV5 | Non-Ducted Indoor Units | 115000 | 13.5 | 28.4 | 129000 | 3.69 | 87000 | 2.43 | R-410A | 9.5833
208812537 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULCV5 |  |  |  | AOUA72ULCV5 | Ducted Indoor Units | 69000 | 12.3 | 21.2 | 77000 | 3.77 | 56000 | 2.45 | R-410A | 5.75
208811487 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULCV5 |  |  |  | AOUA72ULCV5 | Non-Ducted Indoor Units | 69000 | 14.9 | 29 | 77000 | 4.42 | 56000 | 2.65 | R-410A | 5.75
208811488 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULCV5 |  |  |  | AOUA96ULCV5 | Non-Ducted Indoor Units | 92000 | 13.2 | 28 | 103000 | 4 | 73000 | 2.52 | R-410A | 7.6667
208812538 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULCV5 |  |  |  | AOUA96ULCV5 | Ducted Indoor Units | 92000 | 11.7 | 19.9 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
208812539 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 |  |  |  | AOUA120ULCV5 | Ducted Indoor Units | 115000 | 11.3 | 19.8 | 129000 | 3.65 | 87000 | 2.43 | R-410A | 9.5833
208811489 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 |  |  |  | AOUA120ULCV5 | Non-Ducted Indoor Units | 115000 | 13.5 | 28.4 | 129000 | 3.69 | 87000 | 2.43 | R-410A | 9.5833
213896679 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBTJ* |  |  |  | REYQ72XBTJ* | Non-Ducted Indoor Units | 69000 | 12.2 | 19.4 | 69000 | 3.82 | 52000 | 2.36 | R-410A | 5.75
213896710 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBTJ* |  |  |  | REYQ72XBTJ* | Ducted Indoor Units | 69000 | 12.8 | 18.9 | 69000 | 3.6 | 52000 | 2.25 | R-410A | 5.75
213896728 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBTJ* |  |  |  | REYQ72XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 19.15 | 69000 | 3.71 | 52000 | 2.3 | R-410A | 5.75
213896729 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* |  |  |  | REYQ96XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 19.35 | 92000 | 3.62 | 64000 | 2.29 | R-410A | 7.6667
213896680 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* |  |  |  | REYQ96XBTJ* | Non-Ducted Indoor Units | 92000 | 11.4 | 20.4 | 92000 | 3.75 | 64000 | 2.32 | R-410A | 7.6667
213896690 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* |  |  |  | REYQ120XBTJ* | Non-Ducted Indoor Units | 114000 | 10.6 | 20 | 114000 | 3.48 | 70000 | 2.25 | R-410A | 9.5
213896773 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* |  |  |  | REYQ120XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.7 | 18.9 | 114000 | 3.47 | 70000 | 2.25 | R-410A | 9.5
213896734 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYD* |  |  |  | REYQ72XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 19.15 | 69000 | 3.71 | 52000 | 2.3 | R-410A | 5.75
213896716 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYD* |  |  |  | REYQ72XBYD* | Ducted Indoor Units | 69000 | 12.8 | 18.9 | 69000 | 3.6 | 52000 | 2.25 | R-410A | 5.75
213896696 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYD* |  |  |  | REYQ72XBYD* | Non-Ducted Indoor Units | 69000 | 12.2 | 19.4 | 69000 | 3.82 | 52000 | 2.36 | R-410A | 5.75
213896697 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* |  |  |  | REYQ96XBYD* | Non-Ducted Indoor Units | 92000 | 11.4 | 20.4 | 92000 | 3.75 | 64000 | 2.32 | R-410A | 7.6667
213896735 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* |  |  |  | REYQ96XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 19.35 | 92000 | 3.62 | 64000 | 2.29 | R-410A | 7.6667
213896817 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* |  |  |  | REYQ120XBYD* | Non-Ducted Indoor Units | 114000 | 10.6 | 20 | 114000 | 3.48 | 70000 | 2.25 | R-410A | 9.5
213896837 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* |  |  |  | REYQ120XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.7 | 18.9 | 114000 | 3.47 | 70000 | 2.25 | R-410A | 9.5
213896703 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYC* |  |  |  | REYQ72XBYC* | Non-Ducted Indoor Units | 69000 | 12.2 | 19.4 | 69000 | 3.82 | 52000 | 2.36 | R-410A | 5.75
213896722 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYC* |  |  |  | REYQ72XBYC* | Ducted Indoor Units | 69000 | 12.8 | 18.9 | 69000 | 3.6 | 52000 | 2.25 | R-410A | 5.75
213896740 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XBYC* |  |  |  | REYQ72XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 19.15 | 69000 | 3.71 | 52000 | 2.3 | R-410A | 5.75
213896741 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* |  |  |  | REYQ96XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 19.35 | 92000 | 3.62 | 64000 | 2.29 | R-410A | 7.6667
213896704 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* |  |  |  | REYQ96XBYC* | Non-Ducted Indoor Units | 92000 | 11.4 | 20.4 | 92000 | 3.75 | 64000 | 2.32 | R-410A | 7.6667
213896821 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* |  |  |  | REYQ120XBYC* | Non-Ducted Indoor Units | 114000 | 10.6 | 20 | 114000 | 3.48 | 70000 | 2.25 | R-410A | 9.5
213896841 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* |  |  |  | REYQ120XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.7 | 18.9 | 114000 | 3.47 | 70000 | 2.25 | R-410A | 9.5
213896746 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XBYC* |  |  |  | RXYQ72XBYC* | Non-Ducted Indoor Units | 69000 | 11.5 | 18.9 | 69000 | 3.82 | 52000 | 2.36 | R-410A | 5.75
213896805 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XBYC* |  |  |  | RXYQ96XBYC* | Non-Ducted Indoor Units | 92000 | 10.5 | 19.8 | 92000 | 3.75 | 64000 | 2.32 | R-410A | 7.6667
213896806 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* |  |  |  | RXYQ120XBYC* | Non-Ducted Indoor Units | 114000 | 10.3 | 19.3 | 114000 | 3.48 | 70000 | 2.25 | R-410A | 9.5
213896871 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TBTJ* |  |  |  | RXLQ72TBTJ* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
213896883 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TBYD* |  |  |  | RXLQ72TBYD* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
213896887 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TBYC* |  |  |  | RXLQ72TBYC* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
213896876 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TBTJ* |  |  |  | RELQ72TBTJ* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
213896909 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TBYD* |  |  |  | RELQ72TBYD* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
213896915 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TBYC* |  |  |  | RELQ72TBYC* | Non-Ducted Indoor Units | 69000 | 11.5 | 19 | 69000 | 3.78 | 52000 | 2.28 | R-410A | 5.75
214289936 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ072ME2CA* |  |  |  | MVHQ072ME2CA* | Ducted Indoor Units | 69000 | 12 | 20.5 | 77000 | 3.5 | 53000 | 2.4 | R-410A | 5.75
214289937 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ072ME2CA* |  |  |  | MVHQ072ME2CA* | Non-Ducted Indoor Units | 69000 | 12.6 | 23.6 | 77000 | 3.5 | 53000 | 2.4 | R-410A | 5.75
214289957 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ096ME2CA* |  |  |  | MVHQ096ME2CA* | Ducted Indoor Units | 91000 | 12.2 | 21.8 | 103000 | 3.5 | 72000 | 2.4 | R-410A | 7.5833
214289958 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ096ME2CA* |  |  |  | MVHQ096ME2CA* | Non-Ducted Indoor Units | 91000 | 11.9 | 23.1 | 103000 | 3.5 | 72000 | 2.4 | R-410A | 7.5833
214289972 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME2CA* |  |  |  | MVHQ120ME2CA* | Ducted Indoor Units | 115000 | 11.2 | 21.6 | 129000 | 3.5 | 84000 | 2.5 | R-410A | 9.5833
214289973 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME2CA* |  |  |  | MVHQ120ME2CA* | Non-Ducted Indoor Units | 115000 | 11.6 | 23 | 129000 | 3.5 | 84000 | 2.5 | R-410A | 9.5833
214289938 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ072ME4CA* |  |  |  | MVHQ072ME4CA* | Ducted Indoor Units | 69000 | 12 | 20.5 | 77000 | 3.5 | 53000 | 2.4 | R-410A | 5.75
214289939 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ072ME4CA* |  |  |  | MVHQ072ME4CA* | Non-Ducted Indoor Units | 69000 | 12.6 | 23.6 | 77000 | 3.5 | 53000 | 2.4 | R-410A | 5.75
214289959 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ096ME4CA* |  |  |  | MVHQ096ME4CA* | Ducted Indoor Units | 91000 | 12.2 | 21.8 | 103000 | 3.5 | 72000 | 2.4 | R-410A | 7.5833
214289960 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ096ME4CA* |  |  |  | MVHQ096ME4CA* | Non-Ducted Indoor Units | 91000 | 11.9 | 23.1 | 103000 | 3.5 | 72000 | 2.4 | R-410A | 7.5833
214289974 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME4CA* |  |  |  | MVHQ120ME4CA* | Ducted Indoor Units | 115000 | 11.2 | 21.6 | 129000 | 3.5 | 84000 | 2.5 | R-410A | 9.5833
214289975 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME4CA* |  |  |  | MVHQ120ME4CA* | Non-Ducted Indoor Units | 115000 | 11.6 | 23 | 129000 | 3.5 | 84000 | 2.5 | R-410A | 9.5833
214296004 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B33CW |  |  |  | HVAHR120B33CW | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
217189682 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR120B33CW |  |  |  | HVAHR120B33CW* | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
214296014 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B43CW |  |  |  | HVAHR120B43CW | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
217189692 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR120B43CW |  |  |  | HVAHR120B43CW* | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
217189702 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR120B53CW |  |  |  | HVAHR120B53CW* | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
215828403 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B53CW |  |  |  | HVAHR120B53CW | Non-Ducted Indoor Units | 115000 | 11.9 | 19.7 | 129000 | 4 | 92000 | 2.45 | R-410A | 9.5833
217729292 | N/A | LG | HMSR-A-CB | ZRUM072BTE6 |  |  |  | ZRUM072BTE6 | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.05 | 51000 | 2.75 | R-32 | 5.75
217729293 | N/A | LG | HMSR-A-CB | ZRUM072BTE6 |  |  |  | ZRUM072BTE6 | Ducted Indoor Units | 69000 | 11.9 | 19.7 | 77000 | 3.85 | 51000 | 2.65 | R-32 | 5.75
217729759 | N/A | LG | HMSR-A-CB | ZRUM072BTE6 |  |  |  | ZRUM072BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 21.9 | 77000 | 3.95 | 51000 | 2.7 | R-32 | 5.75
217729760 | N/A | LG | HMSR-A-CB | ZRUM096BTE6 |  |  |  | ZRUM096BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 23.3 | 103000 | 4.17 | 67000 | 2.85 | R-32 | 7.6667
217729294 | N/A | LG | HMSR-A-CB | ZRUM096BTE6 |  |  |  | ZRUM096BTE6 | Non-Ducted Indoor Units | 92000 | 13.3 | 27.6 | 103000 | 4.45 | 67000 | 2.95 | R-32 | 7.6667
217729295 | N/A | LG | HMSR-A-CB | ZRUM096BTE6 |  |  |  | ZRUM096BTE6 | Ducted Indoor Units | 92000 | 11 | 19 | 103000 | 3.9 | 67000 | 2.75 | R-32 | 7.6667
217729296 | N/A | LG | HMSR-A-CB | ZRUM121BTE6 |  |  |  | ZRUM121BTE6 | Non-Ducted Indoor Units | 114000 | 12.1 | 25.9 | 129000 | 4.13 | 84000 | 2.9 | R-32 | 9.5
217729761 | N/A | LG | HMSR-A-CB | ZRUM121BTE6 |  |  |  | ZRUM121BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.15 | 22.45 | 129000 | 3.88 | 84000 | 2.77 | R-32 | 9.5
217729780 | N/A | LG | HMSR-A-CB | ZRUM072DTE6 |  |  |  | ZRUM072DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 21.9 | 77000 | 3.95 | 51000 | 2.7 | R-32 | 5.75
217729298 | N/A | LG | HMSR-A-CB | ZRUM072DTE6 |  |  |  | ZRUM072DTE6 | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.05 | 51000 | 2.75 | R-32 | 5.75
217729299 | N/A | LG | HMSR-A-CB | ZRUM072DTE6 |  |  |  | ZRUM072DTE6 | Ducted Indoor Units | 69000 | 11.9 | 19.7 | 77000 | 3.85 | 51000 | 2.65 | R-32 | 5.75
217729300 | N/A | LG | HMSR-A-CB | ZRUM096DTE6 |  |  |  | ZRUM096DTE6 | Non-Ducted Indoor Units | 92000 | 13.3 | 27.6 | 103000 | 4.45 | 67000 | 2.95 | R-32 | 7.6667
217729301 | N/A | LG | HMSR-A-CB | ZRUM096DTE6 |  |  |  | ZRUM096DTE6 | Ducted Indoor Units | 92000 | 11 | 19 | 103000 | 3.9 | 67000 | 2.75 | R-32 | 7.6667
217729781 | N/A | LG | HMSR-A-CB | ZRUM096DTE6 |  |  |  | ZRUM096DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 23.3 | 103000 | 4.17 | 67000 | 2.85 | R-32 | 7.6667
217729782 | N/A | LG | HMSR-A-CB | ZRUM121DTE6 |  |  |  | ZRUM121DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.15 | 22.45 | 129000 | 3.88 | 84000 | 2.77 | R-32 | 9.5
217729302 | N/A | LG | HMSR-A-CB | ZRUM121DTE6 |  |  |  | ZRUM121DTE6 | Non-Ducted Indoor Units | 114000 | 12.1 | 25.9 | 129000 | 4.13 | 84000 | 2.9 | R-32 | 9.5
217734265 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT6P-UL |  |  |  | MMY-MUB0721FT6P-UL | Non-Ducted Indoor Units | 69000 | 12 | 24.2 | 77000 | 4.55 | 56000 | 2.8 | R-454B | 5.75
217734323 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT6P-UL |  |  |  | MMY-MUB0721FT6P-UL | Ducted Indoor Units | 69000 | 12 | 22 | 77000 | 4.18 | 56000 | 2.7 | R-454B | 5.75
217734380 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT6P-UL |  |  |  | MMY-MUB0721FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 23.1 | 77000 | 4.36 | 56000 | 2.75 | R-454B | 5.75
217734382 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL |  |  |  | MMY-MUB0961FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11 | 22.3 | 103000 | 4.16 | 74000 | 2.6 | R-454B | 7.6667
217734325 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL |  |  |  | MMY-MUB0961FT6P-UL | Ducted Indoor Units | 92000 | 11.1 | 20.7 | 103000 | 3.88 | 74000 | 2.6 | R-454B | 7.6667
217734266 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL |  |  |  | MMY-MUB0961FT6P-UL | Non-Ducted Indoor Units | 92000 | 10.9 | 23.9 | 103000 | 4.45 | 74000 | 2.6 | R-454B | 7.6667
217734267 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT6P-UL |  |  |  | MMY-MUB1201FT6P-UL | Non-Ducted Indoor Units | 115000 | 11.5 | 23.3 | 129000 | 4.2 | 92000 | 2.68 | R-454B | 9.5833
217734327 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT6P-UL |  |  |  | MMY-MUB1201FT6P-UL | Ducted Indoor Units | 115000 | 11.6 | 21.7 | 129000 | 3.84 | 92000 | 2.5 | R-454B | 9.5833
217734384 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT6P-UL |  |  |  | MMY-MUB1201FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.55 | 22.5 | 129000 | 4.02 | 92000 | 2.59 | R-454B | 9.5833
217734418 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL |  |  |  | MMY-MUB072H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 23.1 | 77000 | 4.36 | 64000 | 2.6 | R-454B | 5.75
217734307 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL |  |  |  | MMY-MUB072H1FT6PUL | Non-Ducted Indoor Units | 69000 | 12 | 24.2 | 77000 | 4.55 | 64000 | 2.6 | R-454B | 5.75
217734361 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL |  |  |  | MMY-MUB072H1FT6PUL | Ducted Indoor Units | 69000 | 12 | 22 | 77000 | 4.18 | 64000 | 2.6 | R-454B | 5.75
217734363 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL |  |  |  | MMY-MUB096H1FT6PUL | Ducted Indoor Units | 92000 | 12.1 | 21.7 | 103000 | 4.1 | 86000 | 2.69 | R-454B | 7.6667
217734309 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL |  |  |  | MMY-MUB096H1FT6PUL | Non-Ducted Indoor Units | 92000 | 11.8 | 24.3 | 103000 | 4.8 | 86000 | 2.9 | R-454B | 7.6667
217734420 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL |  |  |  | MMY-MUB096H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.95 | 23 | 103000 | 4.45 | 86000 | 2.79 | R-454B | 7.6667
217734422 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL |  |  |  | MMY-MUB120H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.25 | 22.9 | 129000 | 4.17 | 110000 | 2.62 | R-454B | 9.5833
217734311 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL |  |  |  | MMY-MUB120H1FT6PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24 | 129000 | 4.4 | 110000 | 2.7 | R-454B | 9.5833
217734365 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL |  |  |  | MMY-MUB120H1FT6PUL | Ducted Indoor Units | 115000 | 12.1 | 21.8 | 129000 | 3.95 | 110000 | 2.55 | R-454B | 9.5833
217734324 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT9P-UL |  |  |  | MMY-MUB0721FT9P-UL | Ducted Indoor Units | 69000 | 12 | 22 | 77000 | 4.18 | 56000 | 2.7 | R-454B | 5.75
217734288 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT9P-UL |  |  |  | MMY-MUB0721FT9P-UL | Non-Ducted Indoor Units | 69000 | 12 | 24.2 | 77000 | 4.55 | 56000 | 2.8 | R-454B | 5.75
217734381 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT9P-UL |  |  |  | MMY-MUB0721FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 23.1 | 77000 | 4.36 | 56000 | 2.75 | R-454B | 5.75
217734383 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL |  |  |  | MMY-MUB0961FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11 | 22.3 | 103000 | 4.16 | 74000 | 2.6 | R-454B | 7.6667
217734289 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL |  |  |  | MMY-MUB0961FT9P-UL | Non-Ducted Indoor Units | 92000 | 10.9 | 23.9 | 103000 | 4.45 | 74000 | 2.6 | R-454B | 7.6667
217734326 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL |  |  |  | MMY-MUB0961FT9P-UL | Ducted Indoor Units | 92000 | 11.1 | 20.7 | 103000 | 3.88 | 74000 | 2.6 | R-454B | 7.6667
217734328 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT9P-UL |  |  |  | MMY-MUB1201FT9P-UL | Ducted Indoor Units | 115000 | 11.6 | 21.7 | 129000 | 3.84 | 92000 | 2.5 | R-454B | 9.5833
217734290 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT9P-UL |  |  |  | MMY-MUB1201FT9P-UL | Non-Ducted Indoor Units | 115000 | 11.5 | 23.3 | 129000 | 4.2 | 92000 | 2.68 | R-454B | 9.5833
217734385 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1201FT9P-UL |  |  |  | MMY-MUB1201FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.55 | 22.5 | 129000 | 4.02 | 92000 | 2.59 | R-454B | 9.5833
217734419 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL |  |  |  | MMY-MUB072H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 23.1 | 77000 | 4.36 | 64000 | 2.6 | R-454B | 5.75
217734308 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL |  |  |  | MMY-MUB072H1FT9PUL | Non-Ducted Indoor Units | 69000 | 12 | 24.2 | 77000 | 4.55 | 64000 | 2.6 | R-454B | 5.75
217734362 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL |  |  |  | MMY-MUB072H1FT9PUL | Ducted Indoor Units | 69000 | 12 | 22 | 77000 | 4.18 | 64000 | 2.6 | R-454B | 5.75
217734364 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL |  |  |  | MMY-MUB096H1FT9PUL | Ducted Indoor Units | 92000 | 12.1 | 21.7 | 103000 | 4.1 | 86000 | 2.69 | R-454B | 7.6667
217734310 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL |  |  |  | MMY-MUB096H1FT9PUL | Non-Ducted Indoor Units | 92000 | 11.8 | 24.3 | 103000 | 4.8 | 86000 | 2.9 | R-454B | 7.6667
217734421 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL |  |  |  | MMY-MUB096H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.95 | 23 | 103000 | 4.45 | 86000 | 2.79 | R-454B | 7.6667
217734423 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL |  |  |  | MMY-MUB120H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.25 | 22.9 | 129000 | 4.17 | 110000 | 2.62 | R-454B | 9.5833
217734312 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL |  |  |  | MMY-MUB120H1FT9PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24 | 129000 | 4.4 | 110000 | 2.7 | R-454B | 9.5833
217734366 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL |  |  |  | MMY-MUB120H1FT9PUL | Ducted Indoor Units | 115000 | 12.1 | 21.8 | 129000 | 3.95 | 110000 | 2.55 | R-454B | 9.5833
217734975 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT6P-UL |  |  |  | MMY-MUB0721HT6P-UL | Ducted Indoor Units | 69000 | 11.9 | 22 | 77000 | 4.18 | 56000 | 2.7 | R-454B | 5.75
217734976 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT6P-UL |  |  |  | MMY-MUB0721HT6P-UL | Non-Ducted Indoor Units | 69000 | 11.8 | 24.2 | 77000 | 4.55 | 56000 | 2.8 | R-454B | 5.75
217735082 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT6P-UL |  |  |  | MMY-MUB0721HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 23.1 | 77000 | 4.36 | 56000 | 2.75 | R-454B | 5.75
217735086 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL |  |  |  | MMY-MUB0961HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.9 | 22.3 | 103000 | 4.16 | 74000 | 2.6 | R-454B | 7.6667
217734983 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL |  |  |  | MMY-MUB0961HT6P-UL | Ducted Indoor Units | 92000 | 11.1 | 20.7 | 103000 | 3.88 | 74000 | 2.6 | R-454B | 7.6667
217734984 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL |  |  |  | MMY-MUB0961HT6P-UL | Non-Ducted Indoor Units | 92000 | 10.7 | 23.9 | 103000 | 4.45 | 74000 | 2.6 | R-454B | 7.6667
217734991 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT6P-UL |  |  |  | MMY-MUB1201HT6P-UL | Ducted Indoor Units | 115000 | 11.5 | 21.7 | 129000 | 3.84 | 92000 | 2.5 | R-454B | 9.5833
217734992 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT6P-UL |  |  |  | MMY-MUB1201HT6P-UL | Non-Ducted Indoor Units | 115000 | 11.4 | 23 | 129000 | 4.2 | 92000 | 2.68 | R-454B | 9.5833
217735090 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT6P-UL |  |  |  | MMY-MUB1201HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.45 | 22.35 | 129000 | 4.02 | 92000 | 2.59 | R-454B | 9.5833
217735084 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL |  |  |  | MMY-MUB072H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 23.1 | 77000 | 4.36 | 64000 | 2.6 | R-454B | 5.75
217734979 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL |  |  |  | MMY-MUB072H1HT6PUL | Ducted Indoor Units | 69000 | 11.9 | 22 | 77000 | 4.18 | 64000 | 2.6 | R-454B | 5.75
217734980 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL |  |  |  | MMY-MUB072H1HT6PUL | Non-Ducted Indoor Units | 69000 | 11.8 | 24.2 | 77000 | 4.55 | 64000 | 2.6 | R-454B | 5.75
217734987 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL |  |  |  | MMY-MUB096H1HT6PUL | Ducted Indoor Units | 92000 | 12.1 | 21.7 | 103000 | 4.1 | 86000 | 2.69 | R-454B | 7.6667
217734988 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL |  |  |  | MMY-MUB096H1HT6PUL | Non-Ducted Indoor Units | 92000 | 11.7 | 24.2 | 103000 | 4.8 | 86000 | 2.9 | R-454B | 7.6667
217735088 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL |  |  |  | MMY-MUB096H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.95 | 103000 | 4.45 | 86000 | 2.79 | R-454B | 7.6667
217735092 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL |  |  |  | MMY-MUB120H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.15 | 22.85 | 129000 | 4.17 | 110000 | 2.62 | R-454B | 9.5833
217734995 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL |  |  |  | MMY-MUB120H1HT6PUL | Ducted Indoor Units | 115000 | 11.9 | 21.7 | 129000 | 3.95 | 110000 | 2.55 | R-454B | 9.5833
217734996 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL |  |  |  | MMY-MUB120H1HT6PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24 | 129000 | 4.4 | 110000 | 2.7 | R-454B | 9.5833
217734977 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT9P-UL |  |  |  | MMY-MUB0721HT9P-UL | Ducted Indoor Units | 69000 | 11.9 | 22 | 77000 | 4.18 | 56000 | 2.7 | R-454B | 5.75
217734978 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT9P-UL |  |  |  | MMY-MUB0721HT9P-UL | Non-Ducted Indoor Units | 69000 | 11.8 | 24.2 | 77000 | 4.55 | 56000 | 2.8 | R-454B | 5.75
217735083 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0721HT9P-UL |  |  |  | MMY-MUB0721HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 23.1 | 77000 | 4.36 | 56000 | 2.75 | R-454B | 5.75
217735087 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL |  |  |  | MMY-MUB0961HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.9 | 22.3 | 103000 | 4.16 | 74000 | 2.6 | R-454B | 7.6667
217734985 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL |  |  |  | MMY-MUB0961HT9P-UL | Ducted Indoor Units | 92000 | 11.1 | 20.7 | 103000 | 3.88 | 74000 | 2.6 | R-454B | 7.6667
217734986 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL |  |  |  | MMY-MUB0961HT9P-UL | Non-Ducted Indoor Units | 92000 | 10.7 | 23.9 | 103000 | 4.45 | 74000 | 2.6 | R-454B | 7.6667
217734993 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT9P-UL |  |  |  | MMY-MUB1201HT9P-UL | Ducted Indoor Units | 115000 | 11.5 | 21.7 | 129000 | 3.84 | 92000 | 2.5 | R-454B | 9.5833
217734994 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT9P-UL |  |  |  | MMY-MUB1201HT9P-UL | Non-Ducted Indoor Units | 115000 | 11.4 | 23 | 129000 | 4.2 | 92000 | 2.68 | R-454B | 9.5833
217735091 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1201HT9P-UL |  |  |  | MMY-MUB1201HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.45 | 22.35 | 129000 | 4.02 | 92000 | 2.59 | R-454B | 9.5833
217735085 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL |  |  |  | MMY-MUB072H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 23.1 | 77000 | 4.36 | 64000 | 2.6 | R-454B | 5.75
217734981 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL |  |  |  | MMY-MUB072H1HT9PUL | Ducted Indoor Units | 69000 | 11.9 | 22 | 77000 | 4.18 | 64000 | 2.6 | R-454B | 5.75
217734982 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL |  |  |  | MMY-MUB072H1HT9PUL | Non-Ducted Indoor Units | 69000 | 11.8 | 24.2 | 77000 | 4.55 | 64000 | 2.6 | R-454B | 5.75
217734989 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL |  |  |  | MMY-MUB096H1HT9PUL | Ducted Indoor Units | 92000 | 12.1 | 21.7 | 103000 | 4.1 | 86000 | 2.69 | R-454B | 7.6667
217734990 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL |  |  |  | MMY-MUB096H1HT9PUL | Non-Ducted Indoor Units | 92000 | 11.7 | 24.2 | 103000 | 4.8 | 86000 | 2.9 | R-454B | 7.6667
217735089 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL |  |  |  | MMY-MUB096H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.95 | 103000 | 4.45 | 86000 | 2.79 | R-454B | 7.6667
217735093 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL |  |  |  | MMY-MUB120H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.15 | 22.85 | 129000 | 4.17 | 110000 | 2.62 | R-454B | 9.5833
217734997 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL |  |  |  | MMY-MUB120H1HT9PUL | Ducted Indoor Units | 115000 | 11.9 | 21.7 | 129000 | 3.95 | 110000 | 2.55 | R-454B | 9.5833
217734998 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL |  |  |  | MMY-MUB120H1HT9PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24 | 129000 | 4.4 | 110000 | 2.7 | R-454B | 9.5833
217883041 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL |  |  |  | MMY-MUB0721FT2P-UL | Non-Ducted Indoor Units | 69000 | 12 | 24.2 | 77000 | 4.55 | 56000 | 2.8 | R-454B | 5.75
217883043 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL |  |  |  | MMY-MUB0721FT2P-UL | Ducted Indoor Units | 69000 | 12 | 22 | 77000 | 4.18 | 56000 | 2.7 | R-454B | 5.75
217883045 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL |  |  |  | MMY-MUB0721FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 23.1 | 77000 | 4.36 | 56000 | 2.75 | R-454B | 5.75
217901715 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM72TXU-A |  |  |  | PURY-EM72TXU-A | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217901719 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM72TXU-A |  |  |  | PURY-EM72TXU-A | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217901723 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM96TXU-A |  |  |  | PURY-EM96TXU-A | Ducted Indoor Units | 92000 | 13.5 | 23.2 | 103000 | 3.97 | 79000 | 2.45 | R-32 | 7.6667
217901727 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM96TXU-A |  |  |  | PURY-EM96TXU-A | Non-Ducted Indoor Units | 92000 | 14.6 | 26.7 | 103000 | 4.43 | 79000 | 2.69 | R-32 | 7.6667
217901731 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120TXU-A |  |  |  | PURY-EM120TXU-A | Ducted Indoor Units | 115000 | 12.7 | 23.1 | 129000 | 3.73 | 93000 | 2.42 | R-32 | 9.5833
217901735 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120TXU-A |  |  |  | PURY-EM120TXU-A | Non-Ducted Indoor Units | 115000 | 13.3 | 24.1 | 129000 | 4.08 | 93000 | 2.55 | R-32 | 9.5833
217901721 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72TXU-A |  |  |  | PURY-HM72TXU-A | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217901717 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72TXU-A |  |  |  | PURY-HM72TXU-A | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217901729 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96TXU-A |  |  |  | PURY-HM96TXU-A | Non-Ducted Indoor Units | 92000 | 14.2 | 24.6 | 103000 | 4.42 | 79000 | 2.81 | R-32 | 7.6667
217901725 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96TXU-A |  |  |  | PURY-HM96TXU-A | Ducted Indoor Units | 92000 | 13.3 | 21.8 | 103000 | 3.96 | 79000 | 2.58 | R-32 | 7.6667
217901737 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120TXU-A |  |  |  | PURY-HM120TXU-A | Non-Ducted Indoor Units | 115000 | 13.9 | 24.5 | 129000 | 4.24 | 93000 | 2.68 | R-32 | 9.5833
217901733 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120TXU-A |  |  |  | PURY-HM120TXU-A | Ducted Indoor Units | 115000 | 13.2 | 21.9 | 129000 | 3.71 | 93000 | 2.58 | R-32 | 9.5833
217901716 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM72YXU-A |  |  |  | PURY-EM72YXU-A | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217901720 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM72YXU-A |  |  |  | PURY-EM72YXU-A | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217901724 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM96YXU-A |  |  |  | PURY-EM96YXU-A | Ducted Indoor Units | 92000 | 13.5 | 23.2 | 103000 | 3.97 | 79000 | 2.45 | R-32 | 7.6667
217901728 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM96YXU-A |  |  |  | PURY-EM96YXU-A | Non-Ducted Indoor Units | 92000 | 14.6 | 26.7 | 103000 | 4.43 | 79000 | 2.69 | R-32 | 7.6667
217901732 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120YXU-A |  |  |  | PURY-EM120YXU-A | Ducted Indoor Units | 115000 | 12.7 | 23.1 | 129000 | 3.73 | 93000 | 2.42 | R-32 | 9.5833
217901736 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120YXU-A |  |  |  | PURY-EM120YXU-A | Non-Ducted Indoor Units | 115000 | 13.3 | 24.1 | 129000 | 4.08 | 93000 | 2.55 | R-32 | 9.5833
217901722 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72YXU-A |  |  |  | PURY-HM72YXU-A | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217901718 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72YXU-A |  |  |  | PURY-HM72YXU-A | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217901730 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96YXU-A |  |  |  | PURY-HM96YXU-A | Non-Ducted Indoor Units | 92000 | 14.2 | 24.6 | 103000 | 4.42 | 79000 | 2.81 | R-32 | 7.6667
217901726 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96YXU-A |  |  |  | PURY-HM96YXU-A | Ducted Indoor Units | 92000 | 13.3 | 21.8 | 103000 | 3.96 | 79000 | 2.58 | R-32 | 7.6667
217901738 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120YXU-A |  |  |  | PURY-HM120YXU-A | Non-Ducted Indoor Units | 115000 | 13.9 | 24.5 | 129000 | 4.24 | 93000 | 2.68 | R-32 | 9.5833
217901734 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120YXU-A |  |  |  | PURY-HM120YXU-A | Ducted Indoor Units | 115000 | 13.2 | 21.9 | 129000 | 3.71 | 93000 | 2.58 | R-32 | 9.5833
217902261 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AMM0AN |  |  |  | TURYE0723AMM0AN | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217902259 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AMM0AN |  |  |  | TURYE0723AMM0AN | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217902269 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AMM0AN |  |  |  | TURYE0963AMM0AN | Non-Ducted Indoor Units | 92000 | 14.6 | 26.7 | 103000 | 4.43 | 79000 | 2.69 | R-32 | 7.6667
217902267 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AMM0AN |  |  |  | TURYE0963AMM0AN | Ducted Indoor Units | 92000 | 13.5 | 23.2 | 103000 | 3.97 | 79000 | 2.45 | R-32 | 7.6667
217902277 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AMM0AN |  |  |  | TURYE1203AMM0AN | Non-Ducted Indoor Units | 115000 | 13.3 | 24.1 | 129000 | 4.08 | 93000 | 2.55 | R-32 | 9.5833
217902275 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AMM0AN |  |  |  | TURYE1203AMM0AN | Ducted Indoor Units | 115000 | 12.7 | 23.1 | 129000 | 3.73 | 93000 | 2.42 | R-32 | 9.5833
217902260 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AMM0AN |  |  |  | TURYH0723AMM0AN | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217902262 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AMM0AN |  |  |  | TURYH0723AMM0AN | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217902270 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AMM0AN |  |  |  | TURYH0963AMM0AN | Non-Ducted Indoor Units | 92000 | 14.2 | 24.6 | 103000 | 4.42 | 79000 | 2.81 | R-32 | 7.6667
217902268 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AMM0AN |  |  |  | TURYH0963AMM0AN | Ducted Indoor Units | 92000 | 13.3 | 21.8 | 103000 | 3.96 | 79000 | 2.58 | R-32 | 7.6667
217902278 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AMM0AN |  |  |  | TURYH1203AMM0AN | Non-Ducted Indoor Units | 115000 | 13.9 | 24.5 | 129000 | 4.24 | 93000 | 2.68 | R-32 | 9.5833
217902276 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AMM0AN |  |  |  | TURYH1203AMM0AN | Ducted Indoor Units | 115000 | 13.2 | 21.9 | 129000 | 3.71 | 93000 | 2.58 | R-32 | 9.5833
217902265 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AMM0AN |  |  |  | TURYE0724AMM0AN | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217902263 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AMM0AN |  |  |  | TURYE0724AMM0AN | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217902271 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AMM0AN |  |  |  | TURYE0964AMM0AN | Ducted Indoor Units | 92000 | 13.5 | 23.2 | 103000 | 3.97 | 79000 | 2.45 | R-32 | 7.6667
217902273 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AMM0AN |  |  |  | TURYE0964AMM0AN | Non-Ducted Indoor Units | 92000 | 14.6 | 26.7 | 103000 | 4.43 | 79000 | 2.69 | R-32 | 7.6667
217902279 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AMM0AN |  |  |  | TURYE1204AMM0AN | Ducted Indoor Units | 115000 | 12.7 | 23.1 | 129000 | 3.73 | 93000 | 2.42 | R-32 | 9.5833
217902281 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AMM0AN |  |  |  | TURYE1204AMM0AN | Non-Ducted Indoor Units | 115000 | 13.3 | 24.1 | 129000 | 4.08 | 93000 | 2.55 | R-32 | 9.5833
217902266 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AMM0AN |  |  |  | TURYH0724AMM0AN | Non-Ducted Indoor Units | 69000 | 15.3 | 26.1 | 76000 | 4.69 | 61000 | 2.91 | R-32 | 5.75
217902264 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AMM0AN |  |  |  | TURYH0724AMM0AN | Ducted Indoor Units | 69000 | 14.2 | 22.3 | 76000 | 4.01 | 61000 | 2.68 | R-32 | 5.75
217902272 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AMM0AN |  |  |  | TURYH0964AMM0AN | Ducted Indoor Units | 92000 | 13.3 | 21.8 | 103000 | 3.96 | 79000 | 2.58 | R-32 | 7.6667
217902274 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AMM0AN |  |  |  | TURYH0964AMM0AN | Non-Ducted Indoor Units | 92000 | 14.2 | 24.6 | 103000 | 4.42 | 79000 | 2.81 | R-32 | 7.6667
217902280 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AMM0AN |  |  |  | TURYH1204AMM0AN | Ducted Indoor Units | 115000 | 13.2 | 21.9 | 129000 | 3.71 | 93000 | 2.58 | R-32 | 9.5833
217902282 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AMM0AN |  |  |  | TURYH1204AMM0AN | Non-Ducted Indoor Units | 115000 | 13.9 | 24.5 | 129000 | 4.24 | 93000 | 2.68 | R-32 | 9.5833
217901675 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM72TXU-A |  |  |  | PUHY-EM72TXU-A | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217901676 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM72TXU-A |  |  |  | PUHY-EM72TXU-A | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217901683 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM96TXU-A |  |  |  | PUHY-EM96TXU-A | Ducted Indoor Units | 92000 | 13.9 | 24.1 | 103000 | 4.06 | 79000 | 2.56 | R-32 | 7.6667
217901684 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM96TXU-A |  |  |  | PUHY-EM96TXU-A | Non-Ducted Indoor Units | 92000 | 14.8 | 27.7 | 103000 | 4.58 | 79000 | 2.8 | R-32 | 7.6667
217901691 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120TXU-A |  |  |  | PUHY-EM120TXU-A | Ducted Indoor Units | 115000 | 13 | 23.8 | 129000 | 3.87 | 93000 | 2.46 | R-32 | 9.5833
217901692 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120TXU-A |  |  |  | PUHY-EM120TXU-A | Non-Ducted Indoor Units | 115000 | 13.6 | 26.5 | 129000 | 4.22 | 93000 | 2.64 | R-32 | 9.5833
217901679 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72TXU-A |  |  |  | PUHY-HM72TXU-A | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217901680 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72TXU-A |  |  |  | PUHY-HM72TXU-A | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217901687 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96TXU-A |  |  |  | PUHY-HM96TXU-A | Ducted Indoor Units | 92000 | 13.6 | 22.4 | 103000 | 4.04 | 79000 | 2.63 | R-32 | 7.6667
217901688 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96TXU-A |  |  |  | PUHY-HM96TXU-A | Non-Ducted Indoor Units | 92000 | 14.6 | 25.4 | 103000 | 4.53 | 79000 | 2.88 | R-32 | 7.6667
217901695 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120TXU-A |  |  |  | PUHY-HM120TXU-A | Ducted Indoor Units | 115000 | 13.6 | 22.6 | 129000 | 3.82 | 93000 | 2.64 | R-32 | 9.5833
217901696 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120TXU-A |  |  |  | PUHY-HM120TXU-A | Non-Ducted Indoor Units | 115000 | 14.1 | 25.1 | 129000 | 4.38 | 93000 | 2.75 | R-32 | 9.5833
217901677 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM72YXU-A |  |  |  | PUHY-EM72YXU-A | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217901678 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM72YXU-A |  |  |  | PUHY-EM72YXU-A | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217901685 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM96YXU-A |  |  |  | PUHY-EM96YXU-A | Ducted Indoor Units | 92000 | 13.9 | 24.1 | 103000 | 4.06 | 79000 | 2.56 | R-32 | 7.6667
217901686 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM96YXU-A |  |  |  | PUHY-EM96YXU-A | Non-Ducted Indoor Units | 92000 | 14.8 | 27.7 | 103000 | 4.58 | 79000 | 2.8 | R-32 | 7.6667
217901693 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120YXU-A |  |  |  | PUHY-EM120YXU-A | Ducted Indoor Units | 115000 | 13 | 23.8 | 129000 | 3.87 | 93000 | 2.46 | R-32 | 9.5833
217901694 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120YXU-A |  |  |  | PUHY-EM120YXU-A | Non-Ducted Indoor Units | 115000 | 13.6 | 26.5 | 129000 | 4.22 | 93000 | 2.64 | R-32 | 9.5833
217901681 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72YXU-A |  |  |  | PUHY-HM72YXU-A | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217901682 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72YXU-A |  |  |  | PUHY-HM72YXU-A | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217901689 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96YXU-A |  |  |  | PUHY-HM96YXU-A | Ducted Indoor Units | 92000 | 13.6 | 22.4 | 103000 | 4.04 | 79000 | 2.63 | R-32 | 7.6667
217901690 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96YXU-A |  |  |  | PUHY-HM96YXU-A | Non-Ducted Indoor Units | 92000 | 14.6 | 25.4 | 103000 | 4.53 | 79000 | 2.88 | R-32 | 7.6667
217901697 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120YXU-A |  |  |  | PUHY-HM120YXU-A | Ducted Indoor Units | 115000 | 13.6 | 22.6 | 129000 | 3.82 | 93000 | 2.64 | R-32 | 9.5833
217901698 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120YXU-A |  |  |  | PUHY-HM120YXU-A | Non-Ducted Indoor Units | 115000 | 14.1 | 25.1 | 129000 | 4.38 | 93000 | 2.75 | R-32 | 9.5833
217902187 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AMM0AN |  |  |  | TUHYE0723AMM0AN | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217902189 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AMM0AN |  |  |  | TUHYE0723AMM0AN | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217902197 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AMM0AN |  |  |  | TUHYE0963AMM0AN | Non-Ducted Indoor Units | 92000 | 14.8 | 27.7 | 103000 | 4.58 | 79000 | 2.8 | R-32 | 7.6667
217902195 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AMM0AN |  |  |  | TUHYE0963AMM0AN | Ducted Indoor Units | 92000 | 13.9 | 24.1 | 103000 | 4.06 | 79000 | 2.56 | R-32 | 7.6667
217902205 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AMM0AN |  |  |  | TUHYE1203AMM0AN | Non-Ducted Indoor Units | 115000 | 13.6 | 26.5 | 129000 | 4.22 | 93000 | 2.64 | R-32 | 9.5833
217902203 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AMM0AN |  |  |  | TUHYE1203AMM0AN | Ducted Indoor Units | 115000 | 13 | 23.8 | 129000 | 3.87 | 93000 | 2.46 | R-32 | 9.5833
217902190 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AMM0AN |  |  |  | TUHYH0723AMM0AN | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217902188 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AMM0AN |  |  |  | TUHYH0723AMM0AN | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217902196 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AMM0AN |  |  |  | TUHYH0963AMM0AN | Ducted Indoor Units | 92000 | 13.6 | 22.4 | 103000 | 4.04 | 79000 | 2.63 | R-32 | 7.6667
217902198 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AMM0AN |  |  |  | TUHYH0963AMM0AN | Non-Ducted Indoor Units | 92000 | 14.6 | 25.4 | 103000 | 4.53 | 79000 | 2.88 | R-32 | 7.6667
217902204 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AMM0AN |  |  |  | TUHYH1203AMM0AN | Ducted Indoor Units | 115000 | 13.6 | 22.6 | 129000 | 3.82 | 93000 | 2.64 | R-32 | 9.5833
217902206 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AMM0AN |  |  |  | TUHYH1203AMM0AN | Non-Ducted Indoor Units | 115000 | 14.1 | 25.1 | 129000 | 4.38 | 93000 | 2.75 | R-32 | 9.5833
217902193 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AMM0AN |  |  |  | TUHYE0724AMM0AN | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217902191 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AMM0AN |  |  |  | TUHYE0724AMM0AN | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217902199 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AMM0AN |  |  |  | TUHYE0964AMM0AN | Ducted Indoor Units | 92000 | 13.9 | 24.1 | 103000 | 4.06 | 79000 | 2.56 | R-32 | 7.6667
217902201 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AMM0AN |  |  |  | TUHYE0964AMM0AN | Non-Ducted Indoor Units | 92000 | 14.8 | 27.7 | 103000 | 4.58 | 79000 | 2.8 | R-32 | 7.6667
217902207 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AMM0AN |  |  |  | TUHYE1204AMM0AN | Ducted Indoor Units | 115000 | 13 | 23.8 | 129000 | 3.87 | 93000 | 2.46 | R-32 | 9.5833
217902209 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AMM0AN |  |  |  | TUHYE1204AMM0AN | Non-Ducted Indoor Units | 115000 | 13.6 | 26.5 | 129000 | 4.22 | 93000 | 2.64 | R-32 | 9.5833
217902194 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AMM0AN |  |  |  | TUHYH0724AMM0AN | Non-Ducted Indoor Units | 69000 | 15.6 | 27.8 | 76000 | 4.81 | 61000 | 3 | R-32 | 5.75
217902192 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AMM0AN |  |  |  | TUHYH0724AMM0AN | Ducted Indoor Units | 69000 | 14.4 | 23.3 | 76000 | 4.2 | 61000 | 2.8 | R-32 | 5.75
217902200 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AMM0AN |  |  |  | TUHYH0964AMM0AN | Ducted Indoor Units | 92000 | 13.6 | 22.4 | 103000 | 4.04 | 79000 | 2.63 | R-32 | 7.6667
217902202 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AMM0AN |  |  |  | TUHYH0964AMM0AN | Non-Ducted Indoor Units | 92000 | 14.6 | 25.4 | 103000 | 4.53 | 79000 | 2.88 | R-32 | 7.6667
217902210 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AMM0AN |  |  |  | TUHYH1204AMM0AN | Non-Ducted Indoor Units | 115000 | 14.1 | 25.1 | 129000 | 4.38 | 93000 | 2.75 | R-32 | 9.5833
217902208 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AMM0AN |  |  |  | TUHYH1204AMM0AN | Ducted Indoor Units | 115000 | 13.6 | 22.6 | 129000 | 3.82 | 93000 | 2.64 | R-32 | 9.5833
218003112 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVGFG |  |  |  | AM072HCVGFG | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218004887 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVGFG |  |  |  | AM072HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218003044 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVGFG |  |  |  | AM072HCVGFG | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218043859 | N/A | LENNOX | HMSV-A-CB | VPD072S6M-5Y |  |  |  | VPD072S6M-5Y | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218043995 | N/A | LENNOX | HMSV-A-CB | VPD072S6M-5Y |  |  |  | VPD072S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218043927 | N/A | LENNOX | HMSV-A-CB | VPD072S6M-5Y |  |  |  | VPD072S6M-5Y | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218043931 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5Y |  |  |  | VPD096S6M-5Y | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218043999 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5Y |  |  |  | VPD096S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218043863 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5Y |  |  |  | VPD096S6M-5Y | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218004891 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG |  |  |  | AM096HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218003116 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG |  |  |  | AM096HCVGFG | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218003048 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG |  |  |  | AM096HCVGFG | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218003052 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGFG |  |  |  | AM120HCVGFG | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218004385 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGFG |  |  |  | AM120HCVGFG | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218004895 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGFG |  |  |  | AM120HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043867 | N/A | LENNOX | HMSV-A-CB | VPD120S6M-5Y |  |  |  | VPD120S6M-5Y | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218044003 | N/A | LENNOX | HMSV-A-CB | VPD120S6M-5Y |  |  |  | VPD120S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043991 | N/A | LENNOX | HMSV-A-CB | VPD120S6M-5Y |  |  |  | VPD120S6M-5Y | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218003113 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVGFS |  |  |  | AM072HCVGFS | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218004888 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVGFS |  |  |  | AM072HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218003045 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVGFS |  |  |  | AM072HCVGFS | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218043860 | N/A | LENNOX | HMSR-A-CB | VRD072S6M-5Y |  |  |  | VRD072S6M-5Y | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218043996 | N/A | LENNOX | HMSR-A-CB | VRD072S6M-5Y |  |  |  | VRD072S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218043928 | N/A | LENNOX | HMSR-A-CB | VRD072S6M-5Y |  |  |  | VRD072S6M-5Y | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218043932 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5Y |  |  |  | VRD096S6M-5Y | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218044000 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5Y |  |  |  | VRD096S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218043864 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5Y |  |  |  | VRD096S6M-5Y | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218004892 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS |  |  |  | AM096HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218003117 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS |  |  |  | AM096HCVGFS | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218003049 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS |  |  |  | AM096HCVGFS | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218003053 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGFS |  |  |  | AM120HCVGFS | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218004386 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGFS |  |  |  | AM120HCVGFS | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218004896 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGFS |  |  |  | AM120HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043868 | N/A | LENNOX | HMSR-A-CB | VRD120S6M-5Y |  |  |  | VRD120S6M-5Y | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218044004 | N/A | LENNOX | HMSR-A-CB | VRD120S6M-5Y |  |  |  | VRD120S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043992 | N/A | LENNOX | HMSR-A-CB | VRD120S6M-5Y |  |  |  | VRD120S6M-5Y | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218003114 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVGJG |  |  |  | AM072HCVGJG | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218004889 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVGJG |  |  |  | AM072HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218003046 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVGJG |  |  |  | AM072HCVGJG | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218043861 | N/A | LENNOX | HMSV-A-CB | VPD072S6M-5G |  |  |  | VPD072S6M-5G | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218043997 | N/A | LENNOX | HMSV-A-CB | VPD072S6M-5G |  |  |  | VPD072S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218043929 | N/A | LENNOX | HMSV-A-CB | VPD072S6M-5G |  |  |  | VPD072S6M-5G | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218043933 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5G |  |  |  | VPD096S6M-5G | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218044001 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5G |  |  |  | VPD096S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218043865 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5G |  |  |  | VPD096S6M-5G | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218004893 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG |  |  |  | AM096HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218003118 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG |  |  |  | AM096HCVGJG | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218003050 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG |  |  |  | AM096HCVGJG | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218003054 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGJG |  |  |  | AM120HCVGJG | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218004387 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGJG |  |  |  | AM120HCVGJG | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218004897 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGJG |  |  |  | AM120HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043869 | N/A | LENNOX | HMSV-A-CB | VPD120S6M-5G |  |  |  | VPD120S6M-5G | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218044005 | N/A | LENNOX | HMSV-A-CB | VPD120S6M-5G |  |  |  | VPD120S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043993 | N/A | LENNOX | HMSV-A-CB | VPD120S6M-5G |  |  |  | VPD120S6M-5G | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218003115 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVGJS |  |  |  | AM072HCVGJS | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218004890 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVGJS |  |  |  | AM072HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218003047 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVGJS |  |  |  | AM072HCVGJS | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218043862 | N/A | LENNOX | HMSR-A-CB | VRD072S6M-5G |  |  |  | VRD072S6M-5G | Ducted Indoor Units | 69000 | 11.6 | 23.3 | 77000 | 3.9 | 51000 | 2.84 | R-32 | 5.75
218043998 | N/A | LENNOX | HMSR-A-CB | VRD072S6M-5G |  |  |  | VRD072S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.3 | 23.74 | 77000 | 3.91 | 51000 | 2.77 | R-32 | 5.75
218043930 | N/A | LENNOX | HMSR-A-CB | VRD072S6M-5G |  |  |  | VRD072S6M-5G | Non-Ducted Indoor Units | 69000 | 11 | 24.18 | 77000 | 3.93 | 51000 | 2.7 | R-32 | 5.75
218043934 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5G |  |  |  | VRD096S6M-5G | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218044002 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5G |  |  |  | VRD096S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218043866 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5G |  |  |  | VRD096S6M-5G | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218004894 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS |  |  |  | AM096HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.17 | 26.04 | 103000 | 4.07 | 67000 | 2.83 | R-32 | 7.6667
218003119 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS |  |  |  | AM096HCVGJS | Non-Ducted Indoor Units | 92000 | 12.15 | 27.98 | 103000 | 4.21 | 67000 | 2.92 | R-32 | 7.6667
218003051 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS |  |  |  | AM096HCVGJS | Ducted Indoor Units | 92000 | 12.2 | 24.1 | 103000 | 3.94 | 67000 | 2.75 | R-32 | 7.6667
218003055 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGJS |  |  |  | AM120HCVGJS | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218004388 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGJS |  |  |  | AM120HCVGJS | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218004898 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGJS |  |  |  | AM120HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043870 | N/A | LENNOX | HMSR-A-CB | VRD120S6M-5G |  |  |  | VRD120S6M-5G | Ducted Indoor Units | 114000 | 11.7 | 22.6 | 129000 | 3.8 | 84000 | 2.8 | R-32 | 9.5
218044006 | N/A | LENNOX | HMSR-A-CB | VRD120S6M-5G |  |  |  | VRD120S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.42 | 24.26 | 129000 | 3.82 | 84000 | 2.8 | R-32 | 9.5
218043994 | N/A | LENNOX | HMSR-A-CB | VRD120S6M-5G |  |  |  | VRD120S6M-5G | Non-Ducted Indoor Units | 114000 | 11.15 | 25.92 | 129000 | 3.85 | 84000 | 2.81 | R-32 | 9.5
218005667 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG |  |  |  | AM072HCVTFG | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218005699 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG |  |  |  | AM072HCVTFG | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218005739 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG |  |  |  | AM072HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218044063 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y |  |  |  | VPD072L6M-5Y | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218044095 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y |  |  |  | VPD072L6M-5Y | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218044135 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y |  |  |  | VPD072L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218044139 | N/A | LENNOX | HMSV-A-CB | VPD096L6M-5Y |  |  |  | VPD096L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218044099 | N/A | LENNOX | HMSV-A-CB | VPD096L6M-5Y |  |  |  | VPD096L6M-5Y | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218044067 | N/A | LENNOX | HMSV-A-CB | VPD096L6M-5Y |  |  |  | VPD096L6M-5Y | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218005743 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTFG |  |  |  | AM096HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218005703 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTFG |  |  |  | AM096HCVTFG | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218005671 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTFG |  |  |  | AM096HCVTFG | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218005675 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVTFG |  |  |  | AM120HCVTFG | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218005747 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVTFG |  |  |  | AM120HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218005707 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVTFG |  |  |  | AM120HCVTFG | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218044071 | N/A | LENNOX | HMSV-A-CB | VPD120L6M-5Y |  |  |  | VPD120L6M-5Y | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218044103 | N/A | LENNOX | HMSV-A-CB | VPD120L6M-5Y |  |  |  | VPD120L6M-5Y | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218044143 | N/A | LENNOX | HMSV-A-CB | VPD120L6M-5Y |  |  |  | VPD120L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218044096 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y |  |  |  | VRD072L6M-5Y | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218044136 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y |  |  |  | VRD072L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218044064 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y |  |  |  | VRD072L6M-5Y | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218005740 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS |  |  |  | AM072HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218005700 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS |  |  |  | AM072HCVTFS | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218005668 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS |  |  |  | AM072HCVTFS | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218005704 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTFS |  |  |  | AM096HCVTFS | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218005672 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTFS |  |  |  | AM096HCVTFS | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218005744 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTFS |  |  |  | AM096HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218044068 | N/A | LENNOX | HMSR-A-CB | VRD096L6M-5Y |  |  |  | VRD096L6M-5Y | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218044140 | N/A | LENNOX | HMSR-A-CB | VRD096L6M-5Y |  |  |  | VRD096L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218044100 | N/A | LENNOX | HMSR-A-CB | VRD096L6M-5Y |  |  |  | VRD096L6M-5Y | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218044144 | N/A | LENNOX | HMSR-A-CB | VRD120L6M-5Y |  |  |  | VRD120L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218044104 | N/A | LENNOX | HMSR-A-CB | VRD120L6M-5Y |  |  |  | VRD120L6M-5Y | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218044072 | N/A | LENNOX | HMSR-A-CB | VRD120L6M-5Y |  |  |  | VRD120L6M-5Y | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218005748 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVTFS |  |  |  | AM120HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218005708 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVTFS |  |  |  | AM120HCVTFS | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218005676 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVTFS |  |  |  | AM120HCVTFS | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218005701 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG |  |  |  | AM072HCVTJG | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218005741 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG |  |  |  | AM072HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218005669 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG |  |  |  | AM072HCVTJG | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218044065 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G |  |  |  | VPD072L6M-5G | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218044097 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G |  |  |  | VPD072L6M-5G | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218044137 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G |  |  |  | VPD072L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218044141 | N/A | LENNOX | HMSV-A-CB | VPD096L6M-5G |  |  |  | VPD096L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218044101 | N/A | LENNOX | HMSV-A-CB | VPD096L6M-5G |  |  |  | VPD096L6M-5G | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218044069 | N/A | LENNOX | HMSV-A-CB | VPD096L6M-5G |  |  |  | VPD096L6M-5G | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218005745 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTJG |  |  |  | AM096HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218005705 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTJG |  |  |  | AM096HCVTJG | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218005673 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVTJG |  |  |  | AM096HCVTJG | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218005677 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVTJG |  |  |  | AM120HCVTJG | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218005749 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVTJG |  |  |  | AM120HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218005709 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVTJG |  |  |  | AM120HCVTJG | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218044073 | N/A | LENNOX | HMSV-A-CB | VPD120L6M-5G |  |  |  | VPD120L6M-5G | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218044105 | N/A | LENNOX | HMSV-A-CB | VPD120L6M-5G |  |  |  | VPD120L6M-5G | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218044145 | N/A | LENNOX | HMSV-A-CB | VPD120L6M-5G |  |  |  | VPD120L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218044098 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G |  |  |  | VRD072L6M-5G | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218044138 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G |  |  |  | VRD072L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218044066 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G |  |  |  | VRD072L6M-5G | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218005742 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS |  |  |  | AM072HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.15 | 25.66 | 77000 | 4.29 | 77000 | 2.62 | R-32 | 5.75
218005702 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS |  |  |  | AM072HCVTJS | Non-Ducted Indoor Units | 69000 | 12.35 | 26.76 | 77000 | 4.4 | 77000 | 2.64 | R-32 | 5.75
218005670 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS |  |  |  | AM072HCVTJS | Ducted Indoor Units | 69000 | 11.95 | 24.57 | 77000 | 4.18 | 77000 | 2.6 | R-32 | 5.75
218005706 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTJS |  |  |  | AM096HCVTJS | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218005674 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTJS |  |  |  | AM096HCVTJS | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218005746 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVTJS |  |  |  | AM096HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218044070 | N/A | LENNOX | HMSR-A-CB | VRD096L6M-5G |  |  |  | VRD096L6M-5G | Ducted Indoor Units | 92000 | 12.3 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-32 | 7.6667
218044142 | N/A | LENNOX | HMSR-A-CB | VRD096L6M-5G |  |  |  | VRD096L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 25.95 | 103000 | 4 | 103000 | 2.48 | R-32 | 7.6667
218044102 | N/A | LENNOX | HMSR-A-CB | VRD096L6M-5G |  |  |  | VRD096L6M-5G | Non-Ducted Indoor Units | 92000 | 12.7 | 26.8 | 103000 | 4.06 | 103000 | 2.49 | R-32 | 7.6667
218044146 | N/A | LENNOX | HMSR-A-CB | VRD120L6M-5G |  |  |  | VRD120L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218044106 | N/A | LENNOX | HMSR-A-CB | VRD120L6M-5G |  |  |  | VRD120L6M-5G | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218044074 | N/A | LENNOX | HMSR-A-CB | VRD120L6M-5G |  |  |  | VRD120L6M-5G | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218005750 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVTJS |  |  |  | AM120HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.82 | 25.79 | 129000 | 3.91 | 129000 | 2.37 | R-32 | 9.5
218005710 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVTJS |  |  |  | AM120HCVTJS | Non-Ducted Indoor Units | 114000 | 11.4 | 26.6 | 129000 | 3.88 | 129000 | 2.36 | R-32 | 9.5
218005678 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVTJS |  |  |  | AM120HCVTJS | Ducted Indoor Units | 114000 | 12.25 | 24.98 | 129000 | 3.95 | 129000 | 2.38 | R-32 | 9.5
218007897 | N/A | MIDEA | HMSR-A-CB | MV8-2R72V2XN10C |  |  |  | MV8-2R72V2XN10C | Ducted Indoor Units | 69000 | 12.6 | 23.9 | 77000 | 3.87 | 64000 | 2.25 | R-454B | 5.75
218007898 | N/A | MIDEA | HMSR-A-CB | MV8-2R72V2XN10C |  |  |  | MV8-2R72V2XN10C | Non-Ducted Indoor Units | 69000 | 12.8 | 24.5 | 77000 | 4.25 | 64000 | 2.25 | R-454B | 5.75
218007909 | N/A | MIDEA | HMSR-A-CB | MV8-2R72V2XN10C |  |  |  | MV8-2R72V2XN10C | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.7 | 24.2 | 77000 | 4.06 | 64000 | 2.25 | R-454B | 5.75
218007910 | N/A | MIDEA | HMSR-A-CB | MV8-2R96V2XN10C |  |  |  | MV8-2R96V2XN10C | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.35 | 24.6 | 104000 | 4.05 | 87000 | 2.25 | R-454B | 7.6667
218007899 | N/A | MIDEA | HMSR-A-CB | MV8-2R96V2XN10C |  |  |  | MV8-2R96V2XN10C | Ducted Indoor Units | 92000 | 12 | 22.8 | 104000 | 3.9 | 87000 | 2.25 | R-454B | 7.6667
218007900 | N/A | MIDEA | HMSR-A-CB | MV8-2R96V2XN10C |  |  |  | MV8-2R96V2XN10C | Non-Ducted Indoor Units | 92000 | 12.7 | 26.4 | 104000 | 4.2 | 87000 | 2.25 | R-454B | 7.6667
218007901 | N/A | MIDEA | HMSR-A-CB | MV8-2R120V2XN10C |  |  |  | MV8-2R120V2XN10C | Ducted Indoor Units | 115000 | 11.6 | 22 | 130000 | 3.72 | 91000 | 2.25 | R-454B | 9.5833
218007902 | N/A | MIDEA | HMSR-A-CB | MV8-2R120V2XN10C |  |  |  | MV8-2R120V2XN10C | Non-Ducted Indoor Units | 115000 | 12.1 | 24.5 | 130000 | 4.06 | 91000 | 2.25 | R-454B | 9.5833
218007911 | N/A | MIDEA | HMSR-A-CB | MV8-2R120V2XN10C |  |  |  | MV8-2R120V2XN10C | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.85 | 23.25 | 130000 | 3.89 | 91000 | 2.25 | R-454B | 9.5833
218007912 | N/A | MIDEA | HMSR-A-CB | MV8-2R72V2ZN10C |  |  |  | MV8-2R72V2ZN10C | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.7 | 24.2 | 77000 | 4.06 | 64000 | 2.25 | R-454B | 5.75
218007903 | N/A | MIDEA | HMSR-A-CB | MV8-2R72V2ZN10C |  |  |  | MV8-2R72V2ZN10C | Ducted Indoor Units | 69000 | 12.6 | 23.9 | 77000 | 3.87 | 64000 | 2.25 | R-454B | 5.75
218007904 | N/A | MIDEA | HMSR-A-CB | MV8-2R72V2ZN10C |  |  |  | MV8-2R72V2ZN10C | Non-Ducted Indoor Units | 69000 | 12.8 | 24.5 | 77000 | 4.25 | 64000 | 2.25 | R-454B | 5.75
218007905 | N/A | MIDEA | HMSR-A-CB | MV8-2R96V2ZN10C |  |  |  | MV8-2R96V2ZN10C | Ducted Indoor Units | 92000 | 12 | 22.8 | 104000 | 3.9 | 87000 | 2.25 | R-454B | 7.6667
218007906 | N/A | MIDEA | HMSR-A-CB | MV8-2R96V2ZN10C |  |  |  | MV8-2R96V2ZN10C | Non-Ducted Indoor Units | 92000 | 12.7 | 26.4 | 104000 | 4.2 | 87000 | 2.25 | R-454B | 7.6667
218007913 | N/A | MIDEA | HMSR-A-CB | MV8-2R96V2ZN10C |  |  |  | MV8-2R96V2ZN10C | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.35 | 24.6 | 104000 | 4.05 | 87000 | 2.25 | R-454B | 7.6667
218007914 | N/A | MIDEA | HMSR-A-CB | MV8-2R120V2ZN10C |  |  |  | MV8-2R120V2ZN10C | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.85 | 23.25 | 130000 | 3.89 | 91000 | 2.25 | R-454B | 9.5833
218007907 | N/A | MIDEA | HMSR-A-CB | MV8-2R120V2ZN10C |  |  |  | MV8-2R120V2ZN10C | Ducted Indoor Units | 115000 | 11.6 | 22 | 130000 | 3.72 | 91000 | 2.25 | R-454B | 9.5833
218007908 | N/A | MIDEA | HMSR-A-CB | MV8-2R120V2ZN10C |  |  |  | MV8-2R120V2ZN10C | Non-Ducted Indoor Units | 115000 | 12.1 | 24.5 | 130000 | 4.06 | 91000 | 2.25 | R-454B | 9.5833
218008878 | N/A | MIDEA | HMSV-A-CB | MV8-X72V2XN10C |  |  |  | MV8-X72V2XN10C | Ducted Indoor Units | 69000 | 12.2 | 22 | 77000 | 3.87 | 64000 | 2.35 | R-454B | 5.75
218008879 | N/A | MIDEA | HMSV-A-CB | MV8-X72V2XN10C |  |  |  | MV8-X72V2XN10C | Non-Ducted Indoor Units | 69000 | 12.7 | 23 | 77000 | 4.3 | 64000 | 2.51 | R-454B | 5.75
218008880 | N/A | MIDEA | HMSV-A-CB | MV8-X96V2XN10C |  |  |  | MV8-X96V2XN10C | Ducted Indoor Units | 92000 | 11.8 | 22 | 103000 | 3.8 | 87000 | 2.33 | R-454B | 7.6667
218008881 | N/A | MIDEA | HMSV-A-CB | MV8-X96V2XN10C |  |  |  | MV8-X96V2XN10C | Non-Ducted Indoor Units | 92000 | 12.5 | 24.5 | 103000 | 4.05 | 87000 | 2.45 | R-454B | 7.6667
218008882 | N/A | MIDEA | HMSV-A-CB | MV8-X120V2XN10C |  |  |  | MV8-X120V2XN10C | Ducted Indoor Units | 115000 | 11.5 | 21.5 | 129000 | 3.71 | 93000 | 2.31 | R-454B | 9.5833
218008883 | N/A | MIDEA | HMSV-A-CB | MV8-X120V2XN10C |  |  |  | MV8-X120V2XN10C | Non-Ducted Indoor Units | 115000 | 12 | 23 | 129000 | 4 | 93000 | 2.36 | R-454B | 9.5833
218008884 | N/A | MIDEA | HMSV-A-CB | MV8-X72V2ZN10C |  |  |  | MV8-X72V2ZN10C | Ducted Indoor Units | 69000 | 12.2 | 22 | 77000 | 3.87 | 64000 | 2.35 | R-454B | 5.75
218008885 | N/A | MIDEA | HMSV-A-CB | MV8-X72V2ZN10C |  |  |  | MV8-X72V2ZN10C | Non-Ducted Indoor Units | 69000 | 12.7 | 23 | 77000 | 4.3 | 64000 | 2.51 | R-454B | 5.75
218008886 | N/A | MIDEA | HMSV-A-CB | MV8-X96V2ZN10C |  |  |  | MV8-X96V2ZN10C | Ducted Indoor Units | 92000 | 11.8 | 22 | 103000 | 3.8 | 87000 | 2.33 | R-454B | 7.6667
218008887 | N/A | MIDEA | HMSV-A-CB | MV8-X96V2ZN10C |  |  |  | MV8-X96V2ZN10C | Non-Ducted Indoor Units | 92000 | 12.5 | 24.5 | 103000 | 4.05 | 87000 | 2.45 | R-454B | 7.6667
218008888 | N/A | MIDEA | HMSV-A-CB | MV8-X120V2ZN10C |  |  |  | MV8-X120V2ZN10C | Ducted Indoor Units | 115000 | 11.5 | 21.5 | 129000 | 3.71 | 93000 | 2.31 | R-454B | 9.5833
218008889 | N/A | MIDEA | HMSV-A-CB | MV8-X120V2ZN10C |  |  |  | MV8-X120V2ZN10C | Non-Ducted Indoor Units | 115000 | 12 | 23 | 129000 | 4 | 93000 | 2.36 | R-454B | 9.5833
218036901 | N/A | DAIKIN | HMSV-A-CB | RXYA72AATJ* |  |  |  | RXYA72AATJ* | Non-Ducted Indoor Units | 69000 | 12.5 | 23.5 | 69000 | 3.64 | 51000 | 2.4 | R-32 | 5.75
218036937 | N/A | DAIKIN | HMSV-A-CB | RXYA72AATJ* |  |  |  | RXYA72AATJ* | Ducted Indoor Units | 69000 | 12.4 | 21 | 69000 | 3.6 | 51000 | 2.4 | R-32 | 5.75
218036973 | N/A | DAIKIN | HMSV-A-CB | RXYA72AATJ* |  |  |  | RXYA72AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.45 | 22.25 | 69000 | 3.62 | 51000 | 2.4 | R-32 | 5.75
218036974 | N/A | DAIKIN | HMSV-A-CB | RXYA96AATJ* |  |  |  | RXYA96AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 22.65 | 92000 | 3.45 | 72000 | 2.27 | R-32 | 7.6667
218036938 | N/A | DAIKIN | HMSV-A-CB | RXYA96AATJ* |  |  |  | RXYA96AATJ* | Ducted Indoor Units | 92000 | 12 | 20.8 | 92000 | 3.4 | 72000 | 2.25 | R-32 | 7.6667
218036902 | N/A | DAIKIN | HMSV-A-CB | RXYA96AATJ* |  |  |  | RXYA96AATJ* | Non-Ducted Indoor Units | 92000 | 12.2 | 24.5 | 92000 | 3.5 | 72000 | 2.3 | R-32 | 7.6667
218036903 | N/A | DAIKIN | HMSV-A-CB | RXYA120AATJ* |  |  |  | RXYA120AATJ* | Non-Ducted Indoor Units | 114000 | 11.1 | 22.8 | 114000 | 3.4 | 82000 | 2.25 | R-32 | 9.5
218036939 | N/A | DAIKIN | HMSV-A-CB | RXYA120AATJ* |  |  |  | RXYA120AATJ* | Ducted Indoor Units | 114000 | 11.1 | 20 | 114000 | 3.4 | 82000 | 2.25 | R-32 | 9.5
218036975 | N/A | DAIKIN | HMSV-A-CB | RXYA120AATJ* |  |  |  | RXYA120AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.1 | 21.4 | 114000 | 3.4 | 82000 | 2.25 | R-32 | 9.5
218036919 | N/A | DAIKIN | HMSV-A-CB | RXYA72AAYD* |  |  |  | RXYA72AAYD* | Non-Ducted Indoor Units | 69000 | 12.5 | 23.5 | 69000 | 3.64 | 51000 | 2.4 | R-32 | 5.75
218036955 | N/A | DAIKIN | HMSV-A-CB | RXYA72AAYD* |  |  |  | RXYA72AAYD* | Ducted Indoor Units | 69000 | 12.4 | 21 | 69000 | 3.6 | 51000 | 2.4 | R-32 | 5.75
218036991 | N/A | DAIKIN | HMSV-A-CB | RXYA72AAYD* |  |  |  | RXYA72AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.45 | 22.25 | 69000 | 3.62 | 51000 | 2.4 | R-32 | 5.75
218036992 | N/A | DAIKIN | HMSV-A-CB | RXYA96AAYD* |  |  |  | RXYA96AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 22.65 | 92000 | 3.45 | 72000 | 2.27 | R-32 | 7.6667
218036956 | N/A | DAIKIN | HMSV-A-CB | RXYA96AAYD* |  |  |  | RXYA96AAYD* | Ducted Indoor Units | 92000 | 12 | 20.8 | 92000 | 3.4 | 72000 | 2.25 | R-32 | 7.6667
218036920 | N/A | DAIKIN | HMSV-A-CB | RXYA96AAYD* |  |  |  | RXYA96AAYD* | Non-Ducted Indoor Units | 92000 | 12.2 | 24.5 | 92000 | 3.5 | 72000 | 2.3 | R-32 | 7.6667
218036921 | N/A | DAIKIN | HMSV-A-CB | RXYA120AAYD* |  |  |  | RXYA120AAYD* | Non-Ducted Indoor Units | 114000 | 11.1 | 22.8 | 114000 | 3.4 | 82000 | 2.25 | R-32 | 9.5
218036957 | N/A | DAIKIN | HMSV-A-CB | RXYA120AAYD* |  |  |  | RXYA120AAYD* | Ducted Indoor Units | 114000 | 11.1 | 20 | 114000 | 3.4 | 82000 | 2.25 | R-32 | 9.5
218036993 | N/A | DAIKIN | HMSV-A-CB | RXYA120AAYD* |  |  |  | RXYA120AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.1 | 21.4 | 114000 | 3.4 | 82000 | 2.25 | R-32 | 9.5
218037009 | N/A | DAIKIN | HMSR-A-CB | REYA72AATJ* |  |  |  | REYA72AATJ* | Non-Ducted Indoor Units | 69000 | 12.5 | 23.6 | 69000 | 3.8 | 51000 | 2.4 | R-32 | 5.75
218037045 | N/A | DAIKIN | HMSR-A-CB | REYA72AATJ* |  |  |  | REYA72AATJ* | Ducted Indoor Units | 69000 | 12.4 | 21.2 | 69000 | 3.6 | 51000 | 2.4 | R-32 | 5.75
218037081 | N/A | DAIKIN | HMSR-A-CB | REYA72AATJ* |  |  |  | REYA72AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.45 | 22.4 | 69000 | 3.7 | 51000 | 2.4 | R-32 | 5.75
218037082 | N/A | DAIKIN | HMSR-A-CB | REYA96AATJ* |  |  |  | REYA96AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 22.7 | 92000 | 3.7 | 72000 | 2.27 | R-32 | 7.6667
218037046 | N/A | DAIKIN | HMSR-A-CB | REYA96AATJ* |  |  |  | REYA96AATJ* | Ducted Indoor Units | 92000 | 12 | 21.2 | 92000 | 3.6 | 72000 | 2.25 | R-32 | 7.6667
218037010 | N/A | DAIKIN | HMSR-A-CB | REYA96AATJ* |  |  |  | REYA96AATJ* | Non-Ducted Indoor Units | 92000 | 12.2 | 24.2 | 92000 | 3.8 | 72000 | 2.3 | R-32 | 7.6667
218037011 | N/A | DAIKIN | HMSR-A-CB | REYA120AATJ* |  |  |  | REYA120AATJ* | Non-Ducted Indoor Units | 114000 | 11.1 | 23 | 114000 | 3.5 | 82000 | 2.25 | R-32 | 9.5
218037047 | N/A | DAIKIN | HMSR-A-CB | REYA120AATJ* |  |  |  | REYA120AATJ* | Ducted Indoor Units | 114000 | 11.1 | 20.2 | 114000 | 3.5 | 82000 | 2.25 | R-32 | 9.5
218037083 | N/A | DAIKIN | HMSR-A-CB | REYA120AATJ* |  |  |  | REYA120AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.1 | 21.6 | 114000 | 3.5 | 82000 | 2.25 | R-32 | 9.5
218037063 | N/A | DAIKIN | HMSR-A-CB | REYA72AAYD* |  |  |  | REYA72AAYD* | Ducted Indoor Units | 69000 | 12.4 | 21.2 | 69000 | 3.6 | 51000 | 2.4 | R-32 | 5.75
218037027 | N/A | DAIKIN | HMSR-A-CB | REYA72AAYD* |  |  |  | REYA72AAYD* | Non-Ducted Indoor Units | 69000 | 12.5 | 23.6 | 69000 | 3.8 | 51000 | 2.4 | R-32 | 5.75
218037099 | N/A | DAIKIN | HMSR-A-CB | REYA72AAYD* |  |  |  | REYA72AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.45 | 22.4 | 69000 | 3.7 | 51000 | 2.4 | R-32 | 5.75
218037100 | N/A | DAIKIN | HMSR-A-CB | REYA96AAYD* |  |  |  | REYA96AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 22.7 | 92000 | 3.7 | 72000 | 2.27 | R-32 | 7.6667
218037028 | N/A | DAIKIN | HMSR-A-CB | REYA96AAYD* |  |  |  | REYA96AAYD* | Non-Ducted Indoor Units | 92000 | 12.2 | 24.2 | 92000 | 3.8 | 72000 | 2.3 | R-32 | 7.6667
218037064 | N/A | DAIKIN | HMSR-A-CB | REYA96AAYD* |  |  |  | REYA96AAYD* | Ducted Indoor Units | 92000 | 12 | 21.2 | 92000 | 3.6 | 72000 | 2.25 | R-32 | 7.6667
218037065 | N/A | DAIKIN | HMSR-A-CB | REYA120AAYD* |  |  |  | REYA120AAYD* | Ducted Indoor Units | 114000 | 11.1 | 20.2 | 114000 | 3.5 | 82000 | 2.25 | R-32 | 9.5
218037029 | N/A | DAIKIN | HMSR-A-CB | REYA120AAYD* |  |  |  | REYA120AAYD* | Non-Ducted Indoor Units | 114000 | 11.1 | 23 | 114000 | 3.5 | 82000 | 2.25 | R-32 | 9.5
218037101 | N/A | DAIKIN | HMSR-A-CB | REYA120AAYD* |  |  |  | REYA120AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.1 | 21.6 | 114000 | 3.5 | 82000 | 2.25 | R-32 | 9.5
213886360 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH |  |  |  | AM096BXVTFH | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
213886432 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH |  |  |  | AM096BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886392 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH |  |  |  | AM096BXVTFH | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
216602243 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y |  |  |  | VPC096L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
216602117 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y |  |  |  | VPC096L4M-4Y | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
216602170 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y |  |  |  | VPC096L4M-4Y | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
216602177 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4Y |  |  |  | VPC120L4M-4Y | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
216602124 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4Y |  |  |  | VPC120L4M-4Y | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602253 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4Y |  |  |  | VPC120L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886396 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTFH |  |  |  | AM120BXVTFH | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
213886436 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTFH |  |  |  | AM120BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886364 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTFH |  |  |  | AM120BXVTFH | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
213886358 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH |  |  |  | AM072BXVTJH | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
213886430 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH |  |  |  | AM072BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886390 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH |  |  |  | AM072BXVTJH | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602237 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G |  |  |  | VPC072L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
216602113 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G |  |  |  | VPC072L4M-4G | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
216602167 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G |  |  |  | VPC072L4M-4G | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602173 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G |  |  |  | VPC096L4M-4G | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
216602120 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G |  |  |  | VPC096L4M-4G | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
216602248 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G |  |  |  | VPC096L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886394 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH |  |  |  | AM096BXVTJH | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
213886434 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH |  |  |  | AM096BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886362 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH |  |  |  | AM096BXVTJH | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
213886366 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTJH |  |  |  | AM120BXVTJH | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
213886438 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTJH |  |  |  | AM120BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886398 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTJH |  |  |  | AM120BXVTJH | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
216602258 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4G |  |  |  | VPC120L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
216602127 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4G |  |  |  | VPC120L4M-4G | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602180 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120L4M-4G |  |  |  | VPC120L4M-4G | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
216602166 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y |  |  |  | VRC072L4M-4Y | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602111 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y |  |  |  | VRC072L4M-4Y | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
216602235 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y |  |  |  | VRC072L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886389 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR |  |  |  | AM072BXVTFR | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
213886429 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR |  |  |  | AM072BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886357 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR |  |  |  | AM072BXVTFR | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
213886361 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR |  |  |  | AM096BXVTFR | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
213886433 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR |  |  |  | AM096BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886393 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR |  |  |  | AM096BXVTFR | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
216602246 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y |  |  |  | VRC096L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
216602119 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y |  |  |  | VRC096L4M-4Y | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
216602172 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y |  |  |  | VRC096L4M-4Y | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
216602179 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4Y |  |  |  | VRC120L4M-4Y | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
216602126 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4Y |  |  |  | VRC120L4M-4Y | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602256 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4Y |  |  |  | VRC120L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886397 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTFR |  |  |  | AM120BXVTFR | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
213886437 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTFR |  |  |  | AM120BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886365 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTFR |  |  |  | AM120BXVTFR | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
213886359 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR |  |  |  | AM072BXVTJR | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
213886431 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR |  |  |  | AM072BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886391 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR |  |  |  | AM072BXVTJR | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602240 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G |  |  |  | VRC072L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
216602115 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G |  |  |  | VRC072L4M-4G | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
216602169 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G |  |  |  | VRC072L4M-4G | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602175 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G |  |  |  | VRC096L4M-4G | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
216602122 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G |  |  |  | VRC096L4M-4G | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
216602251 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G |  |  |  | VRC096L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886395 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR |  |  |  | AM096BXVTJR | Non-Ducted Indoor Units | 92000 | 13.4 | 28 | 103000 | 4.06 | 103000 | 2.49 | R-410A | 7.6667
213886435 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR |  |  |  | AM096BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.12 | 26.55 | 103000 | 4 | 103000 | 2.48 | R-410A | 7.6667
213886363 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR |  |  |  | AM096BXVTJR | Ducted Indoor Units | 92000 | 12.85 | 25.1 | 103000 | 3.94 | 103000 | 2.47 | R-410A | 7.6667
213886367 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTJR |  |  |  | AM120BXVTJR | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
213886439 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTJR |  |  |  | AM120BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
213886399 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTJR |  |  |  | AM120BXVTJR | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
216602260 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4G |  |  |  | VRC120L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.32 | 25.7 | 129000 | 3.95 | 129000 | 2.28 | R-410A | 9.5
216602129 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4G |  |  |  | VRC120L4M-4G | Ducted Indoor Units | 114000 | 12.65 | 24.9 | 129000 | 3.92 | 129000 | 2.32 | R-410A | 9.5
216602182 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120L4M-4G |  |  |  | VRC120L4M-4G | Non-Ducted Indoor Units | 114000 | 12 | 26.5 | 129000 | 3.98 | 129000 | 2.25 | R-410A | 9.5
216602164 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y |  |  |  | VPC072L4M-4Y | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
216602108 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y |  |  |  | VPC072L4M-4Y | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
216602232 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y |  |  |  | VPC072L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886388 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH |  |  |  | AM072BXVTFH | Non-Ducted Indoor Units | 69000 | 13.1 | 28.3 | 77000 | 4.3 | 77000 | 2.58 | R-410A | 5.75
213886428 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH |  |  |  | AM072BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 26 | 77000 | 4.22 | 77000 | 2.52 | R-410A | 5.75
213886356 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH |  |  |  | AM072BXVTFH | Ducted Indoor Units | 69000 | 12.7 | 23.7 | 77000 | 4.14 | 77000 | 2.46 | R-410A | 5.75
208758264 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-072URB |  |  |  | CHV6-072URB | Ducted Indoor Units | 69000 | 11.4 | 21.9 | 75000 | 3.4 | 52500 | 2.25 | R-410A | 5.75
208758265 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-072URB |  |  |  | CHV6-072URB | Non-Ducted Indoor Units | 69000 | 13.9 | 29.1 | 75000 | 4.03 | 52500 | 2.61 | R-410A | 5.75
208758266 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-072URB |  |  |  | CHV6-072URB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.65 | 25.5 | 75000 | 3.71 | 52500 | 2.43 | R-410A | 5.75
210135408 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 72FFFH |  |  |  | AVWT - 72FFFH | Ducted Indoor Units | 69000 | 11.4 | 21.9 | 75000 | 3.4 | 52500 | 2.25 | R-410A | 5.75
210135420 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 72FFFH |  |  |  | AVWT - 72FFFH | Non-Ducted Indoor Units | 69000 | 13.9 | 29.1 | 75000 | 4.03 | 52500 | 2.61 | R-410A | 5.75
210135423 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 72FFFH |  |  |  | AVWT - 72FFFH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.65 | 25.5 | 75000 | 3.71 | 52500 | 2.43 | R-410A | 5.75
210135424 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 96FFFH |  |  |  | AVWT - 96FFFH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 25.75 | 100000 | 3.74 | 70000 | 2.44 | R-410A | 7.6667
210135409 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 96FFFH |  |  |  | AVWT - 96FFFH | Ducted Indoor Units | 92000 | 11.1 | 21.8 | 100000 | 3.51 | 70000 | 2.32 | R-410A | 7.6667
210135410 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 96FFFH |  |  |  | AVWT - 96FFFH | Non-Ducted Indoor Units | 92000 | 13.2 | 29.7 | 100000 | 3.98 | 70000 | 2.57 | R-410A | 7.6667
208758267 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB |  |  |  | CHV6-096URB | Ducted Indoor Units | 92000 | 11.1 | 21.8 | 100000 | 3.51 | 70000 | 2.32 | R-410A | 7.6667
208758268 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB |  |  |  | CHV6-096URB | Non-Ducted Indoor Units | 92000 | 13.2 | 29.7 | 100000 | 3.98 | 70000 | 2.57 | R-410A | 7.6667
208758269 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB |  |  |  | CHV6-096URB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 25.75 | 100000 | 3.74 | 70000 | 2.44 | R-410A | 7.6667
208758270 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB |  |  |  | CHV6-120URB | Ducted Indoor Units | 114000 | 11.1 | 21.6 | 126000 | 3.42 | 81000 | 2.32 | R-410A | 9.5
208758271 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB |  |  |  | CHV6-120URB | Non-Ducted Indoor Units | 114000 | 13 | 29.4 | 126000 | 4.17 | 81000 | 2.73 | R-410A | 9.5
210135411 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 120FFFH |  |  |  | AVWT - 120FFFH | Ducted Indoor Units | 114000 | 11.1 | 21.6 | 126000 | 3.42 | 81000 | 2.32 | R-410A | 9.5
210135412 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 120FFFH |  |  |  | AVWT - 120FFFH | Non-Ducted Indoor Units | 114000 | 13 | 29.4 | 126000 | 4.17 | 81000 | 2.73 | R-410A | 9.5
210135425 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 120FFFH |  |  |  | AVWT - 120FFFH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.05 | 25.5 | 126000 | 3.79 | 81000 | 2.52 | R-410A | 9.5
213897015 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AATJ* |  |  |  | RXYQ72AATJ* | Non-Ducted Indoor Units | 69000 | 12.5 | 23.2 | 69000 | 3.64 | 51000 | 2.4 | R-410A | 5.75
213897041 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AATJ* |  |  |  | RXYQ72AATJ* | Ducted Indoor Units | 69000 | 12.2 | 19.8 | 69000 | 3.6 | 51000 | 2.4 | R-410A | 5.75
213897059 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AATJ* |  |  |  | RXYQ72AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.35 | 21.5 | 69000 | 3.62 | 51000 | 2.4 | R-410A | 5.75
213897060 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AATJ* |  |  |  | RXYQ96AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 21.5 | 92000 | 3.45 | 66000 | 2.4 | R-410A | 7.6667
213897042 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AATJ* |  |  |  | RXYQ96AATJ* | Ducted Indoor Units | 92000 | 12 | 19.4 | 92000 | 3.4 | 66000 | 2.4 | R-410A | 7.6667
213897016 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AATJ* |  |  |  | RXYQ96AATJ* | Non-Ducted Indoor Units | 92000 | 12.2 | 23.6 | 92000 | 3.5 | 66000 | 2.4 | R-410A | 7.6667
213897043 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AATJ* |  |  |  | RXYQ120AATJ* | Ducted Indoor Units | 114000 | 11.1 | 19.3 | 110000 | 3.4 | 72000 | 2.25 | R-410A | 9.5
213897028 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AAYD* |  |  |  | RXYQ72AAYD* | Non-Ducted Indoor Units | 69000 | 12.5 | 23.2 | 69000 | 3.64 | 51000 | 2.4 | R-410A | 5.75
213897068 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AAYD* |  |  |  | RXYQ72AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.35 | 21.5 | 69000 | 3.62 | 51000 | 2.4 | R-410A | 5.75
213897050 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72AAYD* |  |  |  | RXYQ72AAYD* | Ducted Indoor Units | 69000 | 12.2 | 19.8 | 69000 | 3.6 | 51000 | 2.4 | R-410A | 5.75
213897051 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AAYD* |  |  |  | RXYQ96AAYD* | Ducted Indoor Units | 92000 | 12 | 19.4 | 92000 | 3.4 | 66000 | 2.4 | R-410A | 7.6667
213897069 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AAYD* |  |  |  | RXYQ96AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 21.5 | 92000 | 3.45 | 66000 | 2.4 | R-410A | 7.6667
213897029 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96AAYD* |  |  |  | RXYQ96AAYD* | Non-Ducted Indoor Units | 92000 | 12.2 | 23.6 | 92000 | 3.5 | 66000 | 2.4 | R-410A | 7.6667
213897052 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AAYD* |  |  |  | RXYQ120AAYD* | Ducted Indoor Units | 114000 | 11.1 | 19.3 | 110000 | 3.4 | 72000 | 2.25 | R-410A | 9.5
213885856 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-F(U) |  |  |  | GMV-VQ72WM/C-F(U) | Ducted Indoor Units | 69000 | 11.4 | 21 | 77000 | 4 | 68000 | 2.25 | R-410A | 5.75
213885853 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-F(U) |  |  |  | GMV-VQ72WM/C-F(U) | Non-Ducted Indoor Units | 69000 | 11.8 | 23.8 | 77000 | 4.4 | 68000 | 2.25 | R-410A | 5.75
215685126 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-F(U) |  |  |  | GMV-VQ72WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.6 | 22.4 | 77000 | 4.2 | 68000 | 2.25 | R-410A | 5.75
215685127 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-F(U) |  |  |  | GMV-VQ96WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.8 | 20.55 | 103000 | 3.95 | 76000 | 2.25 | R-410A | 7.6667
213885857 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-F(U) |  |  |  | GMV-VQ96WM/C-F(U) | Ducted Indoor Units | 92000 | 11.6 | 20.2 | 103000 | 3.9 | 78000 | 2.25 | R-410A | 7.6667
213885858 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ120WM/C-F(U) |  |  |  | GMV-VQ120WM/C-F(U) | Ducted Indoor Units | 114000 | 11 | 19.7 | 129000 | 3.8 | 81000 | 2.25 | R-410A | 9.5
215685128 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ120WM/C-F(U) |  |  |  | GMV-VQ120WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 10.5 | 20.05 | 129000 | 3.87 | 81000 | 2.25 | R-410A | 9.5
214728275 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP072C432Y2 |  |  |  | VEP072C432Y2 | Ducted Indoor Units | 69000 | 11.2 | 20.4 | 77000 | 3.68 | 66000 | 2.25 | R-410A | 5.75
215685129 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP072C432Y2 |  |  |  | VEP072C432Y2 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 10.72 | 20.8 | 77000 | 3.81 | 64000 | 2.25 | R-410A | 5.75
215685121 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q72WM/C-F(U) |  |  |  | GMV-Q72WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 10.72 | 20.8 | 77000 | 3.81 | 64000 | 2.25 | R-410A | 5.75
213880759 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q72WM/C-F(U) |  |  |  | GMV-Q72WM/C-F(U) | Ducted Indoor Units | 69000 | 11.2 | 20.4 | 77000 | 3.68 | 66000 | 2.25 | R-410A | 5.75
213928536 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/C-F(U) |  |  |  | GMV-Q96WM/C-F(U) | Ducted Indoor Units | 92000 | 11 | 22.2 | 103000 | 3.8 | 75000 | 2.25 | R-410A | 7.6667
215685122 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/C-F(U) |  |  |  | GMV-Q96WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.45 | 21.75 | 103000 | 3.9 | 75000 | 2.25 | R-410A | 7.6667
215685130 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP096C432Y2 |  |  |  | VEP096C432Y2 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.45 | 21.75 | 103000 | 3.9 | 75000 | 2.25 | R-410A | 7.6667
214728280 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP096C432Y2 |  |  |  | VEP096C432Y2 | Ducted Indoor Units | 92000 | 11 | 22.2 | 103000 | 3.8 | 75000 | 2.25 | R-410A | 7.6667
213686135 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FLFSH |  |  |  | AVWT-72FLFSH | Ducted Indoor Units | 69000 | 11.4 | 21.9 | 75000 | 3.4 | 52500 | 2.25 | R-410A | 5.75
213686136 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FLFSH |  |  |  | AVWT-72FLFSH | Non-Ducted Indoor Units | 69000 | 13.9 | 29.1 | 75000 | 4.03 | 52500 | 2.61 | R-410A | 5.75
213686137 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FLFSH |  |  |  | AVWT-72FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.65 | 25.5 | 75000 | 3.71 | 52500 | 2.43 | R-410A | 5.75
213686138 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH |  |  |  | AVWT-96FLFSH | Ducted Indoor Units | 92000 | 11.1 | 21.8 | 100000 | 3.51 | 70000 | 2.32 | R-410A | 7.6667
213686139 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH |  |  |  | AVWT-96FLFSH | Non-Ducted Indoor Units | 92000 | 13.2 | 29.7 | 100000 | 3.98 | 70000 | 2.57 | R-410A | 7.6667
213686140 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH |  |  |  | AVWT-96FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 25.75 | 100000 | 3.74 | 70000 | 2.44 | R-410A | 7.6667
213686141 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH |  |  |  | AVWT-120FLFSH | Ducted Indoor Units | 114000 | 11.1 | 21.6 | 126000 | 3.42 | 81000 | 2.32 | R-410A | 9.5
213686142 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH |  |  |  | AVWT-120FLFSH | Non-Ducted Indoor Units | 114000 | 13 | 29.4 | 126000 | 4.17 | 81000 | 2.73 | R-410A | 9.5
213686143 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH |  |  |  | AVWT-120FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.05 | 25.5 | 126000 | 3.79 | 81000 | 2.52 | R-410A | 9.5
213893629 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 |  |  |  | PUHY-P72TNU-A1 | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213894863 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 |  |  |  | PUHY-P72TNU-A1 | Ducted Indoor Units | 69000 | 10.9 | 21.6 | 76000 | 3.97 | 56000 | 2.46 | R-410A | 5.75
213916540 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 |  |  |  | PUHY-P72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213916555 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 |  |  |  | PUHY-P72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213894865 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 |  |  |  | PUHY-P72YNU-A1 | Ducted Indoor Units | 69000 | 10.9 | 21.6 | 76000 | 3.97 | 56000 | 2.46 | R-410A | 5.75
213893631 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 |  |  |  | PUHY-P72YNU-A1 | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213893634 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 |  |  |  | PUHY-P96TNU-A1 | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893635 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 |  |  |  | PUHY-P96TNU-A1 | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213916541 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 |  |  |  | PUHY-P96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213916556 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 |  |  |  | PUHY-P96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213893638 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 |  |  |  | PUHY-P96YNU-A1 | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893639 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 |  |  |  | PUHY-P96YNU-A1 | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213894867 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 |  |  |  | PUHY-P120TNU-A1 | Ducted Indoor Units | 115000 | 10.3 | 20.6 | 129000 | 3.7 | 92000 | 2.38 | R-410A | 9.5833
213894875 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 |  |  |  | PUHY-P120TNU-A1 | Non-Ducted Indoor Units | 115000 | 10.4 | 21.6 | 129000 | 4.05 | 92000 | 2.59 | R-410A | 9.5833
213916542 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 |  |  |  | PUHY-P120TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.35 | 21.1 | 129000 | 3.87 | 92000 | 2.48 | R-410A | 9.5833
213916557 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 |  |  |  | PUHY-P120YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.35 | 21.1 | 129000 | 3.87 | 92000 | 2.48 | R-410A | 9.5833
213894877 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 |  |  |  | PUHY-P120YNU-A1 | Non-Ducted Indoor Units | 115000 | 10.4 | 21.6 | 129000 | 4.05 | 92000 | 2.59 | R-410A | 9.5833
213894869 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 |  |  |  | PUHY-P120YNU-A1 | Ducted Indoor Units | 115000 | 10.3 | 20.6 | 129000 | 3.7 | 92000 | 2.38 | R-410A | 9.5833
213893524 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 |  |  |  | PUHY-EP72TNU-A1 | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893525 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 |  |  |  | PUHY-EP72TNU-A1 | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213916490 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 |  |  |  | PUHY-EP72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213916509 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 |  |  |  | PUHY-EP72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213893528 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 |  |  |  | PUHY-EP72YNU-A1 | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893529 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 |  |  |  | PUHY-EP72YNU-A1 | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213893532 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 |  |  |  | PUHY-EP96TNU-A1 | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893533 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 |  |  |  | PUHY-EP96TNU-A1 | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916491 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 |  |  |  | PUHY-EP96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213916510 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 |  |  |  | PUHY-EP96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213893536 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 |  |  |  | PUHY-EP96YNU-A1 | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893537 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 |  |  |  | PUHY-EP96YNU-A1 | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916492 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 |  |  |  | PUHY-EP120TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.8 | 23.35 | 129000 | 4 | 116000 | 2.38 | R-410A | 9.5833
213894871 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 |  |  |  | PUHY-EP120TNU-A1 | Ducted Indoor Units | 115000 | 10.7 | 21.9 | 129000 | 3.8 | 116000 | 2.27 | R-410A | 9.5833
213894879 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 |  |  |  | PUHY-EP120TNU-A1 | Non-Ducted Indoor Units | 115000 | 10.9 | 24.8 | 129000 | 4.21 | 116000 | 2.5 | R-410A | 9.5833
213894881 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 |  |  |  | PUHY-EP120YNU-A1 | Non-Ducted Indoor Units | 115000 | 10.9 | 24.8 | 129000 | 4.21 | 116000 | 2.5 | R-410A | 9.5833
213894873 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 |  |  |  | PUHY-EP120YNU-A1 | Ducted Indoor Units | 115000 | 10.7 | 21.9 | 129000 | 3.8 | 116000 | 2.27 | R-410A | 9.5833
213916511 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 |  |  |  | PUHY-EP120YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.8 | 23.35 | 129000 | 4 | 116000 | 2.38 | R-410A | 9.5833
213916528 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 |  |  |  | PUHY-HP72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213893828 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 |  |  |  | PUHY-HP72TNU-A1 | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213893825 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 |  |  |  | PUHY-HP72TNU-A1 | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893826 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 |  |  |  | PUHY-HP72YNU-A1 | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893829 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 |  |  |  | PUHY-HP72YNU-A1 | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213916534 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 |  |  |  | PUHY-HP72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213916530 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 |  |  |  | PUHY-HP120TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213893540 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 |  |  |  | PUHY-HP120TNU-A1 | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893541 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 |  |  |  | PUHY-HP120TNU-A1 | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893544 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 |  |  |  | PUHY-HP120YNU-A1 | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893545 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 |  |  |  | PUHY-HP120YNU-A1 | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213916536 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 |  |  |  | PUHY-HP120YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213893770 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN |  |  |  | TUHYE0723AN41AN | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893771 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN |  |  |  | TUHYE0723AN41AN | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213916699 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN |  |  |  | TUHYE0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213916701 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN |  |  |  | TUHYE0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213893772 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN |  |  |  | TUHYE0724AN41AN | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213893859 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN |  |  |  | TUHYE0724AN41AN | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893773 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN |  |  |  | TUHYE0963AN41AN | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893774 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN |  |  |  | TUHYE0963AN41AN | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916703 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN |  |  |  | TUHYE0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213916705 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN |  |  |  | TUHYE0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213893775 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN |  |  |  | TUHYE0964AN41AN | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893776 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN |  |  |  | TUHYE0964AN41AN | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213894966 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN |  |  |  | TUHYE1203AN41AN | Ducted Indoor Units | 115000 | 10.7 | 21.9 | 129000 | 3.8 | 116000 | 2.27 | R-410A | 9.5833
213894967 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN |  |  |  | TUHYE1203AN41AN | Non-Ducted Indoor Units | 115000 | 10.9 | 24.8 | 129000 | 4.21 | 116000 | 2.5 | R-410A | 9.5833
213916707 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN |  |  |  | TUHYE1203AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.8 | 23.35 | 129000 | 4 | 116000 | 2.38 | R-410A | 9.5833
213916709 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN |  |  |  | TUHYE1204AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.8 | 23.35 | 129000 | 4 | 116000 | 2.38 | R-410A | 9.5833
213894968 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN |  |  |  | TUHYE1204AN41AN | Ducted Indoor Units | 115000 | 10.7 | 21.9 | 129000 | 3.8 | 116000 | 2.27 | R-410A | 9.5833
213894969 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN |  |  |  | TUHYE1204AN41AN | Non-Ducted Indoor Units | 115000 | 10.9 | 24.8 | 129000 | 4.21 | 116000 | 2.5 | R-410A | 9.5833
213893777 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH1203AN41AN | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893778 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH1203AN41AN | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893787 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0963AN41AN | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893788 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0963AN41AN | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213893854 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0723AN41AN | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893855 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0723AN41AN | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213916773 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213916777 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213916781 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN |  |  |  | TUHYH1203AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213916775 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN |  |  |  | TUHYH0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213893856 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN |  |  |  | TUHYH0724AN41AN | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213893860 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN |  |  |  | TUHYH0724AN41AN | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213916779 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN |  |  |  | TUHYH0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213893789 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN |  |  |  | TUHYH0964AN41AN | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893790 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN |  |  |  | TUHYH0964AN41AN | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213916783 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN |  |  |  | TUHYH1204AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213893779 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN |  |  |  | TUHYH1204AN41AN | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893780 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN |  |  |  | TUHYH1204AN41AN | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893857 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN |  |  |  | TUHYP0723AN41AN | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213894883 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN |  |  |  | TUHYP0723AN41AN | Ducted Indoor Units | 69000 | 10.9 | 21.6 | 76000 | 3.97 | 56000 | 2.46 | R-410A | 5.75
213916794 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN |  |  |  | TUHYP0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213916796 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN |  |  |  | TUHYP0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213894957 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN |  |  |  | TUHYP0724AN41AN | Ducted Indoor Units | 69000 | 10.9 | 21.6 | 76000 | 3.97 | 56000 | 2.46 | R-410A | 5.75
213893858 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN |  |  |  | TUHYP0724AN41AN | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213893821 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN |  |  |  | TUHYP0963AN41AN | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893822 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN |  |  |  | TUHYP0963AN41AN | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213916798 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN |  |  |  | TUHYP0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213916800 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN |  |  |  | TUHYP0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213893823 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN |  |  |  | TUHYP0964AN41AN | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893824 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN |  |  |  | TUHYP0964AN41AN | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213894990 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN |  |  |  | TUHYP1203AN41AN | Ducted Indoor Units | 115000 | 10.3 | 20.6 | 129000 | 3.7 | 92000 | 2.38 | R-410A | 9.5833
213894991 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN |  |  |  | TUHYP1203AN41AN | Non-Ducted Indoor Units | 115000 | 10.4 | 21.6 | 129000 | 4.05 | 92000 | 2.59 | R-410A | 9.5833
213916802 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN |  |  |  | TUHYP1203AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.35 | 21.1 | 129000 | 3.87 | 92000 | 2.48 | R-410A | 9.5833
213916804 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN |  |  |  | TUHYP1204AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.35 | 21.1 | 129000 | 3.87 | 92000 | 2.48 | R-410A | 9.5833
213894992 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN |  |  |  | TUHYP1204AN41AN | Ducted Indoor Units | 115000 | 10.3 | 20.6 | 129000 | 3.7 | 92000 | 2.38 | R-410A | 9.5833
213894993 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN |  |  |  | TUHYP1204AN41AN | Non-Ducted Indoor Units | 115000 | 10.4 | 21.6 | 129000 | 4.05 | 92000 | 2.59 | R-410A | 9.5833
213916529 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 |  |  |  | PUHY-HP96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213893562 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 |  |  |  | PUHY-HP96TNU-A1 | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893563 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 |  |  |  | PUHY-HP96TNU-A1 | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213893566 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 |  |  |  | PUHY-HP96YNU-A1 | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893567 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 |  |  |  | PUHY-HP96YNU-A1 | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213916535 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 |  |  |  | PUHY-HP96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213896102 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72YNU-A1 |  |  |  | PURY-EP72YNU-A1 | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213895982 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72YNU-A1 |  |  |  | PURY-EP72YNU-A1 | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
214050138 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72YNU-A1 |  |  |  | PURY-EP72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 22.85 | 76000 | 4.09 | 61000 | 2.27 | R-410A | 5.75
214050142 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A1 |  |  |  | PURY-EP96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.85 | 23.35 | 103000 | 4.1 | 79000 | 2.27 | R-410A | 7.6667
213896106 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A1 |  |  |  | PURY-EP96YNU-A1 | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896658 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120YNU-A1 |  |  |  | PURY-EP120YNU-A1 | Non-Ducted Indoor Units | 115000 | 10.6 | 23 | 129000 | 4.04 | 93000 | 2.3 | R-410A | 9.5833
214050078 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120YNU-A1 |  |  |  | PURY-EP120YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.5 | 22.35 | 129000 | 3.87 | 93000 | 2.27 | R-410A | 9.5833
213896100 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72TNU-A1 |  |  |  | PURY-EP72TNU-A1 | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213895980 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72TNU-A1 |  |  |  | PURY-EP72TNU-A1 | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
214050136 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72TNU-A1 |  |  |  | PURY-EP72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 22.85 | 76000 | 4.09 | 61000 | 2.27 | R-410A | 5.75
214050140 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A1 |  |  |  | PURY-EP96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.85 | 23.35 | 103000 | 4.1 | 79000 | 2.27 | R-410A | 7.6667
213896104 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A1 |  |  |  | PURY-EP96TNU-A1 | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896656 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120TNU-A1 |  |  |  | PURY-EP120TNU-A1 | Non-Ducted Indoor Units | 115000 | 10.6 | 23 | 129000 | 4.04 | 93000 | 2.3 | R-410A | 9.5833
214050076 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120TNU-A1 |  |  |  | PURY-EP120TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.5 | 22.35 | 129000 | 3.87 | 93000 | 2.27 | R-410A | 9.5833
213895998 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 |  |  |  | PURY-HP72YNU-A1 | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896130 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 |  |  |  | PURY-HP72YNU-A1 | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
214050162 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 |  |  |  | PURY-HP72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 22.25 | 76000 | 3.92 | 64000 | 2.28 | R-410A | 5.75
214050166 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 |  |  |  | PURY-HP96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.8 | 21.75 | 103000 | 4.01 | 87000 | 2.27 | R-410A | 7.6667
213896134 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 |  |  |  | PURY-HP96YNU-A1 | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
213896002 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 |  |  |  | PURY-HP96YNU-A1 | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896662 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP120YNU-A1 |  |  |  | PURY-HP120YNU-A1 | Non-Ducted Indoor Units | 115000 | 10.7 | 22 | 129000 | 4.01 | 93000 | 2.3 | R-410A | 9.5833
214050146 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP120YNU-A1 |  |  |  | PURY-HP120YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.55 | 20.95 | 129000 | 3.81 | 93000 | 2.27 | R-410A | 9.5833
214050160 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 |  |  |  | PURY-HP72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 22.25 | 76000 | 3.92 | 64000 | 2.28 | R-410A | 5.75
213895996 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 |  |  |  | PURY-HP72TNU-A1 | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896127 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 |  |  |  | PURY-HP72TNU-A1 | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213896132 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 |  |  |  | PURY-HP96TNU-A1 | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
213896000 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 |  |  |  | PURY-HP96TNU-A1 | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
214050164 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 |  |  |  | PURY-HP96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.8 | 21.75 | 103000 | 4.01 | 87000 | 2.27 | R-410A | 7.6667
214050144 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP120TNU-A1 |  |  |  | PURY-HP120TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.55 | 20.95 | 129000 | 3.81 | 93000 | 2.27 | R-410A | 9.5833
213896660 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP120TNU-A1 |  |  |  | PURY-HP120TNU-A1 | Non-Ducted Indoor Units | 115000 | 10.7 | 22 | 129000 | 4.01 | 93000 | 2.3 | R-410A | 9.5833
213896014 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YNU-A1 |  |  |  | PURY-P72YNU-A1 | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896150 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YNU-A1 |  |  |  | PURY-P72YNU-A1 | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
214050210 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YNU-A1 |  |  |  | PURY-P72YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.65 | 22.3 | 76000 | 3.92 | 56000 | 2.26 | R-410A | 5.75
214050214 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A1 |  |  |  | PURY-P96YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.3 | 23 | 103000 | 4.01 | 71000 | 2.25 | R-410A | 7.6667
213896154 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A1 |  |  |  | PURY-P96YNU-A1 | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896666 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YNU-A1 |  |  |  | PURY-P120YNU-A1 | Non-Ducted Indoor Units | 115000 | 10.3 | 21.5 | 129000 | 4.01 | 87000 | 2.26 | R-410A | 9.5833
214050208 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TNU-A1 |  |  |  | PURY-P72TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.65 | 22.3 | 76000 | 3.92 | 56000 | 2.26 | R-410A | 5.75
213896148 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TNU-A1 |  |  |  | PURY-P72TNU-A1 | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896012 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TNU-A1 |  |  |  | PURY-P72TNU-A1 | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896152 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A1 |  |  |  | PURY-P96TNU-A1 | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
214050212 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A1 |  |  |  | PURY-P96TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.3 | 23 | 103000 | 4.01 | 71000 | 2.25 | R-410A | 7.6667
213896664 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TNU-A1 |  |  |  | PURY-P120TNU-A1 | Non-Ducted Indoor Units | 115000 | 10.3 | 21.5 | 129000 | 4.01 | 87000 | 2.26 | R-410A | 9.5833
213896022 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AN41AN |  |  |  | TURYE0724AN41AN | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896158 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AN41AN |  |  |  | TURYE0724AN41AN | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
214050284 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AN41AN |  |  |  | TURYE0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 22.85 | 76000 | 4.09 | 61000 | 2.27 | R-410A | 5.75
214050288 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN41AN |  |  |  | TURYE0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.85 | 23.35 | 103000 | 4.1 | 79000 | 2.27 | R-410A | 7.6667
213896162 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN41AN |  |  |  | TURYE0964AN41AN | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896670 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AN41AN |  |  |  | TURYE1204AN41AN | Non-Ducted Indoor Units | 115000 | 10.6 | 23 | 129000 | 4.04 | 93000 | 2.3 | R-410A | 9.5833
214050292 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AN41AN |  |  |  | TURYE1204AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.5 | 22.35 | 129000 | 3.87 | 93000 | 2.27 | R-410A | 9.5833
213896156 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AN41AN |  |  |  | TURYE0723AN41AN | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213896020 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AN41AN |  |  |  | TURYE0723AN41AN | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
214050282 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AN41AN |  |  |  | TURYE0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 22.85 | 76000 | 4.09 | 61000 | 2.27 | R-410A | 5.75
214050286 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN41AN |  |  |  | TURYE0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.85 | 23.35 | 103000 | 4.1 | 79000 | 2.27 | R-410A | 7.6667
213896160 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN41AN |  |  |  | TURYE0963AN41AN | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896668 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AN41AN |  |  |  | TURYE1203AN41AN | Non-Ducted Indoor Units | 115000 | 10.6 | 23 | 129000 | 4.04 | 93000 | 2.3 | R-410A | 9.5833
214050290 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AN41AN |  |  |  | TURYE1203AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.5 | 22.35 | 129000 | 3.87 | 93000 | 2.27 | R-410A | 9.5833
213896190 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN |  |  |  | TURYH0724AN41AN | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213896046 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN |  |  |  | TURYH0724AN41AN | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
214050352 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN |  |  |  | TURYH0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 22.25 | 76000 | 3.92 | 64000 | 2.28 | R-410A | 5.75
214050356 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN |  |  |  | TURYH0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.8 | 21.75 | 103000 | 4.01 | 87000 | 2.27 | R-410A | 7.6667
213896050 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN |  |  |  | TURYH0964AN41AN | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896194 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN |  |  |  | TURYH0964AN41AN | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
213896674 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AN41AN |  |  |  | TURYH1204AN41AN | Non-Ducted Indoor Units | 115000 | 10.7 | 22 | 129000 | 4.01 | 93000 | 2.3 | R-410A | 9.5833
214050360 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AN41AN |  |  |  | TURYH1204AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.55 | 20.95 | 129000 | 3.81 | 93000 | 2.27 | R-410A | 9.5833
214050350 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN |  |  |  | TURYH0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.85 | 22.25 | 76000 | 3.92 | 64000 | 2.28 | R-410A | 5.75
213896188 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN |  |  |  | TURYH0723AN41AN | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213896044 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN |  |  |  | TURYH0723AN41AN | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896048 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN |  |  |  | TURYH0963AN41AN | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896192 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN |  |  |  | TURYH0963AN41AN | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
214050354 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN |  |  |  | TURYH0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.8 | 21.75 | 103000 | 4.01 | 87000 | 2.27 | R-410A | 7.6667
214050358 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AN41AN |  |  |  | TURYH1203AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 10.55 | 20.95 | 129000 | 3.81 | 93000 | 2.27 | R-410A | 9.5833
213896672 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AN41AN |  |  |  | TURYH1203AN41AN | Non-Ducted Indoor Units | 115000 | 10.7 | 22 | 129000 | 4.01 | 93000 | 2.3 | R-410A | 9.5833
213896206 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0724AN41AN |  |  |  | TURYP0724AN41AN | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896062 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0724AN41AN |  |  |  | TURYP0724AN41AN | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
214050376 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0724AN41AN |  |  |  | TURYP0724AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.65 | 22.3 | 76000 | 3.92 | 56000 | 2.26 | R-410A | 5.75
214050380 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN41AN |  |  |  | TURYP0964AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.3 | 23 | 103000 | 4.01 | 71000 | 2.25 | R-410A | 7.6667
213896210 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN41AN |  |  |  | TURYP0964AN41AN | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896678 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1204AN41AN |  |  |  | TURYP1204AN41AN | Non-Ducted Indoor Units | 115000 | 10.3 | 21.5 | 129000 | 4.01 | 87000 | 2.26 | R-410A | 9.5833
214050374 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0723AN41AN |  |  |  | TURYP0723AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.65 | 22.3 | 76000 | 3.92 | 56000 | 2.26 | R-410A | 5.75
213896060 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0723AN41AN |  |  |  | TURYP0723AN41AN | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896204 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0723AN41AN |  |  |  | TURYP0723AN41AN | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896208 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN41AN |  |  |  | TURYP0963AN41AN | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
214050378 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN41AN |  |  |  | TURYP0963AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.3 | 23 | 103000 | 4.01 | 71000 | 2.25 | R-410A | 7.6667
213896676 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1203AN41AN |  |  |  | TURYP1203AN41AN | Non-Ducted Indoor Units | 115000 | 10.3 | 21.5 | 129000 | 4.01 | 87000 | 2.26 | R-410A | 9.5833
9990279 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 |  |  |  | AOUA120RLBV1 | Non-Ducted Indoor Units | 114000 | 11.3 | 23.8 | 129000 | 3.61 | 87000 | 2.43 | R-410A | 9.5
9990277 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 |  |  |  | AOUA72RLBV1 | Non-Ducted Indoor Units | 69000 | 12.5 | 24.1 | 77000 | 4.06 | 56000 | 2.53 | R-410A | 5.75
9990278 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 |  |  |  | AOUA96RLBV1 | Non-Ducted Indoor Units | 92000 | 11.7 | 23.6 | 103000 | 3.72 | 73000 | 2.46 | R-410A | 7.6667
211123650 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 |  |  |  | AOUA96RLBV1 | Ducted Indoor Units | 92000 | 11.3 | 20.2 | 103000 | 3.6 | 73000 | 2.42 | R-410A | 7.6667
213916286 | 1/1/2027 | LG | HMSR-A-CB | ARUM072BTE5 |  |  |  | ARUM072BTE5 | Ducted Indoor Units | 69000 | 10.4 | 18.9 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
213916854 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.15 | 23.35 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
213916284 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Non-Ducted Indoor Units | 92000 | 10.4 | 26.6 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
213916287 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Ducted Indoor Units | 92000 | 11.9 | 20.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
213916288 | 1/1/2027 | LG | HMSR-A-CB | ARUM121BTE5 |  |  |  | ARUM121BTE5 | Ducted Indoor Units | 114000 | 10.3 | 19.1 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
213916309 | 1/1/2027 | LG | HMSR-A-CB | ARUM072DTE5 |  |  |  | ARUM072DTE5 | Ducted Indoor Units | 69000 | 10.4 | 18.9 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
213916862 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.15 | 23.35 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
213916291 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Ducted Indoor Units | 92000 | 11.9 | 20.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
213916289 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Non-Ducted Indoor Units | 92000 | 10.4 | 26.6 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
213916292 | 1/1/2027 | LG | HMSR-A-CB | ARUM121DTE5 |  |  |  | ARUM121DTE5 | Ducted Indoor Units | 114000 | 10.3 | 19.1 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
216699455 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) |  |  |  | GMV-120WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
218043593 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G2 |  |  |  | VEP120C432G2 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
214091436 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091580 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091724 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091581 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091452 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091596 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091740 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091597 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214078203 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091532 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091676 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091533 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091404 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091548 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091692 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091549 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091484 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091628 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091772 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091629 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091500 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091644 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091788 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091645 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214584766 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) |  |  |  | GMV-96WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.5 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
218043596 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G2 |  |  |  | VEP096C432G2 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.5 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
214094178 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094330 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094474 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094331 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094258 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094410 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094554 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094411 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094274 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094426 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094570 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094427 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094506 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094362 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094210 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094363 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094522 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094378 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094226 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094379 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094458 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094314 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094162 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094315 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
202583512 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU96RLAVL |  |  |  | AOU96RLAVL | Non-Ducted Indoor Units | 92000 | 11.6 | 23.1 | 103000 | 3.87 | 73000 | 2.52 | R-410A | 7.6667
202583511 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU72RLAVL |  |  |  | AOU72RLAVL | Non-Ducted Indoor Units | 69000 | 12.1 | 23.9 | 77000 | 4.19 | 56000 | 2.64 | R-410A | 5.75
202583513 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU120RLAVL |  |  |  | AOU120RLAVL | Non-Ducted Indoor Units | 114000 | 11.6 | 24.2 | 129000 | 3.77 | 87000 | 2.42 | R-410A | 9.5
214094242 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094394 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094538 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094395 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B52S |  |  |  | TVAHR096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094346 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094194 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094490 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094347 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B52S |  |  |  | HVAHR096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214094290 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214094442 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214094586 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214094443 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B52S |  |  |  | YVAHR096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091756 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091468 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091612 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091613 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B52S |  |  |  | TVAHP096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091420 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091564 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091708 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091565 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B52S |  |  |  | HVAHP096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
214091804 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.55 | 19.75 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
214091516 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Ducted Indoor Units | 69000 | 12 | 19 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
214091660 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Non-Ducted Indoor Units | 69000 | 13.1 | 20.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
214091661 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B52S |  |  |  | YVAHP096B52S | Non-Ducted Indoor Units | 92000 | 10.8 | 19.6 | 103000 | 3.77 | 72000 | 2.4 | R-410A | 7.6667
213916323 | 1/1/2027 | LG | HMSR-A-CB | ARUM072CTE5 |  |  |  | ARUM072CTE5 | Ducted Indoor Units | 69000 | 10.4 | 18.9 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
213916691 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.15 | 23.35 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
213916324 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Ducted Indoor Units | 92000 | 11.9 | 20.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
213916316 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Non-Ducted Indoor Units | 92000 | 10.4 | 26.6 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
213916325 | 1/1/2027 | LG | HMSR-A-CB | ARUM121CTE5 |  |  |  | ARUM121CTE5 | Ducted Indoor Units | 114000 | 10.3 | 19.1 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
213896312 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72ZKMU-B |  |  |  | PURY-P72ZKMU-B | Non-Ducted Indoor Units | 69000 | 11.4 | 19.8 | 76000 | 3.46 | 56000 | 2.26 | R-410A | 5.75
214050548 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72ZKMU-B |  |  |  | PURY-P72ZKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.35 | 19.1 | 76000 | 3.54 | 56000 | 2.26 | R-410A | 5.75
214050555 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B |  |  |  | PURY-P96ZKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.95 | 19.95 | 103000 | 3.46 | 71000 | 2.26 | R-410A | 7.6667
213896357 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B |  |  |  | PURY-P96ZKMU-B | Ducted Indoor Units | 92000 | 10.9 | 21.1 | 103000 | 3.46 | 71000 | 2.26 | R-410A | 7.6667
213896293 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B |  |  |  | PUHY-P72ZKMU-B | Non-Ducted Indoor Units | 69000 | 12.4 | 22.2 | 76000 | 3.85 | 56000 | 2.25 | R-410A | 5.75
213896282 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B |  |  |  | PUHY-P72ZKMU-B | Ducted Indoor Units | 69000 | 12.3 | 20.2 | 76000 | 3.74 | 56000 | 2.59 | R-410A | 5.75
213916477 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B |  |  |  | PUHY-P72ZKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.35 | 21.2 | 76000 | 3.79 | 56000 | 2.42 | R-410A | 5.75
213916478 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B |  |  |  | PUHY-P96ZKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12 | 21.15 | 103000 | 3.73 | 76000 | 2.56 | R-410A | 7.6667
213896294 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B |  |  |  | PUHY-P96ZKMU-B | Non-Ducted Indoor Units | 92000 | 12.1 | 20.1 | 103000 | 3.74 | 76000 | 2.42 | R-410A | 7.6667
213896337 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B |  |  |  | PUHY-P96ZKMU-B | Ducted Indoor Units | 92000 | 11.9 | 22.2 | 103000 | 3.73 | 76000 | 2.71 | R-410A | 7.6667
213896316 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-B |  |  |  | PUHY-P120ZKMU-B | Ducted Indoor Units | 115000 | 11.4 | 19.5 | 129000 | 3.62 | 92000 | 2.51 | R-410A | 9.5833
217284733 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-W |  |  |  | GMV-VQ72WM/C-W | Non-Ducted Indoor Units | 69000 | 11.8 | 23.8 | 77000 | 4.4 | 68000 | 2.25 | R-410A | 5.75
217284734 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-W |  |  |  | GMV-VQ72WM/C-W | Ducted Indoor Units | 69000 | 11.4 | 21 | 77000 | 4 | 68000 | 2.25 | R-410A | 5.75
217284739 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-W |  |  |  | GMV-VQ72WM/C-W | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.6 | 22.4 | 77000 | 4.2 | 68000 | 2.25 | R-410A | 5.75
217284736 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-W |  |  |  | GMV-VQ96WM/C-W | Ducted Indoor Units | 92000 | 11 | 22.2 | 103000 | 3.8 | 75000 | 2.25 | R-410A | 7.6667
217284737 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-W |  |  |  | GMV-VQ96WM/C-W | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.45 | 21.75 | 103000 | 3.9 | 75000 | 2.25 | R-410A | 7.6667
217563533 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C-W |  |  |  | TVRF-VQ72WM/C-W | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.6 | 22.4 | 77000 | 4.2 | 68000 | 2.25 | R-410A | 5.75
217563467 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C-W |  |  |  | TVRF-VQ72WM/C-W | Non-Ducted Indoor Units | 69000 | 11.8 | 23.8 | 77000 | 4.4 | 68000 | 2.25 | R-410A | 5.75
217563468 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ72WM/C-W |  |  |  | TVRF-VQ72WM/C-W | Ducted Indoor Units | 69000 | 11.4 | 21 | 77000 | 4 | 68000 | 2.25 | R-410A | 5.75
217650552 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ96WM/C-W |  |  |  | TVRF-VQ96WM/C-W | Ducted Indoor Units | 92000 | 11 | 22.2 | 103000 | 3.8 | 75000 | 2.25 | R-410A | 7.6667
217650553 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-VQ96WM/C-W |  |  |  | TVRF-VQ96WM/C-W | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 10.45 | 21.75 | 103000 | 3.9 | 75000 | 2.25 | R-410A | 7.6667
6687545 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV | AOUA72TLBV |  |  | AOUA144TLBVG | Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
207742259 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA72TLBV |  |  | AOUA168TLBVG | Ducted Indoor Units | 160000 | 11 | 20 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
6687547 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA72TLBV |  |  | AOUA168TLBVG | Non-Ducted Indoor Units | 160000 | 11 | 22.2 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
6687549 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA72TLBV |  |  | AOUA192TLBVG | Non-Ducted Indoor Units | 184000 | 11.2 | 24.3 | 206000 | 3.75 | 142000 | 2.49 | R-410A | 15.3333
6687551 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA96TLBV |  |  | AOUA216TLBVG | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
6687553 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA120TLBV |  |  | AOUA240TLBVG | Non-Ducted Indoor Units | 228000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7850824 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV | AOUA72TLCV |  |  | AOUA144TLCVG | Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850826 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA72TLCV |  |  | AOUA168TLCVG | Non-Ducted Indoor Units | 160000 | 11 | 22.2 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850828 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA72TLCV |  |  | AOUA192TLCVG | Non-Ducted Indoor Units | 184000 | 11.2 | 24.3 | 206000 | 3.75 | 142000 | 2.49 | R-410A | 15.3333
7850830 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA96TLCV |  |  | AOUA216TLCVG | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850832 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA120TLCV |  |  | AOUA240TLCVG | Non-Ducted Indoor Units | 228000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7850844 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV | AOUA72RLCV |  |  | AOUA144RLCVG | Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850846 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA72RLCV |  |  | AOUA168RLCVG | Non-Ducted Indoor Units | 160000 | 11 | 22.2 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850848 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA72RLCV |  |  | AOUA192RLCVG | Non-Ducted Indoor Units | 184000 | 11.2 | 24.3 | 206000 | 3.75 | 142000 | 2.49 | R-410A | 15.3333
7850850 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA96RLCV |  |  | AOUA216RLCVG | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850852 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA120RLCV |  |  | AOUA240RLCVG | Non-Ducted Indoor Units | 228000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
214825950 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHD144K/220V |  |  |  | TVRF-SHD144K/220V | Ducted Indoor Units | 138000 | 10.4 | 18.6 | 154000 | 3.38 | 105000 | 2.07 | R-410A | 11.5
216602713 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4J |  |  |  | VPC144S4M-4J | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
216602783 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4J |  |  |  | VPC144S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602727 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4J |  |  |  | VPC144S4M-4J | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
214826406 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144DXVGQH |  |  |  | AM144DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
214826375 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144DXVGQH |  |  |  | AM144DXVGQH | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
214826366 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144DXVGQH |  |  |  | AM144DXVGQH | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
214826367 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168DXVGQH |  |  |  | AM168DXVGQH | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
214826376 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168DXVGQH |  |  |  | AM168DXVGQH | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
214826407 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168DXVGQH |  |  |  | AM168DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602728 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4J |  |  |  | VPC168S4M-4J | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602786 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4J |  |  |  | VPC168S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602714 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4J |  |  |  | VPC168S4M-4J | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602716 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J |  |  |  | VPC192S4M-4J | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
216602788 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J |  |  |  | VPC192S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
214826408 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH |  |  |  | AM192DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
214826368 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH |  |  |  | AM192DXVGQH | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
214826369 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216DXVGQH |  |  |  | AM216DXVGQH | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
214826409 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216DXVGQH |  |  |  | AM216DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602791 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4J |  |  |  | VPC216S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602717 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4J |  |  |  | VPC216S4M-4J | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602719 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC240S4M-4J |  |  |  | VPC240S4M-4J | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
214826370 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM240DXVGQH |  |  |  | AM240DXVGQH | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
216602761 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4J |  |  |  | VRC144S4M-4J | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
216602746 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4J |  |  |  | VRC144S4M-4J | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
214826395 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144DXVGQR |  |  |  | AM144DXVGQR | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
214826386 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144DXVGQR |  |  |  | AM144DXVGQR | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
214826387 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168DXVGQR |  |  |  | AM168DXVGQR | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
214826396 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168DXVGQR |  |  |  | AM168DXVGQR | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602748 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4J |  |  |  | VRC168S4M-4J | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602763 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4J |  |  |  | VRC168S4M-4J | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602749 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4J |  |  |  | VRC192S4M-4J | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
214826388 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR |  |  |  | AM192DXVGQR | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
214826389 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216DXVGQR |  |  |  | AM216DXVGQR | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602751 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4J |  |  |  | VRC216S4M-4J | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602753 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC240S4M-4J |  |  |  | VRC240S4M-4J | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
214826390 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM240DXVGQR |  |  |  | AM240DXVGQR | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
213895939 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* |  |  |  | REYQ144AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 19.8 | 138000 | 3.25 | 90000 | 2.1 | R-410A | 11.5
213895710 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* |  |  |  | REYQ144AATJ* | Non-Ducted Indoor Units | 138000 | 11.2 | 21.5 | 138000 | 3.3 | 90000 | 2.1 | R-410A | 11.5
213896247 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AATJ* |  |  |  | REYQ168AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.45 | 18.95 | 156000 | 3.25 | 104000 | 2.07 | R-410A | 13
213895949 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* |  |  |  | REYQ144AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 19.8 | 138000 | 3.25 | 90000 | 2.1 | R-410A | 11.5
213895713 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* |  |  |  | REYQ144AAYD* | Non-Ducted Indoor Units | 138000 | 11.2 | 21.5 | 138000 | 3.3 | 90000 | 2.1 | R-410A | 11.5
213896255 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AAYD* |  |  |  | REYQ168AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.45 | 18.95 | 156000 | 3.25 | 104000 | 2.07 | R-410A | 13
216602560 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4Y |  |  |  | VPC144S4M-4Y | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
216602464 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4Y |  |  |  | VPC144S4M-4Y | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
216602371 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4Y |  |  |  | VPC144S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893937 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGFH |  |  |  | AM144BXVGFH | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
213893893 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGFH |  |  |  | AM144BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893995 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGFH |  |  |  | AM144BXVGFH | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893941 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGFH |  |  |  | AM168BXVGFH | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
213916416 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGFH |  |  |  | AM168BXVGFH | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602470 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4Y |  |  |  | VPC168S4M-4Y | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602661 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4Y |  |  |  | VPC168S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602621 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4Y |  |  |  | VPC168S4M-4Y | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
213918736 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGFH |  |  |  | AM168BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
213918740 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH |  |  |  | AM192BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602669 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y |  |  |  | VPC192S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602477 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y |  |  |  | VPC192S4M-4Y | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893945 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH |  |  |  | AM192BXVGFH | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893949 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGFH |  |  |  | AM216BXVGFH | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602483 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4Y |  |  |  | VPC216S4M-4Y | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602678 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4Y |  |  |  | VPC216S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
213918744 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGFH |  |  |  | AM216BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602490 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC240S4M-4Y |  |  |  | VPC240S4M-4Y | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
213893953 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM240BXVGFH |  |  |  | AM240BXVGFH | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
216602467 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4G |  |  |  | VPC144S4M-4G | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
216602375 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4G |  |  |  | VPC144S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602563 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC144S4M-4G |  |  |  | VPC144S4M-4G | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893997 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGJH |  |  |  | AM144BXVGJH | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893939 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGJH |  |  |  | AM144BXVGJH | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
213893895 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144BXVGJH |  |  |  | AM144BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893943 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGJH |  |  |  | AM168BXVGJH | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
213916418 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGJH |  |  |  | AM168BXVGJH | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602473 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4G |  |  |  | VPC168S4M-4G | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602624 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4G |  |  |  | VPC168S4M-4G | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602665 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC168S4M-4G |  |  |  | VPC168S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
213918738 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168BXVGJH |  |  |  | AM168BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
213918742 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH |  |  |  | AM192BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602675 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G |  |  |  | VPC192S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602480 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G |  |  |  | VPC192S4M-4G | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893947 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH |  |  |  | AM192BXVGJH | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893951 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGJH |  |  |  | AM216BXVGJH | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602486 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4G |  |  |  | VPC216S4M-4G | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602680 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC216S4M-4G |  |  |  | VPC216S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
213918746 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGJH |  |  |  | AM216BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602493 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC240S4M-4G |  |  |  | VPC240S4M-4G | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
213893955 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM240BXVGJH |  |  |  | AM240BXVGJH | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
214826414 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGFR |  |  |  | AM144DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602801 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4Y |  |  |  | VRC144S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602465 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4Y |  |  |  | VRC144S4M-4Y | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
216602373 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4Y |  |  |  | VRC144S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602562 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4Y |  |  |  | VRC144S4M-4Y | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893996 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGFR |  |  |  | AM144BXVGFR | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893938 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGFR |  |  |  | AM144BXVGFR | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
213893894 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGFR |  |  |  | AM144BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893942 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGFR |  |  |  | AM168BXVGFR | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
213916417 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGFR |  |  |  | AM168BXVGFR | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602472 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4Y |  |  |  | VRC168S4M-4Y | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602804 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4Y |  |  |  | VRC168S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602663 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4Y |  |  |  | VRC168S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
216602623 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4Y |  |  |  | VRC168S4M-4Y | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
214826415 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGFR |  |  |  | AM168DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
213918737 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGFR |  |  |  | AM168BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
213918741 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR |  |  |  | AM192BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
214826416 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR |  |  |  | AM192DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602672 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y |  |  |  | VRC192S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602806 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y |  |  |  | VRC192S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602478 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y |  |  |  | VRC192S4M-4Y | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893946 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR |  |  |  | AM192BXVGFR | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893950 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR |  |  |  | AM216BXVGFR | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602485 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4Y |  |  |  | VRC216S4M-4Y | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602808 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4Y |  |  |  | VRC216S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602679 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4Y |  |  |  | VRC216S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
214826417 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR |  |  |  | AM216DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
213918745 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR |  |  |  | AM216BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602492 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC240S4M-4Y |  |  |  | VRC240S4M-4Y | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
213893954 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM240BXVGFR |  |  |  | AM240BXVGFR | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
216602469 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4G |  |  |  | VRC144S4M-4G | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
216602378 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4G |  |  |  | VRC144S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
216602565 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC144S4M-4G |  |  |  | VRC144S4M-4G | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893998 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGJR |  |  |  | AM144BXVGJR | Non-Ducted Indoor Units | 138000 | 10.7 | 22.6 | 154000 | 3.52 | 100000 | 2.58 | R-410A | 11.5
213893940 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGJR |  |  |  | AM144BXVGJR | Ducted Indoor Units | 138000 | 12.1 | 24.4 | 154000 | 3.68 | 100000 | 2.7 | R-410A | 11.5
213893896 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144BXVGJR |  |  |  | AM144BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 3.6 | 100000 | 2.64 | R-410A | 11.5
213893944 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGJR |  |  |  | AM168BXVGJR | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
213916419 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGJR |  |  |  | AM168BXVGJR | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602475 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4G |  |  |  | VRC168S4M-4G | Ducted Indoor Units | 160000 | 11.1 | 23.3 | 180000 | 3.65 | 118000 | 2.55 | R-410A | 13.3333
216602626 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4G |  |  |  | VRC168S4M-4G | Non-Ducted Indoor Units | 160000 | 10.1 | 25.4 | 180000 | 3.28 | 118000 | 2.35 | R-410A | 13.3333
216602667 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC168S4M-4G |  |  |  | VRC168S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
213918739 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168BXVGJR |  |  |  | AM168BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 24.35 | 180000 | 3.46 | 118000 | 2.45 | R-410A | 13.3333
213918743 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR |  |  |  | AM192BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602676 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G |  |  |  | VRC192S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 23.3 | 206000 | 3.37 | 134000 | 2.43 | R-410A | 15.3333
216602481 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G |  |  |  | VRC192S4M-4G | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893948 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR |  |  |  | AM192BXVGJR | Ducted Indoor Units | 184000 | 11.8 | 24.1 | 206000 | 3.55 | 134000 | 2.65 | R-410A | 15.3333
213893952 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGJR |  |  |  | AM216BXVGJR | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602488 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4G |  |  |  | VRC216S4M-4G | Ducted Indoor Units | 206000 | 10.9 | 22.3 | 232000 | 3.45 | 150000 | 2.6 | R-410A | 17.1667
216602681 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC216S4M-4G |  |  |  | VRC216S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
213918747 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGJR |  |  |  | AM216BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 21.9 | 232000 | 3.32 | 150000 | 2.39 | R-410A | 17.1667
216602495 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC240S4M-4G |  |  |  | VRC240S4M-4G | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
213893956 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM240BXVGJR |  |  |  | AM240BXVGJR | Ducted Indoor Units | 228000 | 10.6 | 22 | 258000 | 3.25 | 168000 | 2.45 | R-410A | 19
208812535 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA96ULBV5 |  |  | AOUA216ULBVG5 | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208812536 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA120ULBV5 |  |  | AOUA240ULBVG5 | Ducted Indoor Units | 230000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208811485 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA96ULBV5 |  |  | AOUA216ULBVG5 | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208811486 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA120ULBV5 |  |  | AOUA240ULBVG5 | Non-Ducted Indoor Units | 230000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208931709 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 |  |  |  | AOUA144ULBV5 | Non-Ducted Indoor Units | 138000 | 14.4 | 28.2 | 154000 | 4.07 | 106000 | 2.48 | R-410A | 11.5
208931864 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 |  |  |  | AOUA144ULBV5 | Ducted Indoor Units | 138000 | 12.2 | 20.4 | 154000 | 3.82 | 106000 | 2.4 | R-410A | 11.5
208931866 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 |  |  |  | AOUA168ULBV5 | Ducted Indoor Units | 160000 | 11.5 | 19.9 | 180000 | 3.61 | 124000 | 2.3 | R-410A | 13.3333
208931711 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 |  |  |  | AOUA168ULBV5 | Non-Ducted Indoor Units | 160000 | 12.2 | 25.7 | 180000 | 3.78 | 124000 | 2.32 | R-410A | 13.3333
208931713 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 |  |  |  | AOUA192ULBV5 | Non-Ducted Indoor Units | 184000 | 11 | 24.6 | 206000 | 3.48 | 140000 | 2.16 | R-410A | 15.3333
208931868 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 |  |  |  | AOUA192ULBV5 | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 206000 | 3.48 | 140000 | 2.23 | R-410A | 15.3333
208812540 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA96ULCV5 |  |  | AOUA216ULCVG5 | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208812541 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA120ULCV5 |  |  | AOUA240ULCVG5 | Ducted Indoor Units | 230000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208811490 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA96ULCV5 |  |  | AOUA216ULCVG5 | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208811491 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA120ULCV5 |  |  | AOUA240ULCVG5 | Non-Ducted Indoor Units | 230000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208931731 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 |  |  |  | AOUA144ULCV5 | Non-Ducted Indoor Units | 138000 | 14.4 | 28.2 | 154000 | 4.07 | 106000 | 2.48 | R-410A | 11.5
208931886 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 |  |  |  | AOUA144ULCV5 | Ducted Indoor Units | 138000 | 12.2 | 20.4 | 154000 | 3.82 | 106000 | 2.4 | R-410A | 11.5
208931888 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 |  |  |  | AOUA168ULCV5 | Ducted Indoor Units | 160000 | 11.5 | 19.9 | 180000 | 3.61 | 124000 | 2.3 | R-410A | 13.3333
208931732 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 |  |  |  | AOUA168ULCV5 | Non-Ducted Indoor Units | 160000 | 12.2 | 25.7 | 180000 | 3.78 | 124000 | 2.32 | R-410A | 13.3333
208931734 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 |  |  |  | AOUA192ULCV5 | Non-Ducted Indoor Units | 184000 | 11 | 24.6 | 206000 | 3.48 | 140000 | 2.16 | R-410A | 15.3333
208931890 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 |  |  |  | AOUA192ULCV5 | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 206000 | 3.48 | 140000 | 2.23 | R-410A | 15.3333
213896730 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* | REYQ96XBTJ* |  |  | REYQ192XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.45 | 18.6 | 184000 | 3.52 | 128000 | 2.2 | R-410A | 15.3333
213896731 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* | REYQ120XBTJ* |  |  | REYQ216XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 18.5 | 206000 | 3.47 | 142000 | 2.19 | R-410A | 17.1667
213896712 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* | REYQ96XBTJ* |  |  | REYQ192XBTJ* | Ducted Indoor Units | 184000 | 11.4 | 18 | 184000 | 3.46 | 128000 | 2.25 | R-410A | 15.3333
213896682 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* | REYQ96XBTJ* |  |  | REYQ192XBTJ* | Non-Ducted Indoor Units | 184000 | 11.5 | 19.2 | 184000 | 3.58 | 128000 | 2.15 | R-410A | 15.3333
213896683 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBTJ* | REYQ120XBTJ* |  |  | REYQ216XBTJ* | Non-Ducted Indoor Units | 206000 | 11.1 | 19.2 | 206000 | 3.53 | 142000 | 2.15 | R-410A | 17.1667
213896684 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ120XBTJ* |  |  | REYQ240XBTJ* | Non-Ducted Indoor Units | 228000 | 10.6 | 19.4 | 228000 | 3.46 | 156000 | 2.14 | R-410A | 19
213896774 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ120XBTJ* |  |  | REYQ240XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.5 | 18.2 | 228000 | 3.37 | 156000 | 2.16 | R-410A | 19
213896797 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XBTJ* |  |  |  | REYQ144XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.45 | 18.15 | 138000 | 3.33 | 88000 | 2.07 | R-410A | 11.5
213896699 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* | REYQ96XBYD* |  |  | REYQ192XBYD* | Non-Ducted Indoor Units | 184000 | 11.5 | 19.2 | 184000 | 3.58 | 128000 | 2.15 | R-410A | 15.3333
213896700 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* | REYQ120XBYD* |  |  | REYQ216XBYD* | Non-Ducted Indoor Units | 206000 | 11.1 | 19.2 | 206000 | 3.53 | 142000 | 2.15 | R-410A | 17.1667
213896718 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* | REYQ96XBYD* |  |  | REYQ192XBYD* | Ducted Indoor Units | 184000 | 11.4 | 18 | 184000 | 3.46 | 128000 | 2.25 | R-410A | 15.3333
213896736 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* | REYQ96XBYD* |  |  | REYQ192XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.45 | 18.6 | 184000 | 3.52 | 128000 | 2.2 | R-410A | 15.3333
213896737 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYD* | REYQ120XBYD* |  |  | REYQ216XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 18.5 | 206000 | 3.47 | 142000 | 2.19 | R-410A | 17.1667
213896750 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ120XBYD* |  |  | REYQ240XBYD* | Non-Ducted Indoor Units | 228000 | 10.6 | 19.4 | 228000 | 3.46 | 156000 | 2.14 | R-410A | 19
213896778 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ120XBYD* |  |  | REYQ240XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.5 | 18.2 | 228000 | 3.37 | 156000 | 2.16 | R-410A | 19
213896800 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XBYD* |  |  |  | REYQ144XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.45 | 18.15 | 138000 | 3.33 | 88000 | 2.07 | R-410A | 11.5
213896742 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* | REYQ96XBYC* |  |  | REYQ192XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.45 | 18.6 | 184000 | 3.52 | 128000 | 2.2 | R-410A | 15.3333
213896743 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* | REYQ120XBYC* |  |  | REYQ216XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 18.5 | 206000 | 3.47 | 142000 | 2.19 | R-410A | 17.1667
213896724 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* | REYQ96XBYC* |  |  | REYQ192XBYC* | Ducted Indoor Units | 184000 | 11.4 | 18 | 184000 | 3.46 | 128000 | 2.25 | R-410A | 15.3333
213896706 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* | REYQ96XBYC* |  |  | REYQ192XBYC* | Non-Ducted Indoor Units | 184000 | 11.5 | 19.2 | 184000 | 3.58 | 128000 | 2.15 | R-410A | 15.3333
213896707 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XBYC* | REYQ120XBYC* |  |  | REYQ216XBYC* | Non-Ducted Indoor Units | 206000 | 11.1 | 19.2 | 206000 | 3.53 | 142000 | 2.15 | R-410A | 17.1667
213896754 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ120XBYC* |  |  | REYQ240XBYC* | Non-Ducted Indoor Units | 228000 | 10.6 | 19.4 | 228000 | 3.46 | 156000 | 2.14 | R-410A | 19
213896782 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ120XBYC* |  |  | REYQ240XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.5 | 18.2 | 228000 | 3.37 | 156000 | 2.16 | R-410A | 19
213896803 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XBYC* |  |  |  | REYQ144XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.45 | 18.15 | 138000 | 3.33 | 88000 | 2.07 | R-410A | 11.5
213896809 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XBYC* | RXYQ120XBYC* |  |  | RXYQ216XBYC* | Non-Ducted Indoor Units | 206000 | 10.2 | 18.4 | 206000 | 3.53 | 142000 | 2.15 | R-410A | 17.1667
213896747 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XBYC* | RXYQ96XBYC* |  |  | RXYQ192XBYC* | Non-Ducted Indoor Units | 184000 | 10.7 | 18.4 | 184000 | 3.58 | 128000 | 2.15 | R-410A | 15.3333
213896810 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* | RXYQ120XBYC* |  |  | RXYQ240XBYC* | Non-Ducted Indoor Units | 228000 | 9.9 | 18.6 | 228000 | 3.46 | 156000 | 2.14 | R-410A | 19
214389359 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ144ME2CA* |  |  |  | MVHQ144ME2CA* | Ducted Indoor Units | 138000 | 10.8 | 20.3 | 154000 | 3.4 | 108000 | 2.4 | R-410A | 11.5
214389360 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ144ME2CA* |  |  |  | MVHQ144ME2CA* | Non-Ducted Indoor Units | 138000 | 10.8 | 20 | 154000 | 3.4 | 108000 | 2.4 | R-410A | 11.5
214229577 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ168ME2CA* |  |  |  | MVHQ168ME2CA* | Ducted Indoor Units | 160000 | 11.5 | 21.5 | 180000 | 3.4 | 122000 | 2.4 | R-410A | 13.3333
214229578 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ168ME2CA* |  |  |  | MVHQ168ME2CA* | Non-Ducted Indoor Units | 160000 | 11.4 | 23.2 | 180000 | 3.6 | 122000 | 2.5 | R-410A | 13.3333
214264484 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME2CA* |  |  |  | MVHQ192ME2CA* | Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.3 | 138000 | 2.4 | R-410A | 15.3333
214264485 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME2CA* |  |  |  | MVHQ192ME2CA* | Non-Ducted Indoor Units | 184000 | 11.2 | 22.2 | 206000 | 3.5 | 138000 | 2.4 | R-410A | 15.3333
214097889 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ216ME2CA* |  |  |  | MVHQ216ME2CA* | Ducted Indoor Units | 206000 | 11.3 | 20.8 | 232000 | 3.3 | 156000 | 2.4 | R-410A | 17.1667
214097890 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ216ME2CA* |  |  |  | MVHQ216ME2CA* | Non-Ducted Indoor Units | 206000 | 10.9 | 22 | 232000 | 3.5 | 156000 | 2.4 | R-410A | 17.1667
214264488 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ240ME2CA* |  |  |  | MVHQ240ME2CA* | Ducted Indoor Units | 222000 | 10.7 | 20.3 | 240000 | 3.3 | 168000 | 2.3 | R-410A | 18.5
214264490 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ240ME2CA* |  |  |  | MVHQ240ME2CA* | Non-Ducted Indoor Units | 222000 | 10.1 | 20.3 | 240000 | 3.4 | 168000 | 2.4 | R-410A | 18.5
214389361 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ144ME4CA* |  |  |  | MVHQ144ME4CA* | Ducted Indoor Units | 138000 | 10.8 | 20.3 | 154000 | 3.4 | 108000 | 2.4 | R-410A | 11.5
214389362 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ144ME4CA* |  |  |  | MVHQ144ME4CA* | Non-Ducted Indoor Units | 138000 | 10.8 | 20 | 154000 | 3.4 | 108000 | 2.4 | R-410A | 11.5
214229579 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ168ME4CA* |  |  |  | MVHQ168ME4CA* | Ducted Indoor Units | 160000 | 11.5 | 21.5 | 180000 | 3.4 | 122000 | 2.4 | R-410A | 13.3333
214229580 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ168ME4CA* |  |  |  | MVHQ168ME4CA* | Non-Ducted Indoor Units | 160000 | 11.4 | 23.2 | 180000 | 3.6 | 122000 | 2.5 | R-410A | 13.3333
214264486 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME4CA* |  |  |  | MVHQ192ME4CA* | Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.3 | 138000 | 2.4 | R-410A | 15.3333
214264487 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME4CA* |  |  |  | MVHQ192ME4CA* | Non-Ducted Indoor Units | 184000 | 11.2 | 22.2 | 206000 | 3.5 | 138000 | 2.4 | R-410A | 15.3333
214065405 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ216ME4CA* |  |  |  | MVHQ216ME4CA* | Ducted Indoor Units | 206000 | 11.3 | 20.8 | 232000 | 3.3 | 156000 | 2.4 | R-410A | 17.1667
214065406 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ216ME4CA* |  |  |  | MVHQ216ME4CA* | Non-Ducted Indoor Units | 206000 | 10.9 | 22 | 232000 | 3.5 | 156000 | 2.4 | R-410A | 17.1667
214264489 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ240ME4CA* |  |  |  | MVHQ240ME4CA* | Ducted Indoor Units | 222000 | 10.7 | 20.3 | 240000 | 3.3 | 168000 | 2.3 | R-410A | 18.5
214264491 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ240ME4CA* |  |  |  | MVHQ240ME4CA* | Non-Ducted Indoor Units | 222000 | 10.1 | 20.3 | 240000 | 3.4 | 168000 | 2.4 | R-410A | 18.5
217189685 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR096B33CW | HVAHR096B33CW |  |  | HVAHR192B33CW* | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
214296007 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B33CW | HVAHR096B33CW |  |  | HVAHR192B33CW | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
217189695 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR096B43CW | HVAHR096B43CW |  |  | HVAHR192B43CW* | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
214296017 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B43CW | HVAHR096B43CW |  |  | HVAHR192B43CW | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
215828405 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B53CW | HVAHR072B53CW |  |  | HVAHR168B53CW | Non-Ducted Indoor Units | 160000 | 11.2 | 18.7 | 180000 | 4.2 | 124000 | 2.6 | R-410A | 13.3333
215828406 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B53CW | HVAHR096B53CW |  |  | HVAHR192B53CW | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
217189704 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR096B53CW | HVAHR072B53CW |  |  | HVAHR168B53CW* | Non-Ducted Indoor Units | 160000 | 11.2 | 18.7 | 180000 | 4.2 | 124000 | 2.6 | R-410A | 13.3333
217189705 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR096B53CW | HVAHR096B53CW |  |  | HVAHR192B53CW* | Non-Ducted Indoor Units | 184000 | 11.4 | 18.4 | 206000 | 4 | 140000 | 2.5 | R-410A | 15.3333
217189707 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR120B53CW | HVAHR120B53CW |  |  | HVAHR240B53CW* | Non-Ducted Indoor Units | 230000 | 12 | 18.6 | 258000 | 4.1 | 178000 | 2.55 | R-410A | 19.1667
215828408 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B53CW | HVAHR120B53CW |  |  | HVAHR240B53CW | Non-Ducted Indoor Units | 230000 | 12 | 18.6 | 258000 | 4.1 | 178000 | 2.55 | R-410A | 19.1667
215828414 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW |  |  |  | HVAHR144B53CW | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 18 | 154000 | 3.6 | 110000 | 2.4 | R-410A | 11.5
215828404 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW |  |  |  | HVAHR144B53CW | Non-Ducted Indoor Units | 138000 | 11.7 | 18.7 | 154000 | 3.8 | 110000 | 2.6 | R-410A | 11.5
217189703 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW |  |  |  | HVAHR144B53CW* | Non-Ducted Indoor Units | 138000 | 11.7 | 18.7 | 154000 | 3.8 | 110000 | 2.6 | R-410A | 11.5
217190041 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW |  |  |  | HVAHR144B53CW* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 18 | 154000 | 3.6 | 110000 | 2.4 | R-410A | 11.5
217729762 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 |  |  |  | ZRUM144BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.6 | 22 | 152000 | 3.9 | 98000 | 2.75 | R-32 | 11.5
217729304 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 |  |  |  | ZRUM144BTE6 | Non-Ducted Indoor Units | 138000 | 11.6 | 23.5 | 152000 | 4 | 98000 | 2.8 | R-32 | 11.5
217729305 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 |  |  |  | ZRUM144BTE6 | Ducted Indoor Units | 138000 | 11.6 | 20.5 | 152000 | 3.8 | 98000 | 2.7 | R-32 | 11.5
217729306 | N/A | LG | HMSR-A-CB | ZRUM168BTE6 |  |  |  | ZRUM168BTE6 | Non-Ducted Indoor Units | 160000 | 11 | 22.6 | 180000 | 3.7 | 117000 | 2.57 | R-32 | 13.3333
217729307 | N/A | LG | HMSR-A-CB | ZRUM168BTE6 |  |  |  | ZRUM168BTE6 | Ducted Indoor Units | 160000 | 11.1 | 19.8 | 180000 | 3.47 | 117000 | 2.62 | R-32 | 13.3333
217729763 | N/A | LG | HMSR-A-CB | ZRUM168BTE6 |  |  |  | ZRUM168BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.05 | 21.2 | 180000 | 3.58 | 117000 | 2.59 | R-32 | 13.3333
217729764 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 |  |  |  | ZRUM192BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 21.25 | 206000 | 3.54 | 134000 | 2.65 | R-32 | 15.3333
217729308 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 |  |  |  | ZRUM192BTE6 | Non-Ducted Indoor Units | 184000 | 10.7 | 22.1 | 206000 | 3.78 | 134000 | 2.7 | R-32 | 15.3333
217729309 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 |  |  |  | ZRUM192BTE6 | Ducted Indoor Units | 184000 | 10.9 | 20.4 | 206000 | 3.3 | 134000 | 2.61 | R-32 | 15.3333
217729310 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 |  |  |  | ZRUM216BTE6 | Non-Ducted Indoor Units | 206000 | 10.5 | 22.3 | 230000 | 3.73 | 150000 | 2.7 | R-32 | 17.1667
217729311 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 |  |  |  | ZRUM216BTE6 | Ducted Indoor Units | 206000 | 11.5 | 22.1 | 230000 | 3.45 | 150000 | 2.67 | R-32 | 17.1667
217729765 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 |  |  |  | ZRUM216BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11 | 22.2 | 230000 | 3.59 | 150000 | 2.68 | R-32 | 17.1667
217729766 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 |  |  |  | ZRUM241BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 222000 | 10.6 | 21.75 | 256000 | 3.39 | 168000 | 2.55 | R-32 | 18.5
217729312 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 |  |  |  | ZRUM241BTE6 | Non-Ducted Indoor Units | 222000 | 10.3 | 21.8 | 256000 | 3.53 | 168000 | 2.6 | R-32 | 18.5
217729313 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 |  |  |  | ZRUM241BTE6 | Ducted Indoor Units | 222000 | 10.9 | 21.7 | 256000 | 3.25 | 168000 | 2.51 | R-32 | 18.5
217729319 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 |  |  |  | ZRUM144DTE6 | Non-Ducted Indoor Units | 138000 | 11.6 | 23.5 | 152000 | 4 | 98000 | 2.8 | R-32 | 11.5
217729320 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 |  |  |  | ZRUM144DTE6 | Ducted Indoor Units | 138000 | 11.6 | 20.5 | 152000 | 3.8 | 98000 | 2.7 | R-32 | 11.5
217729783 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 |  |  |  | ZRUM144DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.6 | 22 | 152000 | 3.9 | 98000 | 2.75 | R-32 | 11.5
217729784 | N/A | LG | HMSR-A-CB | ZRUM168DTE6 |  |  |  | ZRUM168DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.05 | 21.2 | 180000 | 3.58 | 117000 | 2.59 | R-32 | 13.3333
217729321 | N/A | LG | HMSR-A-CB | ZRUM168DTE6 |  |  |  | ZRUM168DTE6 | Non-Ducted Indoor Units | 160000 | 11 | 22.6 | 180000 | 3.7 | 117000 | 2.57 | R-32 | 13.3333
217729322 | N/A | LG | HMSR-A-CB | ZRUM168DTE6 |  |  |  | ZRUM168DTE6 | Ducted Indoor Units | 160000 | 11.1 | 19.8 | 180000 | 3.47 | 117000 | 2.62 | R-32 | 13.3333
217729323 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 |  |  |  | ZRUM192DTE6 | Non-Ducted Indoor Units | 184000 | 10.7 | 22.1 | 206000 | 3.78 | 134000 | 2.7 | R-32 | 15.3333
217729324 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 |  |  |  | ZRUM192DTE6 | Ducted Indoor Units | 184000 | 10.9 | 20.4 | 206000 | 3.3 | 134000 | 2.61 | R-32 | 15.3333
217729785 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 |  |  |  | ZRUM192DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 21.25 | 206000 | 3.54 | 134000 | 2.65 | R-32 | 15.3333
217729786 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 |  |  |  | ZRUM216DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11 | 22.2 | 230000 | 3.59 | 150000 | 2.68 | R-32 | 17.1667
217729325 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 |  |  |  | ZRUM216DTE6 | Non-Ducted Indoor Units | 206000 | 10.5 | 22.3 | 230000 | 3.73 | 150000 | 2.7 | R-32 | 17.1667
217729326 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 |  |  |  | ZRUM216DTE6 | Ducted Indoor Units | 206000 | 11.5 | 22.1 | 230000 | 3.45 | 150000 | 2.67 | R-32 | 17.1667
217729327 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 |  |  |  | ZRUM241DTE6 | Non-Ducted Indoor Units | 222000 | 10.3 | 21.8 | 256000 | 3.53 | 168000 | 2.6 | R-32 | 18.5
217729328 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 |  |  |  | ZRUM241DTE6 | Ducted Indoor Units | 222000 | 10.9 | 21.7 | 256000 | 3.25 | 168000 | 2.51 | R-32 | 18.5
217729787 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 |  |  |  | ZRUM241DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 222000 | 10.6 | 21.75 | 256000 | 3.39 | 168000 | 2.55 | R-32 | 18.5
217734390 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB1921FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.3 | 206000 | 3.78 | 148000 | 2.4 | R-454B | 15.3333
217734333 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB1921FT6P-UL | Ducted Indoor Units | 184000 | 10.7 | 20.6 | 206000 | 3.32 | 148000 | 2.42 | R-454B | 15.3333
217734270 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB1921FT6P-UL | Non-Ducted Indoor Units | 184000 | 11.2 | 24 | 206000 | 4.25 | 148000 | 2.39 | R-454B | 15.3333
217734386 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL |  |  |  | MMY-MUB1441FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.9 | 100000 | 2.62 | R-454B | 11.5
217734392 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  |  | MMY-UB2161FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11 | 22.25 | 232000 | 3.76 | 156000 | 2.52 | R-454B | 17.1667
217734394 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB2401FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.75 | 22 | 258000 | 3.64 | 174000 | 2.44 | R-454B | 19.1667
217734335 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  |  | MMY-UB2161FT6P-UL | Ducted Indoor Units | 206000 | 10.9 | 21.2 | 232000 | 3.43 | 156000 | 2.48 | R-454B | 17.1667
217734329 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL |  |  |  | MMY-MUB1441FT6P-UL | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.81 | 100000 | 2.6 | R-454B | 11.5
217734337 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB2401FT6P-UL | Ducted Indoor Units | 230000 | 10.6 | 21.1 | 258000 | 3.29 | 174000 | 2.45 | R-454B | 19.1667
217734268 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL |  |  |  | MMY-MUB1441FT6P-UL | Non-Ducted Indoor Units | 138000 | 11.3 | 23.1 | 154000 | 4 | 100000 | 2.65 | R-454B | 11.5
217734271 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  |  | MMY-UB2161FT6P-UL | Non-Ducted Indoor Units | 206000 | 11.1 | 23.3 | 232000 | 4.09 | 156000 | 2.56 | R-454B | 17.1667
217734272 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB2401FT6P-UL | Non-Ducted Indoor Units | 230000 | 10.9 | 22.9 | 258000 | 3.99 | 174000 | 2.44 | R-454B | 19.1667
217734269 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL |  |  |  | MMY-MUB1681FT6P-UL | Non-Ducted Indoor Units | 160000 | 10.8 | 23 | 180000 | 3.85 | 122000 | 2.5 | R-454B | 13.3333
217734331 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL |  |  |  | MMY-MUB1681FT6P-UL | Ducted Indoor Units | 160000 | 10.6 | 20.7 | 180000 | 3.65 | 122000 | 2.47 | R-454B | 13.3333
217734388 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL |  |  |  | MMY-MUB1681FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.7 | 21.85 | 180000 | 3.75 | 122000 | 2.48 | R-454B | 13.3333
217734424 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL | MMY-MUB072H1FT6PUL |  |  | MMY-UB144H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 22.95 | 154000 | 4.17 | 128000 | 2.36 | R-454B | 11.5
217734313 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL | MMY-MUB072H1FT6PUL |  |  | MMY-UB144H1FT6PUL | Non-Ducted Indoor Units | 138000 | 11.5 | 23.7 | 154000 | 4.5 | 128000 | 2.39 | R-454B | 11.5
217734367 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT6PUL | MMY-MUB072H1FT6PUL |  |  | MMY-UB144H1FT6PUL | Ducted Indoor Units | 138000 | 12.1 | 22.2 | 154000 | 3.84 | 128000 | 2.33 | R-454B | 11.5
217734315 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  |  | MMY-UB192H1FT6PUL | Non-Ducted Indoor Units | 184000 | 13 | 23.3 | 206000 | 4.45 | 172000 | 2.51 | R-454B | 15.3333
217734426 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  |  | MMY-UB192H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.6 | 22.35 | 206000 | 3.95 | 172000 | 2.42 | R-454B | 15.3333
217734369 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  |  | MMY-UB192H1FT6PUL | Ducted Indoor Units | 184000 | 12.2 | 21.4 | 206000 | 3.46 | 172000 | 2.33 | R-454B | 15.3333
217734371 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  |  | MMY-UB240H1FT6PUL | Ducted Indoor Units | 230000 | 11.7 | 21.4 | 258000 | 3.36 | 220000 | 2.23 | R-454B | 19.1667
217734428 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  |  | MMY-UB240H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.85 | 22.35 | 258000 | 3.78 | 220000 | 2.32 | R-454B | 19.1667
217734317 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  |  | MMY-UB240H1FT6PUL | Non-Ducted Indoor Units | 230000 | 12 | 23.3 | 258000 | 4.2 | 220000 | 2.42 | R-454B | 19.1667
217734391 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB1921FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.3 | 206000 | 3.78 | 148000 | 2.4 | R-454B | 15.3333
217734293 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB1921FT9P-UL | Non-Ducted Indoor Units | 184000 | 11.2 | 24 | 206000 | 4.25 | 148000 | 2.39 | R-454B | 15.3333
217734334 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB1921FT9P-UL | Ducted Indoor Units | 184000 | 10.7 | 20.6 | 206000 | 3.32 | 148000 | 2.42 | R-454B | 15.3333
217734387 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL |  |  |  | MMY-MUB1441FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.9 | 100000 | 2.62 | R-454B | 11.5
217734395 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB2401FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.75 | 22 | 258000 | 3.64 | 174000 | 2.44 | R-454B | 19.1667
217734393 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  |  | MMY-UB2161FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11 | 22.25 | 232000 | 3.76 | 156000 | 2.52 | R-454B | 17.1667
217734291 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL |  |  |  | MMY-MUB1441FT9P-UL | Non-Ducted Indoor Units | 138000 | 11.3 | 23.1 | 154000 | 4 | 100000 | 2.65 | R-454B | 11.5
217734294 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  |  | MMY-UB2161FT9P-UL | Non-Ducted Indoor Units | 206000 | 11.1 | 23.3 | 232000 | 4.09 | 156000 | 2.56 | R-454B | 17.1667
217734295 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB2401FT9P-UL | Non-Ducted Indoor Units | 230000 | 10.9 | 22.9 | 258000 | 3.99 | 174000 | 2.44 | R-454B | 19.1667
217734336 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  |  | MMY-UB2161FT9P-UL | Ducted Indoor Units | 206000 | 10.9 | 21.2 | 232000 | 3.43 | 156000 | 2.48 | R-454B | 17.1667
217734330 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL |  |  |  | MMY-MUB1441FT9P-UL | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.81 | 100000 | 2.6 | R-454B | 11.5
217734338 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB2401FT9P-UL | Ducted Indoor Units | 230000 | 10.6 | 21.1 | 258000 | 3.29 | 174000 | 2.45 | R-454B | 19.1667
217734332 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL |  |  |  | MMY-MUB1681FT9P-UL | Ducted Indoor Units | 160000 | 10.6 | 20.7 | 180000 | 3.65 | 122000 | 2.47 | R-454B | 13.3333
217734292 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL |  |  |  | MMY-MUB1681FT9P-UL | Non-Ducted Indoor Units | 160000 | 10.8 | 23 | 180000 | 3.85 | 122000 | 2.5 | R-454B | 13.3333
217734389 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL |  |  |  | MMY-MUB1681FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.7 | 21.85 | 180000 | 3.75 | 122000 | 2.48 | R-454B | 13.3333
217734425 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL | MMY-MUB072H1FT9PUL |  |  | MMY-UB144H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 22.95 | 154000 | 4.17 | 128000 | 2.36 | R-454B | 11.5
217734314 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL | MMY-MUB072H1FT9PUL |  |  | MMY-UB144H1FT9PUL | Non-Ducted Indoor Units | 138000 | 11.5 | 23.7 | 154000 | 4.5 | 128000 | 2.39 | R-454B | 11.5
217734368 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB072H1FT9PUL | MMY-MUB072H1FT9PUL |  |  | MMY-UB144H1FT9PUL | Ducted Indoor Units | 138000 | 12.1 | 22.2 | 154000 | 3.84 | 128000 | 2.33 | R-454B | 11.5
217734316 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  |  | MMY-UB192H1FT9PUL | Non-Ducted Indoor Units | 184000 | 13 | 23.3 | 206000 | 4.45 | 172000 | 2.51 | R-454B | 15.3333
217734427 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  |  | MMY-UB192H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.6 | 22.35 | 206000 | 3.95 | 172000 | 2.42 | R-454B | 15.3333
217734370 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  |  | MMY-UB192H1FT9PUL | Ducted Indoor Units | 184000 | 12.2 | 21.4 | 206000 | 3.46 | 172000 | 2.33 | R-454B | 15.3333
217734372 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  |  | MMY-UB240H1FT9PUL | Ducted Indoor Units | 230000 | 11.7 | 21.4 | 258000 | 3.36 | 220000 | 2.23 | R-454B | 19.1667
217734429 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  |  | MMY-UB240H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.85 | 22.35 | 258000 | 3.78 | 220000 | 2.32 | R-454B | 19.1667
217734318 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  |  | MMY-UB240H1FT9PUL | Non-Ducted Indoor Units | 230000 | 12 | 23.3 | 258000 | 4.2 | 220000 | 2.42 | R-454B | 19.1667
217735011 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB1921HT6P-UL | Ducted Indoor Units | 184000 | 10.4 | 20.5 | 206000 | 3.32 | 148000 | 2.42 | R-454B | 15.3333
217735012 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB1921HT6P-UL | Non-Ducted Indoor Units | 184000 | 9.9 | 23.8 | 206000 | 4.25 | 148000 | 2.39 | R-454B | 15.3333
217735100 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB1921HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.15 | 22.15 | 206000 | 3.78 | 148000 | 2.4 | R-454B | 15.3333
217735104 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  |  | MMY-UB2161HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.4 | 22 | 232000 | 3.76 | 156000 | 2.52 | R-454B | 17.1667
217735106 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB2401HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.85 | 258000 | 3.64 | 174000 | 2.44 | R-454B | 19.1667
217735094 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL |  |  |  | MMY-MUB1441HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.35 | 22.2 | 154000 | 3.9 | 100000 | 2.62 | R-454B | 11.5
217734999 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL |  |  |  | MMY-MUB1441HT6P-UL | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.81 | 100000 | 2.6 | R-454B | 11.5
217735000 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL |  |  |  | MMY-MUB1441HT6P-UL | Non-Ducted Indoor Units | 138000 | 11.2 | 23.1 | 154000 | 4 | 100000 | 2.65 | R-454B | 11.5
217735018 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  |  | MMY-UB2161HT6P-UL | Ducted Indoor Units | 206000 | 10.9 | 21.2 | 232000 | 3.43 | 156000 | 2.48 | R-454B | 17.1667
217735019 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  |  | MMY-UB2161HT6P-UL | Non-Ducted Indoor Units | 206000 | 9.9 | 22.8 | 232000 | 4.09 | 156000 | 2.56 | R-454B | 17.1667
217735022 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB2401HT6P-UL | Ducted Indoor Units | 230000 | 10.5 | 21.1 | 258000 | 3.29 | 174000 | 2.45 | R-454B | 19.1667
217735003 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL |  |  |  | MMY-MUB1681HT6P-UL | Ducted Indoor Units | 160000 | 10.4 | 20.7 | 180000 | 3.65 | 122000 | 2.47 | R-454B | 13.3333
217735004 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL |  |  |  | MMY-MUB1681HT6P-UL | Non-Ducted Indoor Units | 160000 | 10.8 | 23 | 180000 | 3.85 | 122000 | 2.5 | R-454B | 13.3333
217735096 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL |  |  |  | MMY-MUB1681HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 21.85 | 180000 | 3.75 | 122000 | 2.48 | R-454B | 13.3333
217735098 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL | MMY-MUB072H1HT6PUL |  |  | MMY-UB144H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 22.85 | 154000 | 4.17 | 128000 | 2.36 | R-454B | 11.5
217735007 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL | MMY-MUB072H1HT6PUL |  |  | MMY-UB144H1HT6PUL | Ducted Indoor Units | 138000 | 11.6 | 22.1 | 154000 | 3.84 | 128000 | 2.33 | R-454B | 11.5
217735008 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT6PUL | MMY-MUB072H1HT6PUL |  |  | MMY-UB144H1HT6PUL | Non-Ducted Indoor Units | 138000 | 11.3 | 23.6 | 154000 | 4.5 | 128000 | 2.39 | R-454B | 11.5
217735014 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  |  | MMY-UB192H1HT6PUL | Ducted Indoor Units | 184000 | 10.9 | 21.2 | 206000 | 3.46 | 172000 | 2.33 | R-454B | 15.3333
217735015 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  |  | MMY-UB192H1HT6PUL | Non-Ducted Indoor Units | 184000 | 11.1 | 23 | 206000 | 4.45 | 172000 | 2.51 | R-454B | 15.3333
217735102 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  |  | MMY-UB192H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.95 | 172000 | 2.42 | R-454B | 15.3333
217735108 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  |  | MMY-UB240H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 22.1 | 258000 | 3.78 | 220000 | 2.32 | R-454B | 19.1667
217735026 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  |  | MMY-UB240H1HT6PUL | Ducted Indoor Units | 230000 | 10.9 | 21.2 | 258000 | 3.36 | 220000 | 2.23 | R-454B | 19.1667
217735027 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  |  | MMY-UB240H1HT6PUL | Non-Ducted Indoor Units | 230000 | 11.1 | 23 | 258000 | 4.2 | 220000 | 2.42 | R-454B | 19.1667
217735013 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB1921HT9P-UL | Ducted Indoor Units | 184000 | 10.4 | 20.5 | 206000 | 3.32 | 148000 | 2.42 | R-454B | 15.3333
217735101 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB1921HT9P-UL | Non-Ducted Indoor Units | 184000 | 9.9 | 23.8 | 206000 | 4.25 | 148000 | 2.39 | R-454B | 15.3333
217735136 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB1921HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.15 | 22.15 | 206000 | 3.78 | 148000 | 2.4 | R-454B | 15.3333
217735107 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB2401HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.85 | 258000 | 3.64 | 174000 | 2.44 | R-454B | 19.1667
217735105 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  |  | MMY-UB2161HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.4 | 22 | 232000 | 3.76 | 156000 | 2.52 | R-454B | 17.1667
217735095 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL |  |  |  | MMY-MUB1441HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.35 | 22.2 | 154000 | 3.9 | 100000 | 2.62 | R-454B | 11.5
217735001 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL |  |  |  | MMY-MUB1441HT9P-UL | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.81 | 100000 | 2.6 | R-454B | 11.5
217735002 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL |  |  |  | MMY-MUB1441HT9P-UL | Non-Ducted Indoor Units | 138000 | 11.2 | 23.1 | 154000 | 4 | 100000 | 2.65 | R-454B | 11.5
217735024 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB2401HT9P-UL | Ducted Indoor Units | 230000 | 10.5 | 21.1 | 258000 | 3.29 | 174000 | 2.45 | R-454B | 19.1667
217735020 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  |  | MMY-UB2161HT9P-UL | Ducted Indoor Units | 206000 | 10.9 | 21.2 | 232000 | 3.43 | 156000 | 2.48 | R-454B | 17.1667
217735021 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  |  | MMY-UB2161HT9P-UL | Non-Ducted Indoor Units | 206000 | 9.9 | 22.8 | 232000 | 4.09 | 156000 | 2.56 | R-454B | 17.1667
217735005 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL |  |  |  | MMY-MUB1681HT9P-UL | Ducted Indoor Units | 160000 | 10.4 | 20.7 | 180000 | 3.65 | 122000 | 2.47 | R-454B | 13.3333
217735006 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL |  |  |  | MMY-MUB1681HT9P-UL | Non-Ducted Indoor Units | 160000 | 10.8 | 23 | 180000 | 3.85 | 122000 | 2.5 | R-454B | 13.3333
217735097 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL |  |  |  | MMY-MUB1681HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.6 | 21.85 | 180000 | 3.75 | 122000 | 2.48 | R-454B | 13.3333
217735099 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL | MMY-MUB072H1HT9PUL |  |  | MMY-UB144H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 22.85 | 154000 | 4.17 | 128000 | 2.36 | R-454B | 11.5
217735009 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL | MMY-MUB072H1HT9PUL |  |  | MMY-UB144H1HT9PUL | Ducted Indoor Units | 138000 | 11.6 | 22.1 | 154000 | 3.84 | 128000 | 2.33 | R-454B | 11.5
217735010 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB072H1HT9PUL | MMY-MUB072H1HT9PUL |  |  | MMY-UB144H1HT9PUL | Non-Ducted Indoor Units | 138000 | 11.3 | 23.6 | 154000 | 4.5 | 128000 | 2.39 | R-454B | 11.5
217735016 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  |  | MMY-UB192H1HT9PUL | Ducted Indoor Units | 184000 | 10.9 | 21.2 | 206000 | 3.46 | 172000 | 2.33 | R-454B | 15.3333
217735017 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  |  | MMY-UB192H1HT9PUL | Non-Ducted Indoor Units | 184000 | 11.1 | 23 | 206000 | 4.45 | 172000 | 2.51 | R-454B | 15.3333
217735103 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  |  | MMY-UB192H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.95 | 172000 | 2.42 | R-454B | 15.3333
217735109 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  |  | MMY-UB240H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 22.1 | 258000 | 3.78 | 220000 | 2.32 | R-454B | 19.1667
217735028 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  |  | MMY-UB240H1HT9PUL | Ducted Indoor Units | 230000 | 10.9 | 21.2 | 258000 | 3.36 | 220000 | 2.23 | R-454B | 19.1667
217735029 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  |  | MMY-UB240H1HT9PUL | Non-Ducted Indoor Units | 230000 | 11.1 | 23 | 258000 | 4.2 | 220000 | 2.42 | R-454B | 19.1667
217883042 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL | MMY-MUB0721FT2P-UL |  |  | MMY-UB1441FT2P-UL | Non-Ducted Indoor Units | 138000 | 11.5 | 23.7 | 154000 | 4.5 | 112000 | 2.7 | R-454B | 11.5
217883044 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL | MMY-MUB0721FT2P-UL |  |  | MMY-UB1441FT2P-UL | Ducted Indoor Units | 138000 | 12.1 | 22.2 | 154000 | 3.84 | 112000 | 2.56 | R-454B | 11.5
217883046 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB0721FT2P-UL | MMY-MUB0721FT2P-UL |  |  | MMY-UB1441FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 22.95 | 154000 | 4.17 | 112000 | 2.63 | R-454B | 11.5
217901739 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A |  |  |  | PURY-EM144TXU-A | Ducted Indoor Units | 138000 | 12.3 | 21.3 | 152000 | 3.69 | 118000 | 2.35 | R-32 | 11.5
217901741 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A |  |  |  | PURY-EM144TXU-A | Non-Ducted Indoor Units | 138000 | 12.8 | 23 | 152000 | 4 | 118000 | 2.45 | R-32 | 11.5
217901743 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A |  |  |  | PURY-EM168TXU-A | Ducted Indoor Units | 160000 | 11.5 | 20.7 | 178000 | 3.48 | 136000 | 2.25 | R-32 | 13.3333
217901745 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A |  |  |  | PURY-EM168TXU-A | Non-Ducted Indoor Units | 160000 | 11.8 | 22.9 | 178000 | 3.77 | 136000 | 2.35 | R-32 | 13.3333
217901751 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192TXU-A |  |  |  | PURY-EM192TXU-A | Non-Ducted Indoor Units | 184000 | 11.2 | 23.2 | 184000 | 3.78 | 144000 | 2.29 | R-32 | 15.3333
217901747 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192TXU-A |  |  |  | PURY-EM192TXU-A | Ducted Indoor Units | 184000 | 10.8 | 20 | 184000 | 3.47 | 144000 | 2.21 | R-32 | 15.3333
217902155 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72TXU-A | PURY-HM72TXU-A |  |  | PURY-HM144TSXU-A | Ducted Indoor Units | 138000 | 13.3 | 21.8 | 152000 | 3.88 | 118000 | 2.6 | R-32 | 11.5
217902157 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72TXU-A | PURY-HM72TXU-A |  |  | PURY-HM144TSXU-A | Non-Ducted Indoor Units | 138000 | 14 | 24.6 | 152000 | 4.34 | 118000 | 2.72 | R-32 | 11.5
217901749 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96TXU-A | PURY-HM96TXU-A |  |  | PURY-HM192TSXU-A | Ducted Indoor Units | 184000 | 12.9 | 21.7 | 204000 | 3.86 | 144000 | 2.51 | R-32 | 15.3333
217901753 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96TXU-A | PURY-HM96TXU-A |  |  | PURY-HM192TSXU-A | Non-Ducted Indoor Units | 184000 | 13.8 | 24.2 | 204000 | 4.16 | 144000 | 2.67 | R-32 | 15.3333
217902159 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120TXU-A | PURY-HM120TXU-A |  |  | PURY-HM240TSXU-A | Ducted Indoor Units | 230000 | 12.8 | 21.6 | 258000 | 3.57 | 172000 | 2.49 | R-32 | 19.1667
217902161 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120TXU-A | PURY-HM120TXU-A |  |  | PURY-HM240TSXU-A | Non-Ducted Indoor Units | 230000 | 13.5 | 24.4 | 258000 | 3.92 | 172000 | 2.52 | R-32 | 19.1667
217901742 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A |  |  |  | PURY-EM144YXU-A | Non-Ducted Indoor Units | 138000 | 12.8 | 23 | 152000 | 4 | 118000 | 2.45 | R-32 | 11.5
217901740 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A |  |  |  | PURY-EM144YXU-A | Ducted Indoor Units | 138000 | 12.3 | 21.3 | 152000 | 3.69 | 118000 | 2.35 | R-32 | 11.5
217901746 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A |  |  |  | PURY-EM168YXU-A | Non-Ducted Indoor Units | 160000 | 11.8 | 22.9 | 178000 | 3.77 | 136000 | 2.35 | R-32 | 13.3333
217901744 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A |  |  |  | PURY-EM168YXU-A | Ducted Indoor Units | 160000 | 11.5 | 20.7 | 178000 | 3.48 | 136000 | 2.25 | R-32 | 13.3333
217901752 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192YXU-A |  |  |  | PURY-EM192YXU-A | Non-Ducted Indoor Units | 184000 | 11.2 | 23.2 | 184000 | 3.78 | 144000 | 2.29 | R-32 | 15.3333
217901748 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192YXU-A |  |  |  | PURY-EM192YXU-A | Ducted Indoor Units | 184000 | 10.8 | 20 | 184000 | 3.47 | 144000 | 2.21 | R-32 | 15.3333
217902156 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72YXU-A | PURY-HM72YXU-A |  |  | PURY-HM144YSXU-A | Ducted Indoor Units | 138000 | 13.3 | 21.8 | 152000 | 3.88 | 118000 | 2.6 | R-32 | 11.5
217902158 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM72YXU-A | PURY-HM72YXU-A |  |  | PURY-HM144YSXU-A | Non-Ducted Indoor Units | 138000 | 14 | 24.6 | 152000 | 4.34 | 118000 | 2.72 | R-32 | 11.5
217901750 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96YXU-A | PURY-HM96YXU-A |  |  | PURY-HM192YSXU-A | Ducted Indoor Units | 184000 | 12.9 | 21.7 | 204000 | 3.86 | 144000 | 2.51 | R-32 | 15.3333
217901754 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM96YXU-A | PURY-HM96YXU-A |  |  | PURY-HM192YSXU-A | Non-Ducted Indoor Units | 184000 | 13.8 | 24.2 | 204000 | 4.16 | 144000 | 2.67 | R-32 | 15.3333
217902160 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120YXU-A | PURY-HM120YXU-A |  |  | PURY-HM240YSXU-A | Ducted Indoor Units | 230000 | 12.8 | 21.6 | 258000 | 3.57 | 172000 | 2.49 | R-32 | 19.1667
217902162 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-HM120YXU-A | PURY-HM120YXU-A |  |  | PURY-HM240YSXU-A | Non-Ducted Indoor Units | 230000 | 13.5 | 24.4 | 258000 | 3.92 | 172000 | 2.52 | R-32 | 19.1667
217902285 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN |  |  |  | TURYE1443AMM0AN | Non-Ducted Indoor Units | 138000 | 12.8 | 23 | 152000 | 4 | 118000 | 2.45 | R-32 | 11.5
217902283 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN |  |  |  | TURYE1443AMM0AN | Ducted Indoor Units | 138000 | 12.3 | 21.3 | 152000 | 3.69 | 118000 | 2.35 | R-32 | 11.5
217902291 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN |  |  |  | TURYE1683AMM0AN | Ducted Indoor Units | 160000 | 11.5 | 20.7 | 178000 | 3.48 | 136000 | 2.25 | R-32 | 13.3333
217902292 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN |  |  |  | TURYE1683AMM0AN | Non-Ducted Indoor Units | 160000 | 11.8 | 22.9 | 178000 | 3.77 | 136000 | 2.35 | R-32 | 13.3333
217902297 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AMM0AN |  |  |  | TURYE1923AMM0AN | Non-Ducted Indoor Units | 184000 | 11.2 | 23.2 | 184000 | 3.78 | 144000 | 2.29 | R-32 | 15.3333
217902295 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AMM0AN |  |  |  | TURYE1923AMM0AN | Ducted Indoor Units | 184000 | 10.8 | 20 | 184000 | 3.47 | 144000 | 2.21 | R-32 | 15.3333
217902284 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AMM0AN | TURYH0723AMM0AN |  |  | TURYH1443BMM0AN | Ducted Indoor Units | 138000 | 13.3 | 21.8 | 152000 | 3.88 | 118000 | 2.6 | R-32 | 11.5
217902286 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AMM0AN | TURYH0723AMM0AN |  |  | TURYH1443BMM0AN | Non-Ducted Indoor Units | 138000 | 14 | 24.6 | 152000 | 4.34 | 118000 | 2.72 | R-32 | 11.5
217902296 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AMM0AN | TURYH0963AMM0AN |  |  | TURYH1923BMM0AN | Ducted Indoor Units | 184000 | 12.9 | 21.7 | 204000 | 3.86 | 144000 | 2.51 | R-32 | 15.3333
217902298 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AMM0AN | TURYH0963AMM0AN |  |  | TURYH1923BMM0AN | Non-Ducted Indoor Units | 184000 | 13.8 | 24.2 | 204000 | 4.16 | 144000 | 2.67 | R-32 | 15.3333
217902303 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AMM0AN | TURYH1203AMM0AN |  |  | TURYH2403BMM0AN | Ducted Indoor Units | 230000 | 12.8 | 21.6 | 258000 | 3.57 | 172000 | 2.49 | R-32 | 19.1667
217902304 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1203AMM0AN | TURYH1203AMM0AN |  |  | TURYH2403BMM0AN | Non-Ducted Indoor Units | 230000 | 13.5 | 24.4 | 258000 | 3.92 | 172000 | 2.52 | R-32 | 19.1667
217902287 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN |  |  |  | TURYE1444AMM0AN | Ducted Indoor Units | 138000 | 12.3 | 21.3 | 152000 | 3.69 | 118000 | 2.35 | R-32 | 11.5
217902289 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN |  |  |  | TURYE1444AMM0AN | Non-Ducted Indoor Units | 138000 | 12.8 | 23 | 152000 | 4 | 118000 | 2.45 | R-32 | 11.5
217902293 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN |  |  |  | TURYE1684AMM0AN | Ducted Indoor Units | 160000 | 11.5 | 20.7 | 178000 | 3.48 | 136000 | 2.25 | R-32 | 13.3333
217902294 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN |  |  |  | TURYE1684AMM0AN | Non-Ducted Indoor Units | 160000 | 11.8 | 22.9 | 178000 | 3.77 | 136000 | 2.35 | R-32 | 13.3333
217902299 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AMM0AN |  |  |  | TURYE1924AMM0AN | Ducted Indoor Units | 184000 | 10.8 | 20 | 184000 | 3.47 | 144000 | 2.21 | R-32 | 15.3333
217902301 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AMM0AN |  |  |  | TURYE1924AMM0AN | Non-Ducted Indoor Units | 184000 | 11.2 | 23.2 | 184000 | 3.78 | 144000 | 2.29 | R-32 | 15.3333
217902290 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AMM0AN | TURYH0724AMM0AN |  |  | TURYH1444BMM0AN | Non-Ducted Indoor Units | 138000 | 14 | 24.6 | 152000 | 4.34 | 118000 | 2.72 | R-32 | 11.5
217902288 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AMM0AN | TURYH0724AMM0AN |  |  | TURYH1444BMM0AN | Ducted Indoor Units | 138000 | 13.3 | 21.8 | 152000 | 3.88 | 118000 | 2.6 | R-32 | 11.5
217902302 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AMM0AN | TURYH0964AMM0AN |  |  | TURYH1924BMM0AN | Non-Ducted Indoor Units | 184000 | 13.8 | 24.2 | 204000 | 4.16 | 144000 | 2.67 | R-32 | 15.3333
217902300 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AMM0AN | TURYH0964AMM0AN |  |  | TURYH1924BMM0AN | Ducted Indoor Units | 184000 | 12.9 | 21.7 | 204000 | 3.86 | 144000 | 2.51 | R-32 | 15.3333
217902305 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AMM0AN | TURYH1204AMM0AN |  |  | TURYH2404BMM0AN | Ducted Indoor Units | 230000 | 12.8 | 21.6 | 258000 | 3.57 | 172000 | 2.49 | R-32 | 19.1667
217902306 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH1204AMM0AN | TURYH1204AMM0AN |  |  | TURYH2404BMM0AN | Non-Ducted Indoor Units | 230000 | 13.5 | 24.4 | 258000 | 3.92 | 172000 | 2.52 | R-32 | 19.1667
217901699 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A |  |  |  | PUHY-EM144TXU-A | Ducted Indoor Units | 138000 | 12.7 | 22 | 152000 | 3.7 | 118000 | 2.41 | R-32 | 11.5
217901700 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A |  |  |  | PUHY-EM144TXU-A | Non-Ducted Indoor Units | 138000 | 13.3 | 23.8 | 152000 | 4.16 | 118000 | 2.55 | R-32 | 11.5
217901703 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A |  |  |  | PUHY-EM168TXU-A | Ducted Indoor Units | 160000 | 11.9 | 21.3 | 178000 | 3.55 | 136000 | 2.33 | R-32 | 13.3333
217901704 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A |  |  |  | PUHY-EM168TXU-A | Non-Ducted Indoor Units | 160000 | 12.3 | 23.5 | 178000 | 3.89 | 136000 | 2.42 | R-32 | 13.3333
217901707 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192TXU-A |  |  |  | PUHY-EM192TXU-A | Ducted Indoor Units | 184000 | 11.3 | 21 | 184000 | 3.58 | 144000 | 2.3 | R-32 | 15.3333
217901708 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192TXU-A |  |  |  | PUHY-EM192TXU-A | Non-Ducted Indoor Units | 184000 | 11.7 | 22.5 | 184000 | 3.9 | 144000 | 2.37 | R-32 | 15.3333
217902123 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72TXU-A | PUHY-HM72TXU-A |  |  | PUHY-HM144TSXU-A | Ducted Indoor Units | 138000 | 13.5 | 22.9 | 152000 | 4.02 | 118000 | 2.72 | R-32 | 11.5
217902124 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72TXU-A | PUHY-HM72TXU-A |  |  | PUHY-HM144TSXU-A | Non-Ducted Indoor Units | 138000 | 14.3 | 26.2 | 152000 | 4.45 | 118000 | 2.81 | R-32 | 11.5
217901711 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96TXU-A | PUHY-HM96TXU-A |  |  | PUHY-HM192TSXU-A | Ducted Indoor Units | 184000 | 13.2 | 22.3 | 204000 | 3.94 | 144000 | 2.56 | R-32 | 15.3333
217901712 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96TXU-A | PUHY-HM96TXU-A |  |  | PUHY-HM192TSXU-A | Non-Ducted Indoor Units | 184000 | 14.2 | 24.9 | 204000 | 4.26 | 144000 | 2.74 | R-32 | 15.3333
217902127 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120TXU-A | PUHY-HM120TXU-A |  |  | PUHY-HM240TSXU-A | Ducted Indoor Units | 230000 | 13.2 | 22.3 | 258000 | 3.68 | 172000 | 2.54 | R-32 | 19.1667
217902128 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120TXU-A | PUHY-HM120TXU-A |  |  | PUHY-HM240TSXU-A | Non-Ducted Indoor Units | 230000 | 13.7 | 24.9 | 258000 | 4.05 | 172000 | 2.59 | R-32 | 19.1667
217901701 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A |  |  |  | PUHY-EM144YXU-A | Ducted Indoor Units | 138000 | 12.7 | 22 | 152000 | 3.7 | 118000 | 2.41 | R-32 | 11.5
217901702 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A |  |  |  | PUHY-EM144YXU-A | Non-Ducted Indoor Units | 138000 | 13.3 | 23.8 | 152000 | 4.16 | 118000 | 2.55 | R-32 | 11.5
217901705 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A |  |  |  | PUHY-EM168YXU-A | Ducted Indoor Units | 160000 | 11.9 | 21.3 | 178000 | 3.55 | 136000 | 2.33 | R-32 | 13.3333
217901706 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A |  |  |  | PUHY-EM168YXU-A | Non-Ducted Indoor Units | 160000 | 12.3 | 23.5 | 178000 | 3.89 | 136000 | 2.42 | R-32 | 13.3333
217901709 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192YXU-A |  |  |  | PUHY-EM192YXU-A | Ducted Indoor Units | 184000 | 11.3 | 21 | 184000 | 3.58 | 144000 | 2.3 | R-32 | 15.3333
217901710 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192YXU-A |  |  |  | PUHY-EM192YXU-A | Non-Ducted Indoor Units | 184000 | 11.7 | 22.5 | 184000 | 3.9 | 144000 | 2.37 | R-32 | 15.3333
217902125 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72YXU-A | PUHY-HM72YXU-A |  |  | PUHY-HM144YSXU-A | Ducted Indoor Units | 138000 | 13.5 | 22.9 | 152000 | 4.02 | 118000 | 2.72 | R-32 | 11.5
217902126 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM72YXU-A | PUHY-HM72YXU-A |  |  | PUHY-HM144YSXU-A | Non-Ducted Indoor Units | 138000 | 14.3 | 26.2 | 152000 | 4.45 | 118000 | 2.81 | R-32 | 11.5
217901713 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96YXU-A | PUHY-HM96YXU-A |  |  | PUHY-HM192YSXU-A | Ducted Indoor Units | 184000 | 13.2 | 22.3 | 204000 | 3.94 | 144000 | 2.56 | R-32 | 15.3333
217901714 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM96YXU-A | PUHY-HM96YXU-A |  |  | PUHY-HM192YSXU-A | Non-Ducted Indoor Units | 184000 | 14.2 | 24.9 | 204000 | 4.26 | 144000 | 2.74 | R-32 | 15.3333
217902129 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120YXU-A | PUHY-HM120YXU-A |  |  | PUHY-HM240YSXU-A | Ducted Indoor Units | 230000 | 13.2 | 22.3 | 258000 | 3.68 | 172000 | 2.54 | R-32 | 19.1667
217902130 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-HM120YXU-A | PUHY-HM120YXU-A |  |  | PUHY-HM240YSXU-A | Non-Ducted Indoor Units | 230000 | 13.7 | 24.9 | 258000 | 4.05 | 172000 | 2.59 | R-32 | 19.1667
217902213 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN |  |  |  | TUHYE1443AMM0AN | Non-Ducted Indoor Units | 138000 | 13.3 | 23.8 | 152000 | 4.16 | 118000 | 2.55 | R-32 | 11.5
217902211 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN |  |  |  | TUHYE1443AMM0AN | Ducted Indoor Units | 138000 | 12.7 | 22 | 152000 | 3.7 | 118000 | 2.41 | R-32 | 11.5
217902219 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN |  |  |  | TUHYE1683AMM0AN | Ducted Indoor Units | 160000 | 11.9 | 21.3 | 178000 | 3.55 | 136000 | 2.33 | R-32 | 13.3333
217902220 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN |  |  |  | TUHYE1683AMM0AN | Non-Ducted Indoor Units | 160000 | 12.3 | 23.5 | 178000 | 3.89 | 136000 | 2.42 | R-32 | 13.3333
217902225 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AMM0AN |  |  |  | TUHYE1923AMM0AN | Non-Ducted Indoor Units | 184000 | 11.7 | 22.5 | 184000 | 3.9 | 144000 | 2.37 | R-32 | 15.3333
217902223 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AMM0AN |  |  |  | TUHYE1923AMM0AN | Ducted Indoor Units | 184000 | 11.3 | 21 | 184000 | 3.58 | 144000 | 2.3 | R-32 | 15.3333
217902212 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AMM0AN | TUHYH0723AMM0AN |  |  | TUHYH1443BMM0AN | Ducted Indoor Units | 138000 | 13.5 | 22.9 | 152000 | 4.02 | 118000 | 2.72 | R-32 | 11.5
217902214 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AMM0AN | TUHYH0723AMM0AN |  |  | TUHYH1443BMM0AN | Non-Ducted Indoor Units | 138000 | 14.3 | 26.2 | 152000 | 4.45 | 118000 | 2.81 | R-32 | 11.5
217902224 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AMM0AN | TUHYH0963AMM0AN |  |  | TUHYH1923BMM0AN | Ducted Indoor Units | 184000 | 13.2 | 22.3 | 204000 | 3.94 | 144000 | 2.56 | R-32 | 15.3333
217902226 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AMM0AN | TUHYH0963AMM0AN |  |  | TUHYH1923BMM0AN | Non-Ducted Indoor Units | 184000 | 14.2 | 24.9 | 204000 | 4.26 | 144000 | 2.74 | R-32 | 15.3333
217902231 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AMM0AN | TUHYH1203AMM0AN |  |  | TUHYH2403BMM0AN | Ducted Indoor Units | 230000 | 13.2 | 22.3 | 258000 | 3.68 | 172000 | 2.54 | R-32 | 19.1667
217902232 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AMM0AN | TUHYH1203AMM0AN |  |  | TUHYH2403BMM0AN | Non-Ducted Indoor Units | 230000 | 13.7 | 24.9 | 258000 | 4.05 | 172000 | 2.59 | R-32 | 19.1667
217902215 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN |  |  |  | TUHYE1444AMM0AN | Ducted Indoor Units | 138000 | 12.7 | 22 | 152000 | 3.7 | 118000 | 2.41 | R-32 | 11.5
217902217 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN |  |  |  | TUHYE1444AMM0AN | Non-Ducted Indoor Units | 138000 | 13.3 | 23.8 | 152000 | 4.16 | 118000 | 2.55 | R-32 | 11.5
217902221 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN |  |  |  | TUHYE1684AMM0AN | Ducted Indoor Units | 160000 | 11.9 | 21.3 | 178000 | 3.55 | 136000 | 2.33 | R-32 | 13.3333
217902222 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN |  |  |  | TUHYE1684AMM0AN | Non-Ducted Indoor Units | 160000 | 12.3 | 23.5 | 178000 | 3.89 | 136000 | 2.42 | R-32 | 13.3333
217902227 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AMM0AN |  |  |  | TUHYE1924AMM0AN | Ducted Indoor Units | 184000 | 11.3 | 21 | 184000 | 3.58 | 144000 | 2.3 | R-32 | 15.3333
217902229 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AMM0AN |  |  |  | TUHYE1924AMM0AN | Non-Ducted Indoor Units | 184000 | 11.7 | 22.5 | 184000 | 3.9 | 144000 | 2.37 | R-32 | 15.3333
217902218 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AMM0AN | TUHYH0724AMM0AN |  |  | TUHYH1444BMM0AN | Non-Ducted Indoor Units | 138000 | 14.3 | 26.2 | 152000 | 4.45 | 118000 | 2.81 | R-32 | 11.5
217902216 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AMM0AN | TUHYH0724AMM0AN |  |  | TUHYH1444BMM0AN | Ducted Indoor Units | 138000 | 13.5 | 22.9 | 152000 | 4.02 | 118000 | 2.72 | R-32 | 11.5
217902230 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AMM0AN | TUHYH0964AMM0AN |  |  | TUHYH1924BMM0AN | Non-Ducted Indoor Units | 184000 | 14.2 | 24.9 | 204000 | 4.26 | 144000 | 2.74 | R-32 | 15.3333
217902228 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AMM0AN | TUHYH0964AMM0AN |  |  | TUHYH1924BMM0AN | Ducted Indoor Units | 184000 | 13.2 | 22.3 | 204000 | 3.94 | 144000 | 2.56 | R-32 | 15.3333
217902233 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AMM0AN | TUHYH1204AMM0AN |  |  | TUHYH2404BMM0AN | Ducted Indoor Units | 230000 | 13.2 | 22.3 | 258000 | 3.68 | 172000 | 2.54 | R-32 | 19.1667
217902234 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AMM0AN | TUHYH1204AMM0AN |  |  | TUHYH2404BMM0AN | Non-Ducted Indoor Units | 230000 | 13.7 | 24.9 | 258000 | 4.05 | 172000 | 2.59 | R-32 | 19.1667
218003068 | N/A | SAMSUNG | HMSV-A-CB | AM216HCVGFG |  |  |  | AM216HCVGFG | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218043883 | N/A | LENNOX | HMSV-A-CB | VPD216S6M-5Y |  |  |  | VPD216S6M-5Y | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218004911 | N/A | SAMSUNG | HMSV-A-CB | AM216HCVGFG |  |  |  | AM216HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218044019 | N/A | LENNOX | HMSV-A-CB | VPD216S6M-5Y |  |  |  | VPD216S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218043887 | N/A | LENNOX | HMSV-A-CB | VPD240S6M-5Y |  |  |  | VPD240S6M-5Y | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003072 | N/A | SAMSUNG | HMSV-A-CB | AM240HCVGFG |  |  |  | AM240HCVGFG | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003069 | N/A | SAMSUNG | HMSR-A-CB | AM216HCVGFS |  |  |  | AM216HCVGFS | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218004912 | N/A | SAMSUNG | HMSR-A-CB | AM216HCVGFS |  |  |  | AM216HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218043884 | N/A | LENNOX | HMSR-A-CB | VRD216S6M-5Y |  |  |  | VRD216S6M-5Y | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218044020 | N/A | LENNOX | HMSR-A-CB | VRD216S6M-5Y |  |  |  | VRD216S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218043888 | N/A | LENNOX | HMSR-A-CB | VRD240S6M-5Y |  |  |  | VRD240S6M-5Y | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003073 | N/A | SAMSUNG | HMSR-A-CB | AM240HCVGFS |  |  |  | AM240HCVGFS | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003070 | N/A | SAMSUNG | HMSV-A-CB | AM216HCVGJG |  |  |  | AM216HCVGJG | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218004913 | N/A | SAMSUNG | HMSV-A-CB | AM216HCVGJG |  |  |  | AM216HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218043885 | N/A | LENNOX | HMSV-A-CB | VPD216S6M-5G |  |  |  | VPD216S6M-5G | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218044021 | N/A | LENNOX | HMSV-A-CB | VPD216S6M-5G |  |  |  | VPD216S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218043889 | N/A | LENNOX | HMSV-A-CB | VPD240S6M-5G |  |  |  | VPD240S6M-5G | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003074 | N/A | SAMSUNG | HMSV-A-CB | AM240HCVGJG |  |  |  | AM240HCVGJG | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003071 | N/A | SAMSUNG | HMSR-A-CB | AM216HCVGJS |  |  |  | AM216HCVGJS | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218004914 | N/A | SAMSUNG | HMSR-A-CB | AM216HCVGJS |  |  |  | AM216HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218043886 | N/A | LENNOX | HMSR-A-CB | VRD216S6M-5G |  |  |  | VRD216S6M-5G | Ducted Indoor Units | 206000 | 10.15 | 20.6 | 232000 | 3.45 | 150000 | 2.6 | R-32 | 17.1667
218044022 | N/A | LENNOX | HMSR-A-CB | VRD216S6M-5G |  |  |  | VRD216S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.12 | 21.05 | 232000 | 3.32 | 150000 | 2.39 | R-32 | 17.1667
218043890 | N/A | LENNOX | HMSR-A-CB | VRD240S6M-5G |  |  |  | VRD240S6M-5G | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218003075 | N/A | SAMSUNG | HMSR-A-CB | AM240HCVGJS |  |  |  | AM240HCVGJS | Ducted Indoor Units | 228000 | 9.95 | 20.3 | 258000 | 3.25 | 168000 | 2.45 | R-32 | 19
218043935 | N/A | LENNOX | HMSV-A-CB | VPD144S6M-5Y |  |  |  | VPD144S6M-5Y | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218044007 | N/A | LENNOX | HMSV-A-CB | VPD144S6M-5Y |  |  |  | VPD144S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218043871 | N/A | LENNOX | HMSV-A-CB | VPD144S6M-5Y |  |  |  | VPD144S6M-5Y | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218004899 | N/A | SAMSUNG | HMSV-A-CB | AM144HCVGFG |  |  |  | AM144HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218003120 | N/A | SAMSUNG | HMSV-A-CB | AM144HCVGFG |  |  |  | AM144HCVGFG | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218003056 | N/A | SAMSUNG | HMSV-A-CB | AM144HCVGFG |  |  |  | AM144HCVGFG | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218003060 | N/A | SAMSUNG | HMSV-A-CB | AM168HCVGFG |  |  |  | AM168HCVGFG | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218003124 | N/A | SAMSUNG | HMSV-A-CB | AM168HCVGFG |  |  |  | AM168HCVGFG | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218004903 | N/A | SAMSUNG | HMSV-A-CB | AM168HCVGFG |  |  |  | AM168HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218043875 | N/A | LENNOX | HMSV-A-CB | VPD168S6M-5Y |  |  |  | VPD168S6M-5Y | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218044011 | N/A | LENNOX | HMSV-A-CB | VPD168S6M-5Y |  |  |  | VPD168S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218043939 | N/A | LENNOX | HMSV-A-CB | VPD168S6M-5Y |  |  |  | VPD168S6M-5Y | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218044015 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5Y |  |  |  | VPD192S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218043879 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5Y |  |  |  | VPD192S6M-5Y | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218004907 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG |  |  |  | AM192HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218003064 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG |  |  |  | AM192HCVGFG | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218043936 | N/A | LENNOX | HMSR-A-CB | VRD144S6M-5Y |  |  |  | VRD144S6M-5Y | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218044008 | N/A | LENNOX | HMSR-A-CB | VRD144S6M-5Y |  |  |  | VRD144S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218043872 | N/A | LENNOX | HMSR-A-CB | VRD144S6M-5Y |  |  |  | VRD144S6M-5Y | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218004900 | N/A | SAMSUNG | HMSR-A-CB | AM144HCVGFS |  |  |  | AM144HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218003121 | N/A | SAMSUNG | HMSR-A-CB | AM144HCVGFS |  |  |  | AM144HCVGFS | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218003057 | N/A | SAMSUNG | HMSR-A-CB | AM144HCVGFS |  |  |  | AM144HCVGFS | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218003061 | N/A | SAMSUNG | HMSR-A-CB | AM168HCVGFS |  |  |  | AM168HCVGFS | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218003125 | N/A | SAMSUNG | HMSR-A-CB | AM168HCVGFS |  |  |  | AM168HCVGFS | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218004904 | N/A | SAMSUNG | HMSR-A-CB | AM168HCVGFS |  |  |  | AM168HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218043876 | N/A | LENNOX | HMSR-A-CB | VRD168S6M-5Y |  |  |  | VRD168S6M-5Y | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218044012 | N/A | LENNOX | HMSR-A-CB | VRD168S6M-5Y |  |  |  | VRD168S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218043940 | N/A | LENNOX | HMSR-A-CB | VRD168S6M-5Y |  |  |  | VRD168S6M-5Y | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218044016 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5Y |  |  |  | VRD192S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218043880 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5Y |  |  |  | VRD192S6M-5Y | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218004908 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS |  |  |  | AM192HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218003065 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS |  |  |  | AM192HCVGFS | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218043937 | N/A | LENNOX | HMSV-A-CB | VPD144S6M-5G |  |  |  | VPD144S6M-5G | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218044009 | N/A | LENNOX | HMSV-A-CB | VPD144S6M-5G |  |  |  | VPD144S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218043873 | N/A | LENNOX | HMSV-A-CB | VPD144S6M-5G |  |  |  | VPD144S6M-5G | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218004901 | N/A | SAMSUNG | HMSV-A-CB | AM144HCVGJG |  |  |  | AM144HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218003122 | N/A | SAMSUNG | HMSV-A-CB | AM144HCVGJG |  |  |  | AM144HCVGJG | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218003058 | N/A | SAMSUNG | HMSV-A-CB | AM144HCVGJG |  |  |  | AM144HCVGJG | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218003062 | N/A | SAMSUNG | HMSV-A-CB | AM168HCVGJG |  |  |  | AM168HCVGJG | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218003126 | N/A | SAMSUNG | HMSV-A-CB | AM168HCVGJG |  |  |  | AM168HCVGJG | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218004905 | N/A | SAMSUNG | HMSV-A-CB | AM168HCVGJG |  |  |  | AM168HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218043877 | N/A | LENNOX | HMSV-A-CB | VPD168S6M-5G |  |  |  | VPD168S6M-5G | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218044013 | N/A | LENNOX | HMSV-A-CB | VPD168S6M-5G |  |  |  | VPD168S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218043941 | N/A | LENNOX | HMSV-A-CB | VPD168S6M-5G |  |  |  | VPD168S6M-5G | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218044017 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5G |  |  |  | VPD192S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218043881 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5G |  |  |  | VPD192S6M-5G | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218004909 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG |  |  |  | AM192HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218003066 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG |  |  |  | AM192HCVGJG | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218043938 | N/A | LENNOX | HMSR-A-CB | VRD144S6M-5G |  |  |  | VRD144S6M-5G | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218044010 | N/A | LENNOX | HMSR-A-CB | VRD144S6M-5G |  |  |  | VRD144S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218043874 | N/A | LENNOX | HMSR-A-CB | VRD144S6M-5G |  |  |  | VRD144S6M-5G | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218004902 | N/A | SAMSUNG | HMSR-A-CB | AM144HCVGJS |  |  |  | AM144HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 23.67 | 154000 | 3.66 | 100000 | 2.69 | R-32 | 11.5
218003123 | N/A | SAMSUNG | HMSR-A-CB | AM144HCVGJS |  |  |  | AM144HCVGJS | Non-Ducted Indoor Units | 138000 | 11.3 | 25.16 | 154000 | 3.65 | 100000 | 2.69 | R-32 | 11.5
218003059 | N/A | SAMSUNG | HMSR-A-CB | AM144HCVGJS |  |  |  | AM144HCVGJS | Ducted Indoor Units | 138000 | 11.8 | 22.19 | 154000 | 3.68 | 100000 | 2.7 | R-32 | 11.5
218003063 | N/A | SAMSUNG | HMSR-A-CB | AM168HCVGJS |  |  |  | AM168HCVGJS | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218003127 | N/A | SAMSUNG | HMSR-A-CB | AM168HCVGJS |  |  |  | AM168HCVGJS | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218004906 | N/A | SAMSUNG | HMSR-A-CB | AM168HCVGJS |  |  |  | AM168HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218043878 | N/A | LENNOX | HMSR-A-CB | VRD168S6M-5G |  |  |  | VRD168S6M-5G | Ducted Indoor Units | 160000 | 10.6 | 21.19 | 180000 | 3.67 | 118000 | 2.56 | R-32 | 13.3333
218044014 | N/A | LENNOX | HMSR-A-CB | VRD168S6M-5G |  |  |  | VRD168S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.37 | 22.05 | 180000 | 3.61 | 118000 | 2.53 | R-32 | 13.3333
218043942 | N/A | LENNOX | HMSR-A-CB | VRD168S6M-5G |  |  |  | VRD168S6M-5G | Non-Ducted Indoor Units | 160000 | 10.15 | 22.91 | 180000 | 3.55 | 118000 | 2.51 | R-32 | 13.3333
218044018 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5G |  |  |  | VRD192S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218043882 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5G |  |  |  | VRD192S6M-5G | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218004910 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS |  |  |  | AM192HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 22.3 | 206000 | 3.37 | 134000 | 2.43 | R-32 | 15.3333
218003067 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS |  |  |  | AM192HCVGJS | Ducted Indoor Units | 184000 | 11 | 22.1 | 206000 | 3.55 | 134000 | 2.65 | R-32 | 15.3333
218005679 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG |  |  | AM144HCVTFG | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218005683 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG |  |  | AM168HCVTFG | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218005711 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG |  |  | AM144HCVTFG | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218005715 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG |  |  | AM168HCVTFG | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218005751 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG |  |  | AM144HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218005755 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG |  |  | AM168HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218044075 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y |  |  | VPD144L6M-5Y | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218044079 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD096L6M-5Y |  |  | VPD168L6M-5Y | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218044107 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y |  |  | VPD144L6M-5Y | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218044111 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD096L6M-5Y |  |  | VPD168L6M-5Y | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218044119 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD072L6M-5Y |  | VPD216L6M-5Y | Non-Ducted Indoor Units | 206000 | 11.6 | 24.49 | 232000 | 3.75 | 232000 | 2.25 | R-32 | 17.1667
218044123 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD096L6M-5Y |  | VPD240L6M-5Y | Non-Ducted Indoor Units | 228000 | 11.3 | 24.02 | 258000 | 3.67 | 258000 | 2.13 | R-32 | 19
218044147 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y |  |  | VPD144L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218044151 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD096L6M-5Y |  |  | VPD168L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218044167 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD072L6M-5Y |  | VPD216L6M-5Y | Ducted Indoor Units | 206000 | 11.35 | 23.22 | 232000 | 3.85 | 232000 | 2.36 | R-32 | 17.1667
218044171 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD096L6M-5Y |  | VPD240L6M-5Y | Ducted Indoor Units | 228000 | 10.35 | 22.85 | 258000 | 3.82 | 258000 | 2.24 | R-32 | 19
218044179 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD096L6M-5Y |  | VPD240L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.82 | 23.43 | 258000 | 3.74 | 258000 | 2.18 | R-32 | 19
218044175 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD072L6M-5Y |  | VPD216L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.47 | 23.85 | 232000 | 3.8 | 232000 | 2.3 | R-32 | 17.1667
218044155 | N/A | LENNOX | HMSV-A-CB | VPD096L6M-5Y | VPD096L6M-5Y |  |  | VPD192L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 23.16 | 206000 | 3.79 | 206000 | 2.23 | R-32 | 15.3333
218044115 | N/A | LENNOX | HMSV-A-CB | VPD096L6M-5Y | VPD096L6M-5Y |  |  | VPD192L6M-5Y | Non-Ducted Indoor Units | 184000 | 11.75 | 23.83 | 206000 | 3.76 | 206000 | 2.2 | R-32 | 15.3333
218044083 | N/A | LENNOX | HMSV-A-CB | VPD096L6M-5Y | VPD096L6M-5Y |  |  | VPD192L6M-5Y | Ducted Indoor Units | 184000 | 11.65 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-32 | 15.3333
218044148 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y |  |  | VRD144L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218044152 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD096L6M-5Y |  |  | VRD168L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218044172 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD096L6M-5Y |  | VRD240L6M-5Y | Ducted Indoor Units | 228000 | 10.35 | 22.85 | 258000 | 3.82 | 258000 | 2.24 | R-32 | 19
218044168 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD072L6M-5Y |  | VRD216L6M-5Y | Ducted Indoor Units | 206000 | 11.35 | 23.22 | 232000 | 3.85 | 232000 | 2.36 | R-32 | 17.1667
218044176 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD072L6M-5Y |  | VRD216L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.47 | 23.85 | 232000 | 3.8 | 232000 | 2.3 | R-32 | 17.1667
218044180 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD096L6M-5Y |  | VRD240L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.82 | 23.43 | 258000 | 3.74 | 258000 | 2.18 | R-32 | 19
218044108 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y |  |  | VRD144L6M-5Y | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218044080 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD096L6M-5Y |  |  | VRD168L6M-5Y | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218044112 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD096L6M-5Y |  |  | VRD168L6M-5Y | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218044124 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD096L6M-5Y |  | VRD240L6M-5Y | Non-Ducted Indoor Units | 228000 | 11.3 | 24.02 | 258000 | 3.67 | 258000 | 2.13 | R-32 | 19
218044120 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD072L6M-5Y |  | VRD216L6M-5Y | Non-Ducted Indoor Units | 206000 | 11.6 | 24.49 | 232000 | 3.75 | 232000 | 2.25 | R-32 | 17.1667
218044076 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y |  |  | VRD144L6M-5Y | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218005712 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS |  |  | AM144HCVTFS | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218005716 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS |  |  | AM168HCVTFS | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218005684 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS |  |  | AM168HCVTFS | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218005680 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS |  |  | AM144HCVTFS | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218005756 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS |  |  | AM168HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218005752 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS |  |  | AM144HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218044116 | N/A | LENNOX | HMSR-A-CB | VRD096L6M-5Y | VRD096L6M-5Y |  |  | VRD192L6M-5Y | Non-Ducted Indoor Units | 184000 | 11.75 | 23.83 | 206000 | 3.76 | 206000 | 2.2 | R-32 | 15.3333
218044084 | N/A | LENNOX | HMSR-A-CB | VRD096L6M-5Y | VRD096L6M-5Y |  |  | VRD192L6M-5Y | Ducted Indoor Units | 184000 | 11.65 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-32 | 15.3333
218044156 | N/A | LENNOX | HMSR-A-CB | VRD096L6M-5Y | VRD096L6M-5Y |  |  | VRD192L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 23.16 | 206000 | 3.79 | 206000 | 2.23 | R-32 | 15.3333
218005681 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG |  |  | AM144HCVTJG | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218005685 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG |  |  | AM168HCVTJG | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218005713 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG |  |  | AM144HCVTJG | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218005717 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG |  |  | AM168HCVTJG | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218005753 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG |  |  | AM144HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218005757 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG |  |  | AM168HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218044077 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G |  |  | VPD144L6M-5G | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218044109 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G |  |  | VPD144L6M-5G | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218044081 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD096L6M-5G |  |  | VPD168L6M-5G | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218044113 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD096L6M-5G |  |  | VPD168L6M-5G | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218044121 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD072L6M-5G |  | VPD216L6M-5G | Non-Ducted Indoor Units | 206000 | 11.6 | 24.49 | 232000 | 3.75 | 232000 | 2.25 | R-32 | 17.1667
218044125 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD096L6M-5G |  | VPD240L6M-5G | Non-Ducted Indoor Units | 228000 | 11.3 | 24.02 | 258000 | 3.67 | 258000 | 2.13 | R-32 | 19
218044149 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G |  |  | VPD144L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218044153 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD096L6M-5G |  |  | VPD168L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218044169 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD072L6M-5G |  | VPD216L6M-5G | Ducted Indoor Units | 206000 | 11.35 | 23.22 | 232000 | 3.85 | 232000 | 2.36 | R-32 | 17.1667
218044173 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD096L6M-5G |  | VPD240L6M-5G | Ducted Indoor Units | 228000 | 10.35 | 22.85 | 258000 | 3.82 | 258000 | 2.24 | R-32 | 19
218044181 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD096L6M-5G |  | VPD240L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.82 | 23.43 | 258000 | 3.74 | 258000 | 2.18 | R-32 | 19
218044177 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD072L6M-5G |  | VPD216L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.47 | 23.85 | 232000 | 3.8 | 232000 | 2.3 | R-32 | 17.1667
218044157 | N/A | LENNOX | HMSV-A-CB | VPD096L6M-5G | VPD096L6M-5G |  |  | VPD192L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 23.16 | 206000 | 3.79 | 206000 | 2.23 | R-32 | 15.3333
218044117 | N/A | LENNOX | HMSV-A-CB | VPD096L6M-5G | VPD096L6M-5G |  |  | VPD192L6M-5G | Non-Ducted Indoor Units | 184000 | 11.75 | 23.83 | 206000 | 3.76 | 206000 | 2.2 | R-32 | 15.3333
218044085 | N/A | LENNOX | HMSV-A-CB | VPD096L6M-5G | VPD096L6M-5G |  |  | VPD192L6M-5G | Ducted Indoor Units | 184000 | 11.65 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-32 | 15.3333
218044150 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G |  |  | VRD144L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218044154 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD096L6M-5G |  |  | VRD168L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218044174 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD096L6M-5G |  | VRD240L6M-5G | Ducted Indoor Units | 228000 | 10.35 | 22.85 | 258000 | 3.82 | 258000 | 2.24 | R-32 | 19
218044170 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD072L6M-5G |  | VRD216L6M-5G | Ducted Indoor Units | 206000 | 11.35 | 23.22 | 232000 | 3.85 | 232000 | 2.36 | R-32 | 17.1667
218044178 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD072L6M-5G |  | VRD216L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.47 | 23.85 | 232000 | 3.8 | 232000 | 2.3 | R-32 | 17.1667
218044182 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD096L6M-5G |  | VRD240L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.82 | 23.43 | 258000 | 3.74 | 258000 | 2.18 | R-32 | 19
218044110 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G |  |  | VRD144L6M-5G | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218044082 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD096L6M-5G |  |  | VRD168L6M-5G | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218044114 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD096L6M-5G |  |  | VRD168L6M-5G | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218044126 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD096L6M-5G |  | VRD240L6M-5G | Non-Ducted Indoor Units | 228000 | 11.3 | 24.02 | 258000 | 3.67 | 258000 | 2.13 | R-32 | 19
218044122 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD072L6M-5G |  | VRD216L6M-5G | Non-Ducted Indoor Units | 206000 | 11.6 | 24.49 | 232000 | 3.75 | 232000 | 2.25 | R-32 | 17.1667
218044078 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G |  |  | VRD144L6M-5G | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218005714 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS |  |  | AM144HCVTJS | Non-Ducted Indoor Units | 138000 | 11.95 | 25.44 | 154000 | 3.97 | 154000 | 2.37 | R-32 | 11.5
218005718 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS |  |  | AM168HCVTJS | Non-Ducted Indoor Units | 160000 | 12.1 | 25.12 | 180000 | 3.83 | 180000 | 2.29 | R-32 | 13.3333
218005686 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS |  |  | AM168HCVTJS | Ducted Indoor Units | 160000 | 11.65 | 22.91 | 180000 | 3.88 | 180000 | 2.39 | R-32 | 13.3333
218005682 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS |  |  | AM144HCVTJS | Ducted Indoor Units | 138000 | 11.55 | 20.32 | 154000 | 3.93 | 154000 | 2.47 | R-32 | 11.5
218005758 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS |  |  | AM168HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.87 | 24.01 | 180000 | 3.85 | 180000 | 2.34 | R-32 | 13.3333
218005754 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS |  |  | AM144HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.88 | 154000 | 3.95 | 154000 | 2.42 | R-32 | 11.5
218044118 | N/A | LENNOX | HMSR-A-CB | VRD096L6M-5G | VRD096L6M-5G |  |  | VRD192L6M-5G | Non-Ducted Indoor Units | 184000 | 11.75 | 23.83 | 206000 | 3.76 | 206000 | 2.2 | R-32 | 15.3333
218044086 | N/A | LENNOX | HMSR-A-CB | VRD096L6M-5G | VRD096L6M-5G |  |  | VRD192L6M-5G | Ducted Indoor Units | 184000 | 11.65 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-32 | 15.3333
218044158 | N/A | LENNOX | HMSR-A-CB | VRD096L6M-5G | VRD096L6M-5G |  |  | VRD192L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 23.16 | 206000 | 3.79 | 206000 | 2.23 | R-32 | 15.3333
218066395 | N/A | MIDEA | HMSR-A-CB | MV8-2R72V2XN10C | MV8-2R72V2XN10C |  |  | MV8-2R144V2XN10C | Ducted Indoor Units | 138000 | 11.9 | 21.8 | 152000 | 3.63 | 118000 | 2.35 | R-454B | 11.5
218066396 | N/A | MIDEA | HMSR-A-CB | MV8-2R72V2XN10C | MV8-2R72V2XN10C |  |  | MV8-2R144V2XN10C | Non-Ducted Indoor Units | 138000 | 12.4 | 24.2 | 152000 | 3.96 | 118000 | 2.5 | R-454B | 11.5
218066397 | N/A | MIDEA | HMSR-A-CB | MV8-2R96V2XN10C | MV8-2R96V2XN10C |  |  | MV8-2R192V2XN10C | Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.57 | 144000 | 2.28 | R-454B | 15.3333
218066398 | N/A | MIDEA | HMSR-A-CB | MV8-2R96V2XN10C | MV8-2R96V2XN10C |  |  | MV8-2R192V2XN10C | Non-Ducted Indoor Units | 184000 | 11.7 | 24 | 206000 | 3.73 | 144000 | 2.45 | R-454B | 15.3333
218066399 | N/A | MIDEA | HMSR-A-CB | MV8-2R120V2XN10C | MV8-2R120V2XN10C |  |  | MV8-2R240V2XN10C | Ducted Indoor Units | 230000 | 10.9 | 21 | 258000 | 3.46 | 172000 | 2.27 | R-454B | 19.1667
218066405 | N/A | MIDEA | HMSR-A-CB | MV8-2R120V2XN10C | MV8-2R120V2XN10C |  |  | MV8-2R240V2XN10C | Non-Ducted Indoor Units | 230000 | 11 | 23 | 258000 | 3.52 | 172000 | 2.37 | R-454B | 19.1667
218066400 | N/A | MIDEA | HMSR-A-CB | MV8-2R72V2ZN10C | MV8-2R72V2ZN10C |  |  | MV8-2R144V2ZN10C | Ducted Indoor Units | 138000 | 11.9 | 21.8 | 152000 | 3.63 | 118000 | 2.35 | R-454B | 11.5
218066401 | N/A | MIDEA | HMSR-A-CB | MV8-2R72V2ZN10C | MV8-2R72V2ZN10C |  |  | MV8-2R144V2ZN10C | Non-Ducted Indoor Units | 138000 | 12.4 | 24.2 | 152000 | 3.96 | 118000 | 2.5 | R-454B | 11.5
218066402 | N/A | MIDEA | HMSR-A-CB | MV8-2R96V2ZN10C | MV8-2R96V2ZN10C |  |  | MV8-2R192V2ZN10C | Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.57 | 144000 | 2.28 | R-454B | 15.3333
218066403 | N/A | MIDEA | HMSR-A-CB | MV8-2R96V2ZN10C | MV8-2R96V2ZN10C |  |  | MV8-2R192V2ZN10C | Non-Ducted Indoor Units | 184000 | 11.7 | 24 | 206000 | 3.73 | 144000 | 2.45 | R-454B | 15.3333
218066404 | N/A | MIDEA | HMSR-A-CB | MV8-2R120V2ZN10C | MV8-2R120V2ZN10C |  |  | MV8-2R240V2ZN10C | Ducted Indoor Units | 230000 | 10.9 | 21 | 258000 | 3.46 | 172000 | 2.27 | R-454B | 19.1667
218066406 | N/A | MIDEA | HMSR-A-CB | MV8-2R120V2ZN10C | MV8-2R120V2ZN10C |  |  | MV8-2R240V2ZN10C | Non-Ducted Indoor Units | 230000 | 11 | 23 | 258000 | 3.52 | 172000 | 2.37 | R-454B | 19.1667
218036976 | N/A | DAIKIN | HMSV-A-CB | RXYA144AATJ* |  |  |  | RXYA144AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11 | 21 | 138000 | 3.32 | 90000 | 2.1 | R-32 | 11.5
218036940 | N/A | DAIKIN | HMSV-A-CB | RXYA144AATJ* |  |  |  | RXYA144AATJ* | Ducted Indoor Units | 138000 | 11 | 19.6 | 138000 | 3.35 | 90000 | 2.1 | R-32 | 11.5
218036904 | N/A | DAIKIN | HMSV-A-CB | RXYA144AATJ* |  |  |  | RXYA144AATJ* | Non-Ducted Indoor Units | 138000 | 11 | 22.4 | 138000 | 3.3 | 90000 | 2.1 | R-32 | 11.5
218036905 | N/A | DAIKIN | HMSV-A-CB | RXYA168AATJ* |  |  |  | RXYA168AATJ* | Non-Ducted Indoor Units | 156000 | 10.7 | 21.7 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218036941 | N/A | DAIKIN | HMSV-A-CB | RXYA168AATJ* |  |  |  | RXYA168AATJ* | Ducted Indoor Units | 156000 | 10.7 | 18.8 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218036977 | N/A | DAIKIN | HMSV-A-CB | RXYA168AATJ* |  |  |  | RXYA168AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.7 | 20.25 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218036978 | N/A | DAIKIN | HMSV-A-CB | RXYA192AATJ* |  |  |  | RXYA192AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 20.9 | 184000 | 3.44 | 130000 | 2.24 | R-32 | 15.3333
218036942 | N/A | DAIKIN | HMSV-A-CB | RXYA192AATJ* |  |  |  | RXYA192AATJ* | Ducted Indoor Units | 184000 | 11.3 | 19.4 | 184000 | 3.4 | 130000 | 2.24 | R-32 | 15.3333
218036906 | N/A | DAIKIN | HMSV-A-CB | RXYA192AATJ* |  |  |  | RXYA192AATJ* | Non-Ducted Indoor Units | 184000 | 11.4 | 22.4 | 184000 | 3.48 | 130000 | 2.24 | R-32 | 15.3333
218036907 | N/A | DAIKIN | HMSV-A-CB | RXYA216AATJ* |  |  |  | RXYA216AATJ* | Non-Ducted Indoor Units | 206000 | 10.9 | 21.7 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218036943 | N/A | DAIKIN | HMSV-A-CB | RXYA216AATJ* |  |  |  | RXYA216AATJ* | Ducted Indoor Units | 206000 | 11 | 18.7 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218036979 | N/A | DAIKIN | HMSV-A-CB | RXYA216AATJ* |  |  |  | RXYA216AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 20.2 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218036980 | N/A | DAIKIN | HMSV-A-CB | RXYA240AATJ* |  |  |  | RXYA240AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 19.2 | 220000 | 3.25 | 150000 | 2.18 | R-32 | 19
218036944 | N/A | DAIKIN | HMSV-A-CB | RXYA240AATJ* |  |  |  | RXYA240AATJ* | Ducted Indoor Units | 228000 | 10.7 | 18 | 220000 | 3.25 | 150000 | 2.18 | R-32 | 19
218036908 | N/A | DAIKIN | HMSV-A-CB | RXYA240AATJ* |  |  |  | RXYA240AATJ* | Non-Ducted Indoor Units | 228000 | 10.7 | 20.4 | 220000 | 3.25 | 150000 | 2.18 | R-32 | 19
218036994 | N/A | DAIKIN | HMSV-A-CB | RXYA144AAYD* |  |  |  | RXYA144AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11 | 21 | 138000 | 3.32 | 90000 | 2.1 | R-32 | 11.5
218036958 | N/A | DAIKIN | HMSV-A-CB | RXYA144AAYD* |  |  |  | RXYA144AAYD* | Ducted Indoor Units | 138000 | 11 | 19.6 | 138000 | 3.35 | 90000 | 2.1 | R-32 | 11.5
218036922 | N/A | DAIKIN | HMSV-A-CB | RXYA144AAYD* |  |  |  | RXYA144AAYD* | Non-Ducted Indoor Units | 138000 | 11 | 22.4 | 138000 | 3.3 | 90000 | 2.1 | R-32 | 11.5
218036923 | N/A | DAIKIN | HMSV-A-CB | RXYA168AAYD* |  |  |  | RXYA168AAYD* | Non-Ducted Indoor Units | 156000 | 10.7 | 21.7 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218036959 | N/A | DAIKIN | HMSV-A-CB | RXYA168AAYD* |  |  |  | RXYA168AAYD* | Ducted Indoor Units | 156000 | 10.7 | 18.8 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218036995 | N/A | DAIKIN | HMSV-A-CB | RXYA168AAYD* |  |  |  | RXYA168AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.7 | 20.25 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218036996 | N/A | DAIKIN | HMSV-A-CB | RXYA192AAYD* |  |  |  | RXYA192AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 20.9 | 184000 | 3.44 | 130000 | 2.24 | R-32 | 15.3333
218036960 | N/A | DAIKIN | HMSV-A-CB | RXYA192AAYD* |  |  |  | RXYA192AAYD* | Ducted Indoor Units | 184000 | 11.3 | 19.4 | 184000 | 3.4 | 130000 | 2.24 | R-32 | 15.3333
218036924 | N/A | DAIKIN | HMSV-A-CB | RXYA192AAYD* |  |  |  | RXYA192AAYD* | Non-Ducted Indoor Units | 184000 | 11.4 | 22.4 | 184000 | 3.48 | 130000 | 2.24 | R-32 | 15.3333
218036925 | N/A | DAIKIN | HMSV-A-CB | RXYA216AAYD* |  |  |  | RXYA216AAYD* | Non-Ducted Indoor Units | 206000 | 10.9 | 21.7 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218036961 | N/A | DAIKIN | HMSV-A-CB | RXYA216AAYD* |  |  |  | RXYA216AAYD* | Ducted Indoor Units | 206000 | 11 | 18.7 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218036997 | N/A | DAIKIN | HMSV-A-CB | RXYA216AAYD* |  |  |  | RXYA216AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 20.2 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218036998 | N/A | DAIKIN | HMSV-A-CB | RXYA240AAYD* |  |  |  | RXYA240AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 19.2 | 220000 | 3.25 | 150000 | 2.18 | R-32 | 19
218036962 | N/A | DAIKIN | HMSV-A-CB | RXYA240AAYD* |  |  |  | RXYA240AAYD* | Ducted Indoor Units | 228000 | 10.7 | 18 | 220000 | 3.25 | 150000 | 2.18 | R-32 | 19
218036926 | N/A | DAIKIN | HMSV-A-CB | RXYA240AAYD* |  |  |  | RXYA240AAYD* | Non-Ducted Indoor Units | 228000 | 10.7 | 20.4 | 220000 | 3.25 | 150000 | 2.18 | R-32 | 19
218037084 | N/A | DAIKIN | HMSR-A-CB | REYA144AATJ* |  |  |  | REYA144AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.1 | 21.2 | 138000 | 3.32 | 90000 | 2.1 | R-32 | 11.5
218037048 | N/A | DAIKIN | HMSR-A-CB | REYA144AATJ* |  |  |  | REYA144AATJ* | Ducted Indoor Units | 138000 | 11 | 19.7 | 138000 | 3.35 | 90000 | 2.1 | R-32 | 11.5
218037012 | N/A | DAIKIN | HMSR-A-CB | REYA144AATJ* |  |  |  | REYA144AATJ* | Non-Ducted Indoor Units | 138000 | 11.2 | 22.7 | 138000 | 3.3 | 90000 | 2.1 | R-32 | 11.5
218037013 | N/A | DAIKIN | HMSR-A-CB | REYA168AATJ* |  |  |  | REYA168AATJ* | Non-Ducted Indoor Units | 156000 | 10.7 | 21.7 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218037049 | N/A | DAIKIN | HMSR-A-CB | REYA168AATJ* |  |  |  | REYA168AATJ* | Ducted Indoor Units | 156000 | 10.7 | 19 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218037085 | N/A | DAIKIN | HMSR-A-CB | REYA168AATJ* |  |  |  | REYA168AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.7 | 20.35 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218037086 | N/A | DAIKIN | HMSR-A-CB | REYA192AATJ* |  |  |  | REYA192AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21 | 184000 | 3.44 | 130000 | 2.25 | R-32 | 15.3333
218037050 | N/A | DAIKIN | HMSR-A-CB | REYA192AATJ* |  |  |  | REYA192AATJ* | Ducted Indoor Units | 184000 | 11.3 | 19.8 | 184000 | 3.4 | 130000 | 2.25 | R-32 | 15.3333
218037014 | N/A | DAIKIN | HMSR-A-CB | REYA192AATJ* |  |  |  | REYA192AATJ* | Non-Ducted Indoor Units | 184000 | 11.4 | 22.2 | 184000 | 3.48 | 130000 | 2.25 | R-32 | 15.3333
218037015 | N/A | DAIKIN | HMSR-A-CB | REYA216AATJ* |  |  |  | REYA216AATJ* | Non-Ducted Indoor Units | 206000 | 10.9 | 21.8 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218037051 | N/A | DAIKIN | HMSR-A-CB | REYA216AATJ* |  |  |  | REYA216AATJ* | Ducted Indoor Units | 206000 | 11 | 18.7 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218037087 | N/A | DAIKIN | HMSR-A-CB | REYA216AATJ* |  |  |  | REYA216AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 20.25 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218037088 | N/A | DAIKIN | HMSR-A-CB | REYA240AATJ* |  |  |  | REYA240AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 19.2 | 220000 | 3.3 | 150000 | 2.2 | R-32 | 19
218037052 | N/A | DAIKIN | HMSR-A-CB | REYA240AATJ* |  |  |  | REYA240AATJ* | Ducted Indoor Units | 228000 | 10.7 | 18 | 220000 | 3.3 | 150000 | 2.2 | R-32 | 19
218037016 | N/A | DAIKIN | HMSR-A-CB | REYA240AATJ* |  |  |  | REYA240AATJ* | Non-Ducted Indoor Units | 228000 | 10.7 | 20.4 | 220000 | 3.3 | 150000 | 2.2 | R-32 | 19
218037102 | N/A | DAIKIN | HMSR-A-CB | REYA144AAYD* |  |  |  | REYA144AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.1 | 21.2 | 138000 | 3.32 | 90000 | 2.1 | R-32 | 11.5
218037030 | N/A | DAIKIN | HMSR-A-CB | REYA144AAYD* |  |  |  | REYA144AAYD* | Non-Ducted Indoor Units | 138000 | 11.2 | 22.7 | 138000 | 3.3 | 90000 | 2.1 | R-32 | 11.5
218037066 | N/A | DAIKIN | HMSR-A-CB | REYA144AAYD* |  |  |  | REYA144AAYD* | Ducted Indoor Units | 138000 | 11 | 19.7 | 138000 | 3.35 | 90000 | 2.1 | R-32 | 11.5
218037067 | N/A | DAIKIN | HMSR-A-CB | REYA168AAYD* |  |  |  | REYA168AAYD* | Ducted Indoor Units | 156000 | 10.7 | 19 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218037031 | N/A | DAIKIN | HMSR-A-CB | REYA168AAYD* |  |  |  | REYA168AAYD* | Non-Ducted Indoor Units | 156000 | 10.7 | 21.7 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218037103 | N/A | DAIKIN | HMSR-A-CB | REYA168AAYD* |  |  |  | REYA168AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.7 | 20.35 | 156000 | 3.3 | 104000 | 2.1 | R-32 | 13
218037104 | N/A | DAIKIN | HMSR-A-CB | REYA192AAYD* |  |  |  | REYA192AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21 | 184000 | 3.44 | 130000 | 2.25 | R-32 | 15.3333
218037032 | N/A | DAIKIN | HMSR-A-CB | REYA192AAYD* |  |  |  | REYA192AAYD* | Non-Ducted Indoor Units | 184000 | 11.4 | 22.2 | 184000 | 3.48 | 130000 | 2.25 | R-32 | 15.3333
218037068 | N/A | DAIKIN | HMSR-A-CB | REYA192AAYD* |  |  |  | REYA192AAYD* | Ducted Indoor Units | 184000 | 11.3 | 19.8 | 184000 | 3.4 | 130000 | 2.25 | R-32 | 15.3333
218037069 | N/A | DAIKIN | HMSR-A-CB | REYA216AAYD* |  |  |  | REYA216AAYD* | Ducted Indoor Units | 206000 | 11 | 18.7 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218037033 | N/A | DAIKIN | HMSR-A-CB | REYA216AAYD* |  |  |  | REYA216AAYD* | Non-Ducted Indoor Units | 206000 | 10.9 | 21.8 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218037105 | N/A | DAIKIN | HMSR-A-CB | REYA216AAYD* |  |  |  | REYA216AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 20.25 | 206000 | 3.35 | 144000 | 2.2 | R-32 | 17.1667
218037106 | N/A | DAIKIN | HMSR-A-CB | REYA240AAYD* |  |  |  | REYA240AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 19.2 | 220000 | 3.3 | 150000 | 2.2 | R-32 | 19
218037034 | N/A | DAIKIN | HMSR-A-CB | REYA240AAYD* |  |  |  | REYA240AAYD* | Non-Ducted Indoor Units | 228000 | 10.7 | 20.4 | 220000 | 3.3 | 150000 | 2.2 | R-32 | 19
218037070 | N/A | DAIKIN | HMSR-A-CB | REYA240AAYD* |  |  |  | REYA240AAYD* | Ducted Indoor Units | 228000 | 10.7 | 18 | 220000 | 3.3 | 150000 | 2.2 | R-32 | 19
216602281 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y | VPC096L4M-4Y |  |  | VPC192L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
216602143 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y | VPC096L4M-4Y |  |  | VPC192L4M-4Y | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
216602197 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4Y | VPC096L4M-4Y |  |  | VPC192L4M-4Y | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
213886370 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH |  |  | AM144BXVTJH | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
213886374 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM096BXVTJH |  |  | AM168BXVTJH | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
213886442 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH |  |  | AM144BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
213886446 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM096BXVTJH |  |  | AM168BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
213886402 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH |  |  | AM144BXVTJH | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
213886406 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM096BXVTJH |  |  | AM168BXVTJH | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
216602276 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC096L4M-4G |  |  | VPC168L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
216602267 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G |  |  | VPC144L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
216602207 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC072L4M-4G |  | VPC216L4M-4G | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
216602214 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC096L4M-4G |  | VPC240L4M-4G | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
216602325 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC072L4M-4G |  | VPC216L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
216602333 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC096L4M-4G |  | VPC240L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
216602311 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC072L4M-4G |  | VPC216L4M-4G | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
216602318 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC096L4M-4G |  | VPC240L4M-4G | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
216602133 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G |  |  | VPC144L4M-4G | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
216602193 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC096L4M-4G |  |  | VPC168L4M-4G | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
216602187 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G |  |  | VPC144L4M-4G | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
216602139 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC096L4M-4G |  |  | VPC168L4M-4G | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
216602146 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G | VPC096L4M-4G |  |  | VPC192L4M-4G | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
216602285 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G | VPC096L4M-4G |  |  | VPC192L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
216602200 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096L4M-4G | VPC096L4M-4G |  |  | VPC192L4M-4G | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
216602185 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y |  |  | VRC144L4M-4Y | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
216602191 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC096L4M-4Y |  |  | VRC168L4M-4Y | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
216602138 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC096L4M-4Y |  |  | VRC168L4M-4Y | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
216602132 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y |  |  | VRC144L4M-4Y | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
216602265 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y |  |  | VRC144L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
216602205 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC072L4M-4Y |  | VRC216L4M-4Y | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
216602212 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC096L4M-4Y |  | VRC240L4M-4Y | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
216602274 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC096L4M-4Y |  |  | VRC168L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
216602316 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC096L4M-4Y |  | VRC240L4M-4Y | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
216602323 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC072L4M-4Y |  | VRC216L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
216602309 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC072L4M-4Y |  | VRC216L4M-4Y | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
216602331 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC096L4M-4Y |  | VRC240L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213886401 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR |  |  | AM144BXVTFR | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
213886405 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM096BXVTFR |  |  | AM168BXVTFR | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
213886413 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM072BXVTFR |  | AM216BXVTFR1 | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
213886417 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM096BXVTFR |  | AM240BXVTFR1 | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
213886373 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM096BXVTFR |  |  | AM168BXVTFR | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
213886441 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR |  |  | AM144BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
213886445 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM096BXVTFR |  |  | AM168BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
213886369 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR |  |  | AM144BXVTFR | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
213893862 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM072BXVTFR |  | AM216BXVTFR1 | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
213893866 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM096BXVTFR |  | AM240BXVTFR1 | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
213893870 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM072BXVTFR |  | AM216BXVTFR1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
213893874 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM096BXVTFR |  | AM240BXVTFR1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213886449 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM096BXVTFR |  |  | AM192BXVTFR1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
213886377 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM096BXVTFR |  |  | AM192BXVTFR1 | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
213886409 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM096BXVTFR |  |  | AM192BXVTFR1 | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
216602283 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y | VRC096L4M-4Y |  |  | VRC192L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
216602144 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y | VRC096L4M-4Y |  |  | VRC192L4M-4Y | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
216602198 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4Y | VRC096L4M-4Y |  |  | VRC192L4M-4Y | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
213886375 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM096BXVTJR |  |  | AM168BXVTJR | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
213886371 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR |  |  | AM144BXVTJR | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
213886443 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR |  |  | AM144BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
213886447 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM096BXVTJR |  |  | AM168BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
213886403 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR |  |  | AM144BXVTJR | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
213886407 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM096BXVTJR |  |  | AM168BXVTJR | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
216602279 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC096L4M-4G |  |  | VRC168L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
216602269 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G |  |  | VRC144L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
216602216 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC096L4M-4G |  | VRC240L4M-4G | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
216602208 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC072L4M-4G |  | VRC216L4M-4G | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
216602312 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC072L4M-4G |  | VRC216L4M-4G | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
216602319 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC096L4M-4G |  | VRC240L4M-4G | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
216602335 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC096L4M-4G |  | VRC240L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
216602328 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC072L4M-4G |  | VRC216L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
216602135 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G |  |  | VRC144L4M-4G | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
216602195 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC096L4M-4G |  |  | VRC168L4M-4G | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
216602188 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G |  |  | VRC144L4M-4G | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
216602141 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC096L4M-4G |  |  | VRC168L4M-4G | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
216602148 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G | VRC096L4M-4G |  |  | VRC192L4M-4G | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
216602287 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G | VRC096L4M-4G |  |  | VRC192L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
216602202 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096L4M-4G | VRC096L4M-4G |  |  | VRC192L4M-4G | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
216602183 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y |  |  | VPC144L4M-4Y | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
216602190 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC096L4M-4Y |  |  | VPC168L4M-4Y | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
216602130 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y |  |  | VPC144L4M-4Y | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
216602136 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC096L4M-4Y |  |  | VPC168L4M-4Y | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
216602262 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y |  |  | VPC144L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
216602272 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC096L4M-4Y |  |  | VPC168L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
216602203 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC072L4M-4Y |  | VPC216L4M-4Y | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
216602210 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC096L4M-4Y |  | VPC240L4M-4Y | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
216602308 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC072L4M-4Y |  | VPC216L4M-4Y | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
216602321 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC072L4M-4Y |  | VPC216L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
216602314 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC096L4M-4Y |  | VPC240L4M-4Y | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
216602330 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC096L4M-4Y |  | VPC240L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213886400 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH |  |  | AM144BXVTFH | Non-Ducted Indoor Units | 138000 | 12.7 | 26.9 | 154000 | 3.88 | 154000 | 2.32 | R-410A | 11.5
213886404 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM096BXVTFH |  |  | AM168BXVTFH | Non-Ducted Indoor Units | 160000 | 12.8 | 26.4 | 180000 | 3.79 | 180000 | 2.26 | R-410A | 13.3333
213886440 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH |  |  | AM144BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.5 | 23.25 | 154000 | 3.88 | 154000 | 2.33 | R-410A | 11.5
213886444 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM096BXVTFH |  |  | AM168BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.52 | 24.45 | 180000 | 3.82 | 180000 | 2.29 | R-410A | 13.3333
213886368 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH |  |  | AM144BXVTFH | Ducted Indoor Units | 138000 | 12.3 | 19.6 | 154000 | 3.89 | 154000 | 2.34 | R-410A | 11.5
213886372 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM096BXVTFH |  |  | AM168BXVTFH | Ducted Indoor Units | 160000 | 12.25 | 22.5 | 180000 | 3.86 | 180000 | 2.32 | R-410A | 13.3333
210135426 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 144FFFH |  |  |  | AVWT - 144FFFH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 23.25 | 150000 | 3.35 | 105000 | 2.34 | R-410A | 11.5
210135414 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 144FFFH |  |  |  | AVWT - 144FFFH | Non-Ducted Indoor Units | 138000 | 11.4 | 25.5 | 150000 | 3.5 | 105000 | 2.41 | R-410A | 11.5
208758272 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB |  |  |  | CHV6-120URB | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 23.25 | 150000 | 3.35 | 105000 | 2.34 | R-410A | 11.5
208758274 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB |  |  |  | CHV6-144URB | Non-Ducted Indoor Units | 138000 | 11.4 | 25.5 | 150000 | 3.5 | 105000 | 2.41 | R-410A | 11.5
208758276 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-168URB |  |  |  | CHV6-168URB | Ducted Indoor Units | 160000 | 10.9 | 20.8 | 170000 | 3.26 | 115000 | 2.07 | R-410A | 13.3333
208758277 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-168URB |  |  |  | CHV6-168URB | Non-Ducted Indoor Units | 160000 | 11.1 | 24.1 | 170000 | 3.39 | 115000 | 2.28 | R-410A | 13.3333
210135427 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 168FFFH |  |  |  | AVWT - 168FFFH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 22.45 | 170000 | 3.32 | 115000 | 2.17 | R-410A | 13.3333
210135418 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 168FFFH |  |  |  | AVWT - 168FFFH | Ducted Indoor Units | 160000 | 10.9 | 20.8 | 170000 | 3.26 | 115000 | 2.07 | R-410A | 13.3333
210135419 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 168FFFH |  |  |  | AVWT - 168FFFH | Non-Ducted Indoor Units | 160000 | 11.1 | 24.1 | 170000 | 3.39 | 115000 | 2.28 | R-410A | 13.3333
210135428 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 192FFFH |  |  |  | AVWT - 192FFFH | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.95 | 200000 | 3.31 | 140000 | 2.34 | R-410A | 15.3333
210135416 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT - 192FFFH |  |  |  | AVWT - 192FFFH | Non-Ducted Indoor Units | 184000 | 11.2 | 24.5 | 200000 | 3.4 | 140000 | 2.43 | R-410A | 15.3333
208758278 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-168URB |  |  |  | CHV6-168URB | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.95 | 200000 | 3.31 | 140000 | 2.34 | R-410A | 15.3333
208758280 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-192URB |  |  |  | CHV6-192URB | Non-Ducted Indoor Units | 184000 | 11.2 | 24.5 | 200000 | 3.4 | 140000 | 2.43 | R-410A | 15.3333
213897062 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* |  |  |  | RXYQ144AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 20.3 | 138000 | 3.32 | 90000 | 2.1 | R-410A | 11.5
213897044 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* |  |  |  | RXYQ144AATJ* | Ducted Indoor Units | 138000 | 10.9 | 18.8 | 138000 | 3.35 | 90000 | 2.1 | R-410A | 11.5
213897018 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* |  |  |  | RXYQ144AATJ* | Non-Ducted Indoor Units | 138000 | 11 | 21.8 | 138000 | 3.3 | 90000 | 2.1 | R-410A | 11.5
213897085 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* |  |  |  | RXYQ168AATJ* | Non-Ducted Indoor Units | 156000 | 10.3 | 21.7 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897095 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* |  |  |  | RXYQ168AATJ* | Ducted Indoor Units | 156000 | 10.2 | 18.4 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897111 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* |  |  |  | RXYQ168AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.25 | 20.05 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897063 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* |  |  |  | RXYQ192AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.25 | 20.2 | 184000 | 3.44 | 130000 | 2.22 | R-410A | 15.3333
213897045 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* |  |  |  | RXYQ192AATJ* | Ducted Indoor Units | 184000 | 11.2 | 18.6 | 184000 | 3.4 | 130000 | 2.22 | R-410A | 15.3333
213897019 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* |  |  |  | RXYQ192AATJ* | Non-Ducted Indoor Units | 184000 | 11.3 | 21.8 | 184000 | 3.48 | 130000 | 2.22 | R-410A | 15.3333
213897086 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* |  |  |  | RXYQ216AATJ* | Non-Ducted Indoor Units | 206000 | 10.3 | 20.8 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213897112 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* |  |  |  | RXYQ216AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.6 | 19.6 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213895075 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* |  |  |  | RXYQ216AATJ* | Ducted Indoor Units | 206000 | 10.9 | 18.4 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213897113 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AATJ* |  |  |  | RXYQ240AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.25 | 19 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
213897096 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AATJ* |  |  |  | RXYQ240AATJ* | Ducted Indoor Units | 228000 | 9.9 | 18 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
213897020 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AATJ* |  |  |  | RXYQ240AATJ* | Non-Ducted Indoor Units | 228000 | 10.6 | 20 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
213897053 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* |  |  |  | RXYQ144AAYD* | Ducted Indoor Units | 138000 | 10.9 | 18.8 | 138000 | 3.35 | 90000 | 2.1 | R-410A | 11.5
213897071 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* |  |  |  | RXYQ144AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 20.3 | 138000 | 3.32 | 90000 | 2.1 | R-410A | 11.5
213897031 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* |  |  |  | RXYQ144AAYD* | Non-Ducted Indoor Units | 138000 | 11 | 21.8 | 138000 | 3.3 | 90000 | 2.1 | R-410A | 11.5
213897090 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* |  |  |  | RXYQ168AAYD* | Non-Ducted Indoor Units | 156000 | 10.3 | 21.7 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897103 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* |  |  |  | RXYQ168AAYD* | Ducted Indoor Units | 156000 | 10.2 | 18.4 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897120 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* |  |  |  | RXYQ168AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 10.25 | 20.05 | 156000 | 3.3 | 100000 | 2.1 | R-410A | 13
213897072 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* |  |  |  | RXYQ192AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.25 | 20.2 | 184000 | 3.44 | 130000 | 2.22 | R-410A | 15.3333
213897054 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* |  |  |  | RXYQ192AAYD* | Ducted Indoor Units | 184000 | 11.2 | 18.6 | 184000 | 3.4 | 130000 | 2.22 | R-410A | 15.3333
213897032 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* |  |  |  | RXYQ192AAYD* | Non-Ducted Indoor Units | 184000 | 11.3 | 21.8 | 184000 | 3.48 | 130000 | 2.22 | R-410A | 15.3333
213897091 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* |  |  |  | RXYQ216AAYD* | Non-Ducted Indoor Units | 206000 | 10.3 | 20.8 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213897121 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* |  |  |  | RXYQ216AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.6 | 19.6 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213895076 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* |  |  |  | RXYQ216AAYD* | Ducted Indoor Units | 206000 | 10.9 | 18.4 | 206000 | 3.35 | 136000 | 2.18 | R-410A | 17.1667
213897122 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AAYD* |  |  |  | RXYQ240AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.25 | 19 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
213897104 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AAYD* |  |  |  | RXYQ240AAYD* | Ducted Indoor Units | 228000 | 9.9 | 18 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
213897033 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AAYD* |  |  |  | RXYQ240AAYD* | Non-Ducted Indoor Units | 228000 | 10.6 | 20 | 220000 | 3.25 | 150000 | 2.15 | R-410A | 19
214091398 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-F(U) | GMV-VQ72WM/C-F(U) |  |  | GMV-VQ144WM/C-F(U) | Non-Ducted Indoor Units | 138000 | 11.4 | 23.5 | 154000 | 4 | 131000 | 2.07 | R-410A | 11.5
214091401 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72WM/C-F(U) | GMV-VQ72WM/C-F(U) |  |  | GMV-VQ144WM/C-F(U) | Ducted Indoor Units | 138000 | 11.7 | 22.4 | 154000 | 3.95 | 131000 | 2.07 | R-410A | 11.5
214091402 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-F(U) | GMV-VQ96WM/C-F(U) |  |  | GMV-VQ192WM/C-F(U) | Ducted Indoor Units | 184000 | 11.1 | 20.3 | 206000 | 3.66 | 150000 | 2.07 | R-410A | 15.3333
214091399 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ96WM/C-F(U) | GMV-VQ96WM/C-F(U) |  |  | GMV-VQ192WM/C-F(U) | Non-Ducted Indoor Units | 184000 | 10.3 | 20.4 | 206000 | 3.93 | 150000 | 2.07 | R-410A | 15.3333
214091403 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ120WM/C-F(U) | GMV-VQ120WM/C-F(U) |  |  | GMV-VQ240WM/C-F(U) | Ducted Indoor Units | 228000 | 10.5 | 19.5 | 256000 | 3.41 | 170000 | 2.07 | R-410A | 19
213928537 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q144WM/C-F(U) |  |  |  | GMV-Q144WM/C-F(U) | Ducted Indoor Units | 138000 | 10.4 | 18.6 | 154000 | 3.38 | 105000 | 2.07 | R-410A | 11.5
214728281 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP144C432Y2 |  |  |  | VEP144C432Y2 | Ducted Indoor Units | 138000 | 10.4 | 18.6 | 154000 | 3.38 | 105000 | 2.07 | R-410A | 11.5
215685124 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q144WM/C-F(U) |  |  |  | GMV-Q144WM/C-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 19.65 | 154000 | 3.44 | 100000 | 2.07 | R-410A | 11.5
215685132 | 1/1/2027 | LENNOX | HMSR-A-CB | VEP144C432Y2 |  |  |  | VEP144C432Y2 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 19.65 | 154000 | 3.44 | 100000 | 2.07 | R-410A | 11.5
213686145 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH |  |  |  | AVWT-144FLFSH | Non-Ducted Indoor Units | 138000 | 11.4 | 25.5 | 150000 | 3.5 | 105000 | 2.41 | R-410A | 11.5
213686146 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH |  |  |  | AVWT-144FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 23.25 | 150000 | 3.35 | 105000 | 2.34 | R-410A | 11.5
213686148 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-168FLFSH |  |  |  | AVWT-168FLFSH | Non-Ducted Indoor Units | 160000 | 11.1 | 24.1 | 170000 | 3.39 | 115000 | 2.28 | R-410A | 13.3333
213686149 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-168FLFSH |  |  |  | AVWT-168FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.75 | 22.45 | 170000 | 3.29 | 115000 | 2.16 | R-410A | 13.3333
213686151 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-192FLFSH |  |  |  | AVWT-192FLFSH | Non-Ducted Indoor Units | 184000 | 11.2 | 24.5 | 200000 | 3.4 | 140000 | 2.43 | R-410A | 15.3333
213686152 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-192FLFSH |  |  |  | AVWT-192FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.95 | 200000 | 3.31 | 140000 | 2.34 | R-410A | 15.3333
213893577 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P216TSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.6 | 21.6 | 232000 | 3.93 | 168000 | 2.53 | R-410A | 17.1667
213893573 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  |  | PUHY-P192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213894787 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  |  | PUHY-P192TSNU-A1 | Ducted Indoor Units | 184000 | 10.5 | 20.2 | 206000 | 3.7 | 152000 | 2.38 | R-410A | 15.3333
213894795 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P216TSNU-A1 | Ducted Indoor Units | 206000 | 10 | 19.9 | 232000 | 3.57 | 168000 | 2.3 | R-410A | 17.1667
213916544 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  |  | PUHY-P192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 21.5 | 206000 | 3.88 | 152000 | 2.51 | R-410A | 15.3333
213916545 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P216TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.3 | 20.75 | 232000 | 3.75 | 168000 | 2.41 | R-410A | 17.1667
213916559 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  |  | PUHY-P192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 21.5 | 206000 | 3.88 | 152000 | 2.51 | R-410A | 15.3333
213916560 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P216YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.3 | 20.75 | 232000 | 3.75 | 168000 | 2.41 | R-410A | 17.1667
213894797 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P216YSNU-A1 | Ducted Indoor Units | 206000 | 10 | 19.9 | 232000 | 3.57 | 168000 | 2.3 | R-410A | 17.1667
213894789 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  |  | PUHY-P192YSNU-A1 | Ducted Indoor Units | 184000 | 10.5 | 20.2 | 206000 | 3.7 | 152000 | 2.38 | R-410A | 15.3333
213893575 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  |  | PUHY-P192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213893579 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P216YSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.6 | 21.6 | 232000 | 3.93 | 168000 | 2.53 | R-410A | 17.1667
213894823 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P240TSNU-A1 | Non-Ducted Indoor Units | 230000 | 9.9 | 20.4 | 258000 | 3.59 | 168000 | 2.3 | R-410A | 19.1667
213894815 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P240TSNU-A1 | Ducted Indoor Units | 230000 | 9.9 | 19.3 | 258000 | 3.45 | 168000 | 2.22 | R-410A | 19.1667
213916546 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  |  | PUHY-P240TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 9.9 | 19.85 | 258000 | 3.52 | 168000 | 2.26 | R-410A | 19.1667
213916561 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P240YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 9.9 | 19.85 | 258000 | 3.52 | 168000 | 2.26 | R-410A | 19.1667
213894817 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P240YSNU-A1 | Ducted Indoor Units | 230000 | 9.9 | 19.3 | 258000 | 3.45 | 168000 | 2.22 | R-410A | 19.1667
213894825 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  |  | PUHY-P240YSNU-A1 | Non-Ducted Indoor Units | 230000 | 9.9 | 20.4 | 258000 | 3.59 | 168000 | 2.3 | R-410A | 19.1667
213893569 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 |  |  |  | PUHY-P144TNU-A1 | Non-Ducted Indoor Units | 138000 | 10.6 | 21.6 | 152000 | 3.9 | 109000 | 2.64 | R-410A | 11.5
213894767 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 |  |  |  | PUHY-P144TNU-A1 | Ducted Indoor Units | 138000 | 10 | 20.6 | 152000 | 3.57 | 109000 | 2.26 | R-410A | 11.5
213916543 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 |  |  |  | PUHY-P144TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.3 | 21.1 | 152000 | 3.73 | 109000 | 2.45 | R-410A | 11.5
213916558 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 |  |  |  | PUHY-P144YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.3 | 21.1 | 152000 | 3.73 | 109000 | 2.45 | R-410A | 11.5
213894769 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 |  |  |  | PUHY-P144YNU-A1 | Ducted Indoor Units | 138000 | 10 | 20.6 | 152000 | 3.57 | 109000 | 2.26 | R-410A | 11.5
213893571 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 |  |  |  | PUHY-P144YNU-A1 | Non-Ducted Indoor Units | 138000 | 10.6 | 21.6 | 152000 | 3.9 | 109000 | 2.64 | R-410A | 11.5
213893471 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP216TSNU-A1 | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213893464 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  |  | PUHY-EP192TSNU-A1 | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893465 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  |  | PUHY-EP192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213916496 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  |  | PUHY-EP192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916498 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP216TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213894799 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP216TSNU-A1 | Ducted Indoor Units | 206000 | 10.5 | 21.2 | 232000 | 3.65 | 196000 | 2.12 | R-410A | 17.1667
213894801 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP216YSNU-A1 | Ducted Indoor Units | 206000 | 10.5 | 21.2 | 232000 | 3.65 | 196000 | 2.12 | R-410A | 17.1667
213916515 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  |  | PUHY-EP192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916517 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP216YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893468 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  |  | PUHY-EP192YSNU-A1 | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893469 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  |  | PUHY-EP192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213893473 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP216YSNU-A1 | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213916500 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP240TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.75 | 258000 | 3.63 | 208000 | 2.16 | R-410A | 19.1667
213894818 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP240TSNU-A1 | Ducted Indoor Units | 230000 | 10.2 | 21 | 258000 | 3.54 | 208000 | 2.11 | R-410A | 19.1667
213894827 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  |  | PUHY-EP240TSNU-A1 | Non-Ducted Indoor Units | 230000 | 10 | 22.5 | 258000 | 3.73 | 208000 | 2.22 | R-410A | 19.1667
213894829 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP240YSNU-A1 | Non-Ducted Indoor Units | 230000 | 10 | 22.5 | 258000 | 3.73 | 208000 | 2.22 | R-410A | 19.1667
213894820 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP240YSNU-A1 | Ducted Indoor Units | 230000 | 10.2 | 21 | 258000 | 3.54 | 208000 | 2.11 | R-410A | 19.1667
213916519 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  |  | PUHY-EP240YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.75 | 258000 | 3.63 | 208000 | 2.16 | R-410A | 19.1667
213893459 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 |  |  |  | PUHY-EP144TNU-A1 | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213916493 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 |  |  |  | PUHY-EP144TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.6 | 22.2 | 152000 | 3.84 | 134000 | 2.49 | R-410A | 11.5
213894771 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 |  |  |  | PUHY-EP144TNU-A1 | Ducted Indoor Units | 138000 | 10.5 | 21.2 | 152000 | 3.68 | 134000 | 2.38 | R-410A | 11.5
213894773 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 |  |  |  | PUHY-EP144YNU-A1 | Ducted Indoor Units | 138000 | 10.5 | 21.2 | 152000 | 3.68 | 134000 | 2.38 | R-410A | 11.5
213916512 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 |  |  |  | PUHY-EP144YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.6 | 22.2 | 152000 | 3.84 | 134000 | 2.49 | R-410A | 11.5
213893461 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 |  |  |  | PUHY-EP144YNU-A1 | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213916494 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168TNU-A1 |  |  |  | PUHY-EP168TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.1 | 21.8 | 178000 | 3.86 | 138000 | 2.5 | R-410A | 13.3333
213894775 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168TNU-A1 |  |  |  | PUHY-EP168TNU-A1 | Ducted Indoor Units | 160000 | 10.1 | 20.4 | 178000 | 3.61 | 138000 | 2.39 | R-410A | 13.3333
213894779 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168TNU-A1 |  |  |  | PUHY-EP168TNU-A1 | Non-Ducted Indoor Units | 160000 | 10.1 | 23.2 | 178000 | 4.11 | 138000 | 2.61 | R-410A | 13.3333
213894777 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168YNU-A1 |  |  |  | PUHY-EP168YNU-A1 | Ducted Indoor Units | 160000 | 10.1 | 20.4 | 178000 | 3.61 | 138000 | 2.39 | R-410A | 13.3333
213894781 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168YNU-A1 |  |  |  | PUHY-EP168YNU-A1 | Non-Ducted Indoor Units | 160000 | 10.1 | 23.2 | 178000 | 4.11 | 138000 | 2.61 | R-410A | 13.3333
213916513 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP168YNU-A1 |  |  |  | PUHY-EP168YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.1 | 21.8 | 178000 | 3.86 | 138000 | 2.5 | R-410A | 13.3333
213916495 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A1 |  |  |  | PUHY-EP192TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.25 | 21.7 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.3333
213894782 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A1 |  |  |  | PUHY-EP192TNU-A1 | Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.3333
213894784 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A1 |  |  |  | PUHY-EP192TNU-A1 | Non-Ducted Indoor Units | 184000 | 10.3 | 22.4 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.3333
213894785 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A1 |  |  |  | PUHY-EP192YNU-A1 | Non-Ducted Indoor Units | 184000 | 10.3 | 22.4 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.3333
213894783 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A1 |  |  |  | PUHY-EP192YNU-A1 | Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.3333
213916514 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A1 |  |  |  | PUHY-EP192YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.25 | 21.7 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.3333
213916497 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216TNU-A1 |  |  |  | PUHY-EP216TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 9.9 | 20.95 | 232000 | 3.51 | 162000 | 2.21 | R-410A | 17.1667
213894791 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216TNU-A1 |  |  |  | PUHY-EP216TNU-A1 | Ducted Indoor Units | 206000 | 9.9 | 20.2 | 232000 | 3.3 | 162000 | 2.12 | R-410A | 17.1667
213894803 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216TNU-A1 |  |  |  | PUHY-EP216TNU-A1 | Non-Ducted Indoor Units | 206000 | 9.9 | 21.7 | 232000 | 3.72 | 162000 | 2.31 | R-410A | 17.1667
213894805 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216YNU-A1 |  |  |  | PUHY-EP216YNU-A1 | Non-Ducted Indoor Units | 206000 | 9.9 | 21.7 | 232000 | 3.72 | 162000 | 2.31 | R-410A | 17.1667
213894793 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216YNU-A1 |  |  |  | PUHY-EP216YNU-A1 | Ducted Indoor Units | 206000 | 9.9 | 20.2 | 232000 | 3.3 | 162000 | 2.12 | R-410A | 17.1667
213916516 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP216YNU-A1 |  |  |  | PUHY-EP216YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 9.9 | 20.95 | 232000 | 3.51 | 162000 | 2.21 | R-410A | 17.1667
213916499 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240TNU-A1 |  |  |  | PUHY-EP240TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 9.9 | 19.9 | 240000 | 3.37 | 162000 | 2.16 | R-410A | 17.8333
213894806 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240TNU-A1 |  |  |  | PUHY-EP240TNU-A1 | Ducted Indoor Units | 214000 | 9.9 | 18.9 | 240000 | 3.25 | 162000 | 2.1 | R-410A | 17.8333
213894811 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240TNU-A1 |  |  |  | PUHY-EP240TNU-A1 | Non-Ducted Indoor Units | 214000 | 9.9 | 20.9 | 240000 | 3.5 | 162000 | 2.22 | R-410A | 17.8333
213894813 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240YNU-A1 |  |  |  | PUHY-EP240YNU-A1 | Non-Ducted Indoor Units | 214000 | 9.9 | 20.9 | 240000 | 3.5 | 162000 | 2.22 | R-410A | 17.8333
213894807 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240YNU-A1 |  |  |  | PUHY-EP240YNU-A1 | Ducted Indoor Units | 214000 | 9.9 | 18.9 | 240000 | 3.25 | 162000 | 2.1 | R-410A | 17.8333
213916518 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP240YNU-A1 |  |  |  | PUHY-EP240YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 9.9 | 19.9 | 240000 | 3.37 | 162000 | 2.16 | R-410A | 17.8333
213916531 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 | PUHY-HP72TNU-A1 |  |  | PUHY-HP144TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213893830 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 | PUHY-HP72TNU-A1 |  |  | PUHY-HP144TSNU-A1 | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893832 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A1 | PUHY-HP72TNU-A1 |  |  | PUHY-HP144TSNU-A1 | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213893834 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 | PUHY-HP72YNU-A1 |  |  | PUHY-HP144YSNU-A1 | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213893843 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 | PUHY-HP72YNU-A1 |  |  | PUHY-HP144YSNU-A1 | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213916537 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A1 | PUHY-HP72YNU-A1 |  |  | PUHY-HP144YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213916533 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 | PUHY-HP120TNU-A1 |  |  | PUHY-HP240TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.5 | 19.65 | 258000 | 3.64 | 174000 | 2.23 | R-410A | 19.1667
213894831 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 | PUHY-HP120TNU-A1 |  |  | PUHY-HP240TSNU-A1 | Non-Ducted Indoor Units | 230000 | 10.1 | 20.2 | 258000 | 3.78 | 174000 | 2.27 | R-410A | 19.1667
213893555 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A1 | PUHY-HP120TNU-A1 |  |  | PUHY-HP240TSNU-A1 | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213893557 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 | PUHY-HP120YNU-A1 |  |  | PUHY-HP240YSNU-A1 | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213894833 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 | PUHY-HP120YNU-A1 |  |  | PUHY-HP240YSNU-A1 | Non-Ducted Indoor Units | 230000 | 10.1 | 20.2 | 258000 | 3.78 | 174000 | 2.27 | R-410A | 19.1667
213916539 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A1 | PUHY-HP120YNU-A1 |  |  | PUHY-HP240YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.5 | 19.65 | 258000 | 3.64 | 174000 | 2.23 | R-410A | 19.1667
213893740 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE0963AN41AN |  |  | TUHYE1923BN41AN | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893741 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE0963AN41AN |  |  | TUHYE1923BN41AN | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213916720 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE0963AN41AN |  |  | TUHYE1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916723 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE0964AN41AN |  |  | TUHYE1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213893742 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE0964AN41AN |  |  | TUHYE1924BN41AN | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893743 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE0964AN41AN |  |  | TUHYE1924BN41AN | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213894984 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN |  |  | TUHYE2403BN41AN | Ducted Indoor Units | 230000 | 10.2 | 21 | 258000 | 3.54 | 208000 | 2.11 | R-410A | 19.1667
213894985 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN |  |  | TUHYE2403BN41AN | Non-Ducted Indoor Units | 230000 | 10 | 22.5 | 258000 | 3.73 | 208000 | 2.22 | R-410A | 19.1667
213916735 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN |  |  | TUHYE2403BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.75 | 258000 | 3.63 | 208000 | 2.16 | R-410A | 19.1667
213916739 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN |  |  | TUHYE2404BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.1 | 21.75 | 258000 | 3.63 | 208000 | 2.16 | R-410A | 19.1667
213894988 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN |  |  | TUHYE2404BN41AN | Ducted Indoor Units | 230000 | 10.2 | 21 | 258000 | 3.54 | 208000 | 2.11 | R-410A | 19.1667
213894989 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN |  |  | TUHYE2404BN41AN | Non-Ducted Indoor Units | 230000 | 10 | 22.5 | 258000 | 3.73 | 208000 | 2.22 | R-410A | 19.1667
213893738 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN |  |  |  | TUHYE1443AN41AN | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213894890 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN |  |  |  | TUHYE1443AN41AN | Ducted Indoor Units | 138000 | 10.5 | 21.2 | 152000 | 3.68 | 134000 | 2.38 | R-410A | 11.5
213916711 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN |  |  |  | TUHYE1443AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.6 | 22.2 | 152000 | 3.84 | 134000 | 2.49 | R-410A | 11.5
213916713 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN |  |  |  | TUHYE1444AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.6 | 22.2 | 152000 | 3.84 | 134000 | 2.49 | R-410A | 11.5
213894891 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN |  |  |  | TUHYE1444AN41AN | Ducted Indoor Units | 138000 | 10.5 | 21.2 | 152000 | 3.68 | 134000 | 2.38 | R-410A | 11.5
213893739 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN |  |  |  | TUHYE1444AN41AN | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213894970 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AN41AN |  |  |  | TUHYE1683AN41AN | Ducted Indoor Units | 160000 | 10.1 | 20.4 | 178000 | 3.61 | 138000 | 2.39 | R-410A | 13.3333
213894971 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AN41AN |  |  |  | TUHYE1683AN41AN | Non-Ducted Indoor Units | 160000 | 10.1 | 23.2 | 178000 | 4.11 | 138000 | 2.61 | R-410A | 13.3333
213916715 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AN41AN |  |  |  | TUHYE1683AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.1 | 21.8 | 178000 | 3.86 | 138000 | 2.5 | R-410A | 13.3333
213916717 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AN41AN |  |  |  | TUHYE1684AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.1 | 21.8 | 178000 | 3.86 | 138000 | 2.5 | R-410A | 13.3333
213894972 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AN41AN |  |  |  | TUHYE1684AN41AN | Ducted Indoor Units | 160000 | 10.1 | 20.4 | 178000 | 3.61 | 138000 | 2.39 | R-410A | 13.3333
213894973 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AN41AN |  |  |  | TUHYE1684AN41AN | Non-Ducted Indoor Units | 160000 | 10.1 | 23.2 | 178000 | 4.11 | 138000 | 2.61 | R-410A | 13.3333
213894974 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN41AN |  |  |  | TUHYE1923AN41AN | Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.3333
213894975 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN41AN |  |  |  | TUHYE1923AN41AN | Non-Ducted Indoor Units | 184000 | 10.3 | 22.4 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.3333
213916718 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN41AN |  |  |  | TUHYE1923AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.25 | 21.7 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.3333
213916721 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN41AN |  |  |  | TUHYE1924AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.25 | 21.7 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.3333
213894976 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN41AN |  |  |  | TUHYE1924AN41AN | Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.3333
213894977 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN41AN |  |  |  | TUHYE1924AN41AN | Non-Ducted Indoor Units | 184000 | 10.3 | 22.4 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.3333
213894982 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2403AN41AN |  |  |  | TUHYE2403AN41AN | Ducted Indoor Units | 214000 | 9.9 | 18.9 | 240000 | 3.25 | 162000 | 2.1 | R-410A | 17.8333
213894983 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2403AN41AN |  |  |  | TUHYE2403AN41AN | Non-Ducted Indoor Units | 214000 | 9.9 | 20.9 | 240000 | 3.5 | 162000 | 2.22 | R-410A | 17.8333
213916733 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2403AN41AN |  |  |  | TUHYE2403AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 9.9 | 19.9 | 240000 | 3.37 | 162000 | 2.16 | R-410A | 17.8333
213916737 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2404AN41AN |  |  |  | TUHYE2404AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 9.9 | 19.9 | 240000 | 3.37 | 162000 | 2.16 | R-410A | 17.8333
213894986 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2404AN41AN |  |  |  | TUHYE2404AN41AN | Ducted Indoor Units | 214000 | 9.9 | 18.9 | 240000 | 3.25 | 162000 | 2.1 | R-410A | 17.8333
213894987 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE2404AN41AN |  |  |  | TUHYE2404AN41AN | Non-Ducted Indoor Units | 214000 | 9.9 | 20.9 | 240000 | 3.5 | 162000 | 2.22 | R-410A | 17.8333
213893845 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN | TUHYH0723AN41AN |  |  | TUHYH1443BN41AN | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893846 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN | TUHYH0723AN41AN |  |  | TUHYH1443BN41AN | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213916785 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN41AN | TUHYH0723AN41AN |  |  | TUHYH1443BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213916938 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN | TUHYH0724AN41AN |  |  | TUHYH1444BN41AN | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213916939 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN | TUHYH0724AN41AN |  |  | TUHYH1444BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213893847 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN41AN | TUHYH0724AN41AN |  |  | TUHYH1444BN41AN | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893781 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN41AN | TUHYH0963AN41AN |  |  | TUHYH1923BN41AN | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893782 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN41AN | TUHYH0963AN41AN |  |  | TUHYH1923BN41AN | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213916788 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN41AN | TUHYH0963AN41AN |  |  | TUHYH1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213916940 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN | TUHYH0964AN41AN |  |  | TUHYH1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213916936 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN | TUHYH0964AN41AN |  |  | TUHYH1924BN41AN | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213893783 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN41AN | TUHYH0964AN41AN |  |  | TUHYH1924BN41AN | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893785 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AN41AN | TUHYH1203AN41AN |  |  | TUHYH2403BN41AN | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213894926 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AN41AN | TUHYH1203AN41AN |  |  | TUHYH2403BN41AN | Non-Ducted Indoor Units | 230000 | 10.1 | 20.2 | 258000 | 3.78 | 174000 | 2.27 | R-410A | 19.1667
213916791 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AN41AN | TUHYH1203AN41AN |  |  | TUHYH2403BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.5 | 19.65 | 258000 | 3.64 | 174000 | 2.23 | R-410A | 19.1667
213916937 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN | TUHYH1204AN41AN |  |  | TUHYH2404BN41AN | Non-Ducted Indoor Units | 230000 | 10.1 | 20.2 | 258000 | 3.78 | 174000 | 2.27 | R-410A | 19.1667
213916941 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN | TUHYH1204AN41AN |  |  | TUHYH2404BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.5 | 19.65 | 258000 | 3.64 | 174000 | 2.23 | R-410A | 19.1667
213893786 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN41AN | TUHYH1204AN41AN |  |  | TUHYH2404BN41AN | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213893793 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP0963AN41AN |  |  | TUHYP1923BN41AN | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213893795 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN |  |  | TUHYP2163BN41AN | Non-Ducted Indoor Units | 206000 | 10.6 | 21.6 | 232000 | 3.93 | 168000 | 2.53 | R-410A | 17.1667
213894898 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP0963AN41AN |  |  | TUHYP1923BN41AN | Ducted Indoor Units | 184000 | 10.5 | 20.2 | 206000 | 3.7 | 152000 | 2.38 | R-410A | 15.3333
213894910 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN |  |  | TUHYP2163BN41AN | Ducted Indoor Units | 206000 | 10 | 19.9 | 232000 | 3.57 | 168000 | 2.3 | R-410A | 17.1667
213916810 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP0963AN41AN |  |  | TUHYP1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 21.5 | 206000 | 3.88 | 152000 | 2.51 | R-410A | 15.3333
213916814 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN |  |  | TUHYP2163BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.3 | 20.75 | 232000 | 3.75 | 168000 | 2.41 | R-410A | 17.1667
213916816 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN |  |  | TUHYP2164BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.3 | 20.75 | 232000 | 3.75 | 168000 | 2.41 | R-410A | 17.1667
213916812 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP0964AN41AN |  |  | TUHYP1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 21.5 | 206000 | 3.88 | 152000 | 2.51 | R-410A | 15.3333
213894911 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN |  |  | TUHYP2164BN41AN | Ducted Indoor Units | 206000 | 10 | 19.9 | 232000 | 3.57 | 168000 | 2.3 | R-410A | 17.1667
213894899 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP0964AN41AN |  |  | TUHYP1924BN41AN | Ducted Indoor Units | 184000 | 10.5 | 20.2 | 206000 | 3.7 | 152000 | 2.38 | R-410A | 15.3333
213893796 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN |  |  | TUHYP2164BN41AN | Non-Ducted Indoor Units | 206000 | 10.6 | 21.6 | 232000 | 3.93 | 168000 | 2.53 | R-410A | 17.1667
213893794 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP0964AN41AN |  |  | TUHYP1924BN41AN | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213894994 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN |  |  | TUHYP2403BN41AN | Ducted Indoor Units | 230000 | 9.9 | 19.3 | 258000 | 3.45 | 168000 | 2.22 | R-410A | 19.1667
213894995 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN |  |  | TUHYP2403BN41AN | Non-Ducted Indoor Units | 230000 | 9.9 | 20.4 | 258000 | 3.59 | 168000 | 2.3 | R-410A | 19.1667
213916818 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN |  |  | TUHYP2403BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 9.9 | 19.85 | 258000 | 3.52 | 168000 | 2.26 | R-410A | 19.1667
213916820 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN |  |  | TUHYP2404BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 9.9 | 19.85 | 258000 | 3.52 | 168000 | 2.26 | R-410A | 19.1667
213894996 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN |  |  | TUHYP2404BN41AN | Ducted Indoor Units | 230000 | 9.9 | 19.3 | 258000 | 3.45 | 168000 | 2.22 | R-410A | 19.1667
213894997 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN |  |  | TUHYP2404BN41AN | Non-Ducted Indoor Units | 230000 | 9.9 | 20.4 | 258000 | 3.59 | 168000 | 2.3 | R-410A | 19.1667
213893791 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN |  |  |  | TUHYP1443AN41AN | Non-Ducted Indoor Units | 138000 | 10.6 | 21.6 | 152000 | 3.9 | 109000 | 2.64 | R-410A | 11.5
213894884 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN |  |  |  | TUHYP1443AN41AN | Ducted Indoor Units | 138000 | 10 | 20.6 | 152000 | 3.57 | 109000 | 2.26 | R-410A | 11.5
213916806 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN |  |  |  | TUHYP1443AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.3 | 21.1 | 152000 | 3.73 | 109000 | 2.45 | R-410A | 11.5
213916808 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN |  |  |  | TUHYP1444AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.3 | 21.1 | 152000 | 3.73 | 109000 | 2.45 | R-410A | 11.5
213894885 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN |  |  |  | TUHYP1444AN41AN | Ducted Indoor Units | 138000 | 10 | 20.6 | 152000 | 3.57 | 109000 | 2.26 | R-410A | 11.5
213893792 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN |  |  |  | TUHYP1444AN41AN | Non-Ducted Indoor Units | 138000 | 10.6 | 21.6 | 152000 | 3.9 | 109000 | 2.64 | R-410A | 11.5
213916532 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 | PUHY-HP96TNU-A1 |  |  | PUHY-HP192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893548 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 | PUHY-HP96TNU-A1 |  |  | PUHY-HP192TSNU-A1 | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893549 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A1 | PUHY-HP96TNU-A1 |  |  | PUHY-HP192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213893552 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 | PUHY-HP96YNU-A1 |  |  | PUHY-HP192YSNU-A1 | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893553 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 | PUHY-HP96YNU-A1 |  |  | PUHY-HP192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213916538 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A1 | PUHY-HP96YNU-A1 |  |  | PUHY-HP192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
214050094 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 21.45 | 204000 | 3.82 | 158000 | 2.11 | R-410A | 15.3333
213896078 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213895966 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP192YSNU-A1 | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896082 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP216YSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.6 | 21.8 | 232000 | 3.89 | 172000 | 2.15 | R-410A | 17.1667
213896386 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP216YSNU-A1 | Ducted Indoor Units | 206000 | 10.3 | 20 | 232000 | 3.56 | 172000 | 2.09 | R-410A | 17.1667
214050102 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120YNU-A1 | PURY-EP96YNU-A1 |  |  | PURY-EP216YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 20.9 | 232000 | 3.72 | 172000 | 2.12 | R-410A | 17.1667
214050082 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144YNU-A1 |  |  |  | PURY-EP144YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.05 | 21.95 | 152000 | 3.67 | 118000 | 2.1 | R-410A | 11.5
213896466 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144YNU-A1 |  |  |  | PURY-EP144YNU-A1 | Non-Ducted Indoor Units | 138000 | 10.1 | 22.7 | 152000 | 3.86 | 118000 | 2.15 | R-410A | 11.5
213896470 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168YNU-A1 |  |  |  | PURY-EP168YNU-A1 | Non-Ducted Indoor Units | 160000 | 10.1 | 22.6 | 178000 | 3.8 | 136000 | 2.15 | R-410A | 13.3333
214050086 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168YNU-A1 |  |  |  | PURY-EP168YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 21.4 | 178000 | 3.55 | 136000 | 2.09 | R-410A | 13.3333
214050092 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192YNU-A1 |  |  |  | PURY-EP192YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.55 | 144000 | 2.14 | R-410A | 15.3333
213896474 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192YNU-A1 |  |  |  | PURY-EP192YNU-A1 | Non-Ducted Indoor Units | 184000 | 10.2 | 22.2 | 204000 | 3.76 | 144000 | 2.2 | R-410A | 15.3333
213896378 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192YNU-A1 |  |  |  | PURY-EP192YNU-A1 | Ducted Indoor Units | 184000 | 10.2 | 19.8 | 204000 | 3.34 | 144000 | 2.09 | R-410A | 15.3333
214050090 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 21.45 | 204000 | 3.82 | 158000 | 2.11 | R-410A | 15.3333
213896076 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213895964 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP192TSNU-A1 | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896080 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP216TSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.6 | 21.8 | 232000 | 3.89 | 172000 | 2.15 | R-410A | 17.1667
213896382 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP216TSNU-A1 | Ducted Indoor Units | 206000 | 10.3 | 20 | 232000 | 3.56 | 172000 | 2.09 | R-410A | 17.1667
214050098 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP120TNU-A1 | PURY-EP96TNU-A1 |  |  | PURY-EP216TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 20.9 | 232000 | 3.72 | 172000 | 2.12 | R-410A | 17.1667
214050080 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144TNU-A1 |  |  |  | PURY-EP144TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.05 | 21.95 | 152000 | 3.67 | 118000 | 2.1 | R-410A | 11.5
213896464 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144TNU-A1 |  |  |  | PURY-EP144TNU-A1 | Non-Ducted Indoor Units | 138000 | 10.1 | 22.7 | 152000 | 3.86 | 118000 | 2.15 | R-410A | 11.5
213896468 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168TNU-A1 |  |  |  | PURY-EP168TNU-A1 | Non-Ducted Indoor Units | 160000 | 10.1 | 22.6 | 178000 | 3.8 | 136000 | 2.15 | R-410A | 13.3333
214050084 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168TNU-A1 |  |  |  | PURY-EP168TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 21.4 | 178000 | 3.55 | 136000 | 2.09 | R-410A | 13.3333
214050088 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192TNU-A1 |  |  |  | PURY-EP192TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.55 | 144000 | 2.14 | R-410A | 15.3333
213896472 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192TNU-A1 |  |  |  | PURY-EP192TNU-A1 | Non-Ducted Indoor Units | 184000 | 10.2 | 22.2 | 204000 | 3.76 | 144000 | 2.2 | R-410A | 15.3333
213896376 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP192TNU-A1 |  |  |  | PURY-EP192TNU-A1 | Ducted Indoor Units | 184000 | 10.2 | 19.8 | 204000 | 3.34 | 144000 | 2.09 | R-410A | 15.3333
213895990 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 | PURY-HP72YNU-A1 |  |  | PURY-HP144YSNU-A1 | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213896113 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 | PURY-HP72YNU-A1 |  |  | PURY-HP144YSNU-A1 | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
214050150 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A1 | PURY-HP72YNU-A1 |  |  | PURY-HP144YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.65 | 152000 | 3.63 | 128000 | 2.11 | R-410A | 11.5
214050154 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 | PURY-HP96YNU-A1 |  |  | PURY-HP192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 20.4 | 206000 | 3.74 | 174000 | 2.12 | R-410A | 15.3333
213896123 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 | PURY-HP96YNU-A1 |  |  | PURY-HP192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
213895994 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A1 | PURY-HP96YNU-A1 |  |  | PURY-HP192YSNU-A1 | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
214050148 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 | PURY-HP72TNU-A1 |  |  | PURY-HP144TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.65 | 152000 | 3.63 | 128000 | 2.11 | R-410A | 11.5
213895988 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 | PURY-HP72TNU-A1 |  |  | PURY-HP144TSNU-A1 | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213896109 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A1 | PURY-HP72TNU-A1 |  |  | PURY-HP144TSNU-A1 | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213896118 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 | PURY-HP96TNU-A1 |  |  | PURY-HP192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
213895992 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 | PURY-HP96TNU-A1 |  |  | PURY-HP192TSNU-A1 | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
214050152 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A1 | PURY-HP96TNU-A1 |  |  | PURY-HP192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 20.4 | 206000 | 3.74 | 174000 | 2.12 | R-410A | 15.3333
214050182 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P192YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 20.8 | 204000 | 3.74 | 142000 | 2.17 | R-410A | 15.3333
213896138 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P192YSNU-A1 | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896006 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P192YSNU-A1 | Ducted Indoor Units | 184000 | 10.5 | 20.1 | 204000 | 3.6 | 142000 | 2.18 | R-410A | 15.3333
213896502 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P216YSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.3 | 21 | 232000 | 3.82 | 158000 | 2.09 | R-410A | 17.1667
213896410 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P216YSNU-A1 | Ducted Indoor Units | 206000 | 10 | 19.8 | 232000 | 3.49 | 158000 | 2.19 | R-410A | 17.1667
214050186 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YNU-A1 | PURY-P96YNU-A1 |  |  | PURY-P216YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.15 | 20.4 | 232000 | 3.65 | 158000 | 2.14 | R-410A | 17.1667
214050174 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YNU-A1 |  |  |  | PURY-P144YNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 21.05 | 152000 | 3.63 | 97000 | 2.1 | R-410A | 11.5
213896494 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YNU-A1 |  |  |  | PURY-P144YNU-A1 | Non-Ducted Indoor Units | 138000 | 10 | 21.6 | 152000 | 3.84 | 97000 | 2.16 | R-410A | 11.5
213896498 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P168YNU-A1 |  |  |  | PURY-P168YNU-A1 | Non-Ducted Indoor Units | 160000 | 10 | 21.8 | 178000 | 3.8 | 119000 | 2.32 | R-410A | 13.3333
213896004 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P192TSNU-A1 | Ducted Indoor Units | 184000 | 10.5 | 20.1 | 204000 | 3.6 | 142000 | 2.18 | R-410A | 15.3333
213896136 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P192TSNU-A1 | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
214050180 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P192TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 20.8 | 204000 | 3.74 | 142000 | 2.17 | R-410A | 15.3333
214050184 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P216TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.15 | 20.4 | 232000 | 3.65 | 158000 | 2.14 | R-410A | 17.1667
213896408 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P216TSNU-A1 | Ducted Indoor Units | 206000 | 10 | 19.8 | 232000 | 3.49 | 158000 | 2.19 | R-410A | 17.1667
213896500 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TNU-A1 | PURY-P96TNU-A1 |  |  | PURY-P216TSNU-A1 | Non-Ducted Indoor Units | 206000 | 10.3 | 21 | 232000 | 3.82 | 158000 | 2.09 | R-410A | 17.1667
213896492 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TNU-A1 |  |  |  | PURY-P144TNU-A1 | Non-Ducted Indoor Units | 138000 | 10 | 21.6 | 152000 | 3.84 | 97000 | 2.16 | R-410A | 11.5
214050172 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TNU-A1 |  |  |  | PURY-P144TNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 21.05 | 152000 | 3.63 | 97000 | 2.1 | R-410A | 11.5
213896496 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P168TNU-A1 |  |  |  | PURY-P168TNU-A1 | Non-Ducted Indoor Units | 160000 | 10 | 21.8 | 178000 | 3.8 | 119000 | 2.32 | R-410A | 13.3333
214050308 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN41AN | TURYE0964AN41AN |  |  | TURYE1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 21.45 | 204000 | 3.82 | 158000 | 2.11 | R-410A | 15.3333
213896166 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN41AN | TURYE0964AN41AN |  |  | TURYE1924BN41AN | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213896030 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN41AN | TURYE0964AN41AN |  |  | TURYE1924BN41AN | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896170 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AN41AN | TURYE0964AN41AN |  |  | TURYE2164BN41AN | Non-Ducted Indoor Units | 206000 | 10.6 | 21.8 | 232000 | 3.89 | 172000 | 2.15 | R-410A | 17.1667
213896434 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AN41AN | TURYE0964AN41AN |  |  | TURYE2164BN41AN | Ducted Indoor Units | 206000 | 10.3 | 20 | 232000 | 3.56 | 172000 | 2.09 | R-410A | 17.1667
214050316 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AN41AN | TURYE0964AN41AN |  |  | TURYE2164BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 20.9 | 232000 | 3.72 | 172000 | 2.12 | R-410A | 17.1667
214050296 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AN41AN |  |  |  | TURYE1444AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.05 | 21.95 | 152000 | 3.67 | 118000 | 2.1 | R-410A | 11.5
213896510 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AN41AN |  |  |  | TURYE1444AN41AN | Non-Ducted Indoor Units | 138000 | 10.1 | 22.7 | 152000 | 3.86 | 118000 | 2.15 | R-410A | 11.5
213896514 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AN41AN |  |  |  | TURYE1684AN41AN | Non-Ducted Indoor Units | 160000 | 10.1 | 22.6 | 178000 | 3.8 | 136000 | 2.15 | R-410A | 13.3333
214050300 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AN41AN |  |  |  | TURYE1684AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 21.4 | 178000 | 3.55 | 136000 | 2.09 | R-410A | 13.3333
214050306 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AN41AN |  |  |  | TURYE1924AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.55 | 144000 | 2.14 | R-410A | 15.3333
213896426 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AN41AN |  |  |  | TURYE1924AN41AN | Ducted Indoor Units | 184000 | 10.2 | 19.8 | 204000 | 3.34 | 144000 | 2.09 | R-410A | 15.3333
213896518 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AN41AN |  |  |  | TURYE1924AN41AN | Non-Ducted Indoor Units | 184000 | 10.2 | 22.2 | 204000 | 3.76 | 144000 | 2.2 | R-410A | 15.3333
214050304 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN41AN | TURYE0963AN41AN |  |  | TURYE1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 21.45 | 204000 | 3.82 | 158000 | 2.11 | R-410A | 15.3333
213896028 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN41AN | TURYE0963AN41AN |  |  | TURYE1923BN41AN | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896164 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN41AN | TURYE0963AN41AN |  |  | TURYE1923BN41AN | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213896168 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AN41AN | TURYE0963AN41AN |  |  | TURYE2163BN41AN | Non-Ducted Indoor Units | 206000 | 10.6 | 21.8 | 232000 | 3.89 | 172000 | 2.15 | R-410A | 17.1667
213896430 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AN41AN | TURYE0963AN41AN |  |  | TURYE2163BN41AN | Ducted Indoor Units | 206000 | 10.3 | 20 | 232000 | 3.56 | 172000 | 2.09 | R-410A | 17.1667
214050312 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AN41AN | TURYE0963AN41AN |  |  | TURYE2163BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.45 | 20.9 | 232000 | 3.72 | 172000 | 2.12 | R-410A | 17.1667
214050294 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AN41AN |  |  |  | TURYE1443AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.05 | 21.95 | 152000 | 3.67 | 118000 | 2.1 | R-410A | 11.5
213896508 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AN41AN |  |  |  | TURYE1443AN41AN | Non-Ducted Indoor Units | 138000 | 10.1 | 22.7 | 152000 | 3.86 | 118000 | 2.15 | R-410A | 11.5
213896512 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AN41AN |  |  |  | TURYE1683AN41AN | Non-Ducted Indoor Units | 160000 | 10.1 | 22.6 | 178000 | 3.8 | 136000 | 2.15 | R-410A | 13.3333
214050298 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AN41AN |  |  |  | TURYE1683AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 21.4 | 178000 | 3.55 | 136000 | 2.09 | R-410A | 13.3333
214050302 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AN41AN |  |  |  | TURYE1923AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 21 | 204000 | 3.55 | 144000 | 2.14 | R-410A | 15.3333
213896424 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AN41AN |  |  |  | TURYE1923AN41AN | Ducted Indoor Units | 184000 | 10.2 | 19.8 | 204000 | 3.34 | 144000 | 2.09 | R-410A | 15.3333
213896516 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AN41AN |  |  |  | TURYE1923AN41AN | Non-Ducted Indoor Units | 184000 | 10.2 | 22.2 | 204000 | 3.76 | 144000 | 2.2 | R-410A | 15.3333
213896198 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN | TURYH0724AN41AN |  |  | TURYH1444BN41AN | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213896054 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN | TURYH0724AN41AN |  |  | TURYH1444BN41AN | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
214050364 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN41AN | TURYH0724AN41AN |  |  | TURYH1444BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.65 | 152000 | 3.63 | 128000 | 2.11 | R-410A | 11.5
214050368 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN | TURYH0964AN41AN |  |  | TURYH1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 20.4 | 206000 | 3.74 | 174000 | 2.12 | R-410A | 15.3333
213896058 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN | TURYH0964AN41AN |  |  | TURYH1924BN41AN | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896202 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN41AN | TURYH0964AN41AN |  |  | TURYH1924BN41AN | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
214050362 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN | TURYH0723AN41AN |  |  | TURYH1443BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.65 | 152000 | 3.63 | 128000 | 2.11 | R-410A | 11.5
213896196 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN | TURYH0723AN41AN |  |  | TURYH1443BN41AN | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213896052 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN41AN | TURYH0723AN41AN |  |  | TURYH1443BN41AN | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213896056 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN | TURYH0963AN41AN |  |  | TURYH1923BN41AN | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896200 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN | TURYH0963AN41AN |  |  | TURYH1923BN41AN | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
214050366 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN41AN | TURYH0963AN41AN |  |  | TURYH1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 20.4 | 206000 | 3.74 | 174000 | 2.12 | R-410A | 15.3333
214050396 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN41AN | TURYP0964AN41AN |  |  | TURYP1924BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 20.8 | 204000 | 3.74 | 142000 | 2.17 | R-410A | 15.3333
213896070 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN41AN | TURYP0964AN41AN |  |  | TURYP1924BN41AN | Ducted Indoor Units | 184000 | 10.5 | 20.1 | 204000 | 3.6 | 142000 | 2.18 | R-410A | 15.3333
213896214 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN41AN | TURYP0964AN41AN |  |  | TURYP1924BN41AN | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896458 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1204AN41AN | TURYP0964AN41AN |  |  | TURYP2164BN41AN | Ducted Indoor Units | 206000 | 10 | 19.8 | 232000 | 3.49 | 158000 | 2.19 | R-410A | 17.1667
213896546 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1204AN41AN | TURYP0964AN41AN |  |  | TURYP2164BN41AN | Non-Ducted Indoor Units | 206000 | 10.3 | 21 | 232000 | 3.82 | 158000 | 2.09 | R-410A | 17.1667
214050400 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1204AN41AN | TURYP0964AN41AN |  |  | TURYP2164BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.15 | 20.4 | 232000 | 3.65 | 158000 | 2.14 | R-410A | 17.1667
214050388 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1444AN41AN |  |  |  | TURYP1444AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 21.05 | 152000 | 3.63 | 97000 | 2.1 | R-410A | 11.5
213896538 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1444AN41AN |  |  |  | TURYP1444AN41AN | Non-Ducted Indoor Units | 138000 | 10 | 21.6 | 152000 | 3.84 | 97000 | 2.16 | R-410A | 11.5
213896542 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1684AN41AN |  |  |  | TURYP1684AN41AN | Non-Ducted Indoor Units | 160000 | 10 | 21.8 | 178000 | 3.8 | 119000 | 2.32 | R-410A | 13.3333
213896212 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN41AN | TURYP0963AN41AN |  |  | TURYP1923BN41AN | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896068 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN41AN | TURYP0963AN41AN |  |  | TURYP1923BN41AN | Ducted Indoor Units | 184000 | 10.5 | 20.1 | 204000 | 3.6 | 142000 | 2.18 | R-410A | 15.3333
214050394 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN41AN | TURYP0963AN41AN |  |  | TURYP1923BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.6 | 20.8 | 204000 | 3.74 | 142000 | 2.17 | R-410A | 15.3333
214050398 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1203AN41AN | TURYP0963AN41AN |  |  | TURYP2163BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.15 | 20.4 | 232000 | 3.65 | 158000 | 2.14 | R-410A | 17.1667
213896544 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1203AN41AN | TURYP0963AN41AN |  |  | TURYP2163BN41AN | Non-Ducted Indoor Units | 206000 | 10.3 | 21 | 232000 | 3.82 | 158000 | 2.09 | R-410A | 17.1667
213896456 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1203AN41AN | TURYP0963AN41AN |  |  | TURYP2163BN41AN | Ducted Indoor Units | 206000 | 10 | 19.8 | 232000 | 3.49 | 158000 | 2.19 | R-410A | 17.1667
213896536 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1443AN41AN |  |  |  | TURYP1443AN41AN | Non-Ducted Indoor Units | 138000 | 10 | 21.6 | 152000 | 3.84 | 97000 | 2.16 | R-410A | 11.5
214050386 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1443AN41AN |  |  |  | TURYP1443AN41AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 9.9 | 21.05 | 152000 | 3.63 | 97000 | 2.1 | R-410A | 11.5
213896540 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP1683AN41AN |  |  |  | TURYP1683AN41AN | Non-Ducted Indoor Units | 160000 | 10 | 21.8 | 178000 | 3.8 | 119000 | 2.32 | R-410A | 13.3333
9990282 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA72RLBV1 |  |  | AOUA192RLBVG1 | Non-Ducted Indoor Units | 184000 | 11.2 | 24.3 | 206000 | 3.75 | 142000 | 2.49 | R-410A | 15.3333
9990283 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA96RLBV1 |  |  | AOUA216RLBVG1 | Non-Ducted Indoor Units | 206000 | 10.9 | 20 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
9990284 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA120RLBV1 |  |  | AOUA240RLBVG1 | Non-Ducted Indoor Units | 228000 | 10.9 | 20.8 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
9990280 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 | AOUA72RLBV1 |  |  | AOUA144RLBVG1 | Non-Ducted Indoor Units | 138000 | 11.4 | 22.2 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
9990281 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA72RLBV1 |  |  | AOUA168RLBVG1 | Non-Ducted Indoor Units | 160000 | 11 | 22.2 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
213916856 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.75 | 19.95 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
213916298 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Ducted Indoor Units | 138000 | 11 | 18.2 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
213916293 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Non-Ducted Indoor Units | 138000 | 10.5 | 21.7 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
213916857 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 |  |  |  | ARUM168BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 19.5 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
213916858 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 20.65 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
213916300 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Ducted Indoor Units | 184000 | 10.5 | 19.9 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
213916295 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Non-Ducted Indoor Units | 184000 | 9.9 | 21.4 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
213916864 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.75 | 19.95 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
213916310 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Ducted Indoor Units | 138000 | 11 | 18.2 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
213916304 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Non-Ducted Indoor Units | 138000 | 10.5 | 21.7 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
213916865 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 |  |  |  | ARUM168DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 19.5 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
213916866 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 20.65 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
213916312 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Ducted Indoor Units | 184000 | 10.5 | 19.9 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
213916306 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Non-Ducted Indoor Units | 184000 | 9.9 | 21.4 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
214432114 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B32S | TVAHP096B32S |  |  | TVAHP192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091583 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091440 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311042 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B42S | TVAHP096B42S |  |  | TVAHP192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091599 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091456 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311040 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S | HVAHP096B32S |  |  | HVAHP192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091535 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214078207 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432076 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S | HVAHP096B42S |  |  | HVAHP192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091551 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091408 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432080 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S | YVAHP096B32S |  |  | YVAHP192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091631 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091488 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432116 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S | YVAHP096B42S |  |  | YVAHP192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091647 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091504 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432094 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S | HVAHR096B42S |  |  | HVAHR192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094333 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094182 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432098 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S | YVAHR096B32S |  |  | YVAHR192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094413 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094262 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432134 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S | YVAHR096B42S |  |  | YVAHR192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094429 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094278 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432132 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B32S | TVAHR096B32S |  |  | TVAHR192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094365 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094214 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311059 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B42S | TVAHR096B42S |  |  | TVAHR192B42H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094381 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094230 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311057 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S | HVAHR096B32S |  |  | HVAHR192B32H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094317 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094166 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432096 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR096B52S | TVAHR096B52S |  |  | TVAHR192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094397 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B52S |  |  |  | TVAHR144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094246 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR168B52S |  |  |  | TVAHR168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432130 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B52S | HVAHR096B52S |  |  | HVAHR192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094349 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S |  |  |  | HVAHR144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094198 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S |  |  |  | HVAHR168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311061 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B52S | YVAHR096B52S |  |  | YVAHR192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214094445 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S |  |  |  | YVAHR144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214094294 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S |  |  |  | YVAHR168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432078 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B52S | TVAHP096B52S |  |  | TVAHP192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091615 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B52S |  |  |  | TVAHP144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091472 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP168B52S |  |  |  | TVAHP168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214432112 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B52S | HVAHP096B52S |  |  | HVAHP192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091567 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S |  |  |  | HVAHP144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091424 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S |  |  |  | HVAHP168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
214311044 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B52S | YVAHP096B52S |  |  | YVAHP192B52H | Non-Ducted Indoor Units | 184000 | 10.7 | 18.3 | 206000 | 4.16 | 140000 | 2.51 | R-410A | 15.3333
214091663 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S |  |  |  | YVAHP144B52S | Non-Ducted Indoor Units | 138000 | 9.9 | 18.3 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
214091520 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S |  |  |  | YVAHP168B52S | Ducted Indoor Units | 160000 | 9.9 | 18 | 180000 | 3.52 | 124000 | 2.26 | R-410A | 13.3333
213916693 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.75 | 19.95 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
213916326 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Ducted Indoor Units | 138000 | 11 | 18.2 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
213916318 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Non-Ducted Indoor Units | 138000 | 10.5 | 21.7 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
213916694 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 |  |  |  | ARUM168CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.05 | 19.5 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
213916695 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.2 | 20.65 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
213916328 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Ducted Indoor Units | 184000 | 10.5 | 19.9 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
213916320 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Non-Ducted Indoor Units | 184000 | 9.9 | 21.4 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
214050519 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B | PURY-P96ZKMU-B |  |  | PURY-P192ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.4 | 18.65 | 204000 | 3.42 | 142000 | 2.13 | R-410A | 15.3333
214050513 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B | PURY-P72ZKMU-B |  |  | PURY-P168ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.7 | 18.3 | 178000 | 3.44 | 119000 | 2.12 | R-410A | 13.3333
213896343 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B | PURY-P72ZKMU-B |  |  | PURY-P168ZSKMU-B | Ducted Indoor Units | 160000 | 10.6 | 19.1 | 178000 | 3.6 | 119000 | 2.13 | R-410A | 13.3333
213896345 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96ZKMU-B | PURY-P96ZKMU-B |  |  | PURY-P192ZSKMU-B | Ducted Indoor Units | 184000 | 10.3 | 19.6 | 204000 | 3.48 | 142000 | 2.1 | R-410A | 15.3333
213896285 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B |  |  | PUHY-P168ZSKMU-B | Non-Ducted Indoor Units | 160000 | 11.4 | 19.2 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
213896322 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B |  |  | PUHY-P192ZSKMU-B | Ducted Indoor Units | 184000 | 11 | 18.7 | 204000 | 3.48 | 150000 | 2.45 | R-410A | 15.3333
213896320 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B |  |  | PUHY-P168ZSKMU-B | Ducted Indoor Units | 160000 | 11.3 | 20.7 | 178000 | 3.54 | 132000 | 2.6 | R-410A | 13.3333
213916481 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B |  |  | PUHY-P168ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.35 | 19.95 | 178000 | 3.68 | 132000 | 2.39 | R-410A | 13.3333
213916482 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B |  |  | PUHY-P192ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 18.25 | 204000 | 3.58 | 150000 | 2.31 | R-410A | 15.3333
213916483 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B |  |  | PUHY-P216ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 18.8 | 232000 | 3.53 | 164000 | 2.28 | R-410A | 17.1667
213896324 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B |  |  | PUHY-P216ZSKMU-B | Ducted Indoor Units | 206000 | 10.8 | 19.8 | 232000 | 3.51 | 164000 | 2.48 | R-410A | 17.1667
213896318 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144ZKMU-B |  |  |  | PUHY-P144ZKMU-B | Ducted Indoor Units | 138000 | 9.9 | 18.5 | 152000 | 3.46 | 109000 | 2.32 | R-410A | 11.5
6687555 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA72TLBV |  | AOUA264TLBVG | Non-Ducted Indoor Units | 252000 | 10.9 | 20.8 | 282000 | 3.45 | 194000 | 2.29 | R-410A | 21
6687557 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA96TLBV |  | AOUA288TLBVG | Non-Ducted Indoor Units | 274000 | 10.6 | 20.8 | 308000 | 3.36 | 210000 | 2.29 | R-410A | 22.8333
7850834 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA72TLCV |  | AOUA264TLCVG | Non-Ducted Indoor Units | 252000 | 10.9 | 20.8 | 282000 | 3.45 | 194000 | 2.29 | R-410A | 21
7850836 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA96TLCV |  | AOUA288TLCVG | Non-Ducted Indoor Units | 274000 | 10.6 | 20.8 | 308000 | 3.36 | 210000 | 2.29 | R-410A | 22.8333
7850854 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA72RLCV |  | AOUA264RLCVG | Non-Ducted Indoor Units | 252000 | 10.9 | 20.8 | 282000 | 3.45 | 194000 | 2.29 | R-410A | 21
7850856 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA96RLCV |  | AOUA288RLCVG | Non-Ducted Indoor Units | 274000 | 10.6 | 20.8 | 308000 | 3.36 | 210000 | 2.29 | R-410A | 22.8333
216602813 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC168S4M-4J |  |  | VPC264S4M-4J | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602815 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC192S4M-4J |  |  | VPC288S4M-4J | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602817 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC216S4M-4J |  |  | VPC312S4M-4J | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602827 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC240S4M-4J |  |  | VPC336S4M-4J | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216602721 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC240S4M-4J |  |  | VPC336S4M-4J | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216602736 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC168S4M-4J |  |  | VPC264S4M-4J | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602737 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC192S4M-4J |  |  | VPC288S4M-4J | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602739 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC216S4M-4J |  |  | VPC312S4M-4J | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
214833153 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM168DXVGQH |  |  | AM264DXVGQH | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
214833154 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM192DXVGQH |  |  | AM288DXVGQH | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
214833155 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM216DXVGQH |  |  | AM312DXVGQH | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
214826380 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM168DXVGQH |  |  | AM264DXVGQH | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
214826381 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM192DXVGQH |  |  | AM288DXVGQH | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
214826382 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM216DXVGQH |  |  | AM312DXVGQH | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
214836585 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM168DXVGQH |  |  | AM264DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
214836586 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM192DXVGQH |  |  | AM288DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
214836587 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM216DXVGQH |  |  | AM312DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
214836588 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM240DXVGQH |  |  | AM336DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
214833161 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM240DXVGQH |  |  | AM336DXVGQH | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
214826371 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096DXVGQH | AM240DXVGQH |  |  | AM336DXVGQH | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216602864 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC168S4M-4J |  |  | VPC264S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602866 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC192S4M-4J |  |  | VPC288S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602869 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC216S4M-4J |  |  | VPC312S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602871 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4J | VPC240S4M-4J |  |  | VPC336S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602873 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC240S4M-4J |  |  | VPC360S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602880 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC120S4M-4J | VPC192S4M-4J |  | VPC432S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
214833159 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM120DXVGQH | AM192DXVGQH |  | AM432DXVGQH | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
214833165 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM120DXVGQH | AM192DXVGQH |  | AM432DXVGQH | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
214833166 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM144DXVGQH | AM192DXVGQH |  | AM456DXVGQH | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
214836589 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM240DXVGQH |  |  | AM360DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
214836592 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM120DXVGQH | AM192DXVGQH |  | AM432DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
214833156 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120DXVGQH | AM240DXVGQH |  |  | AM360DXVGQH | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602824 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC120S4M-4J | VPC192S4M-4J |  | VPC432S4M-4J | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602835 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC120S4M-4J | VPC192S4M-4J |  | VPC432S4M-4J | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602837 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC144S4M-4J | VPC192S4M-4J |  | VPC456S4M-4J | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602819 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4J | VPC240S4M-4J |  |  | VPC360S4M-4J | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602820 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC192S4M-4J |  |  | VPC384S4M-4J | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
216602822 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC216S4M-4J |  |  | VPC408S4M-4J | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602831 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC192S4M-4J |  |  | VPC384S4M-4J | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602834 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC216S4M-4J |  |  | VPC408S4M-4J | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
214833157 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM192DXVGQH |  |  | AM384DXVGQH | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
214833158 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM216DXVGQH |  |  | AM408DXVGQH | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
214836590 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM192DXVGQH |  |  | AM384DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
214836591 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM216DXVGQH |  |  | AM408DXVGQH | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
214833163 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM192DXVGQH |  |  | AM384DXVGQH | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
214833164 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192DXVGQH | AM216DXVGQH |  |  | AM408DXVGQH | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602876 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC192S4M-4J |  |  | VPC384S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602878 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4J | VPC216S4M-4J |  |  | VPC408S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602771 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC168S4M-4J |  |  | VRC264S4M-4J | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602772 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC192S4M-4J |  |  | VRC288S4M-4J | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602774 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC216S4M-4J |  |  | VRC312S4M-4J | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602839 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC168S4M-4J |  |  | VRC264S4M-4J | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602841 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC192S4M-4J |  |  | VRC288S4M-4J | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602842 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC216S4M-4J |  |  | VRC312S4M-4J | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216598841 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM240DXVGQR |  |  | AM336DXVGQR | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216598842 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM168DXVGQR |  |  | AM264DXVGQR | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216598843 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM192DXVGQR |  |  | AM288DXVGQR | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216598844 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM216DXVGQR |  |  | AM312DXVGQR | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216598845 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM168DXVGQR |  |  | AM264DXVGQR | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216598846 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM192DXVGQR |  |  | AM288DXVGQR | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216598847 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM216DXVGQR |  |  | AM312DXVGQR | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216598853 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM240DXVGQR |  |  | AM336DXVGQR | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216598859 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM168DXVGQR |  |  | AM264DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216598860 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM192DXVGQR |  |  | AM288DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216598861 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM216DXVGQR |  |  | AM312DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216598862 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096DXVGQR | AM240DXVGQR |  |  | AM336DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602884 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC168S4M-4J |  |  | VRC264S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602886 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC192S4M-4J |  |  | VRC288S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602889 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC216S4M-4J |  |  | VRC312S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602891 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC240S4M-4J |  |  | VRC336S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602853 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC240S4M-4J |  |  | VRC336S4M-4J | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216602754 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4J | VRC240S4M-4J |  |  | VRC336S4M-4J | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216602849 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J | VRC120S4M-4J | VRC192S4M-4J |  | VRC432S4M-4J | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602860 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J | VRC120S4M-4J | VRC192S4M-4J |  | VRC432S4M-4J | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602862 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J | VRC144S4M-4J | VRC192S4M-4J |  | VRC456S4M-4J | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602893 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC240S4M-4J |  |  | VRC360S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602900 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC120S4M-4J | VRC192S4M-4J |  | VRC432S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216598863 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM240DXVGQR |  |  | AM360DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216598857 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM120DXVGQR | AM192DXVGQR |  | AM432DXVGQR | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216598858 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM144DXVGQR | AM192DXVGQR |  | AM456DXVGQR | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216598866 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM120DXVGQR | AM192DXVGQR |  | AM432DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216598851 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM120DXVGQR | AM192DXVGQR |  | AM432DXVGQR | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216598848 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120DXVGQR | AM240DXVGQR |  |  | AM360DXVGQR | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602844 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4J | VRC240S4M-4J |  |  | VRC360S4M-4J | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602846 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4J | VRC192S4M-4J |  |  | VRC384S4M-4J | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
216602847 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4J | VRC216S4M-4J |  |  | VRC408S4M-4J | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216598849 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM192DXVGQR |  |  | AM384DXVGQR | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
216598850 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM216DXVGQR |  |  | AM408DXVGQR | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216598855 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM192DXVGQR |  |  | AM384DXVGQR | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216598856 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM216DXVGQR |  |  | AM408DXVGQR | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216598864 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM192DXVGQR |  |  | AM384DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216598865 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192DXVGQR | AM216DXVGQR |  |  | AM408DXVGQR | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602895 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC192S4M-4J |  |  | VRC384S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602898 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC216S4M-4J |  |  | VRC408S4M-4J | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602856 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4J | VRC192S4M-4J |  |  | VRC384S4M-4J | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602858 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4J | VRC216S4M-4J |  |  | VRC408S4M-4J | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
213895940 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AATJ* | REYQ144AATJ* |  |  | REYQ264AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.65 | 19.6 | 252000 | 3.45 | 168000 | 2.2 | R-410A | 21
213895899 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AATJ* | REYQ144AATJ* |  |  | REYQ264AATJ* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.2 | 252000 | 3.7 | 168000 | 2.2 | R-410A | 21
213895900 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* | REYQ144AATJ* |  |  | REYQ288AATJ* | Non-Ducted Indoor Units | 274000 | 11.4 | 20.7 | 274000 | 3.4 | 194000 | 2.2 | R-410A | 22.8333
213895901 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* | REYQ168AATJ* |  |  | REYQ312AATJ* | Non-Ducted Indoor Units | 296000 | 10.9 | 20.4 | 296000 | 3.4 | 212000 | 2.2 | R-410A | 24.6667
213895941 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* | REYQ144AATJ* |  |  | REYQ288AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.9 | 19.25 | 274000 | 3.3 | 194000 | 2.15 | R-410A | 22.8333
213895942 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AATJ* | REYQ168AATJ* |  |  | REYQ312AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.55 | 19 | 296000 | 3.3 | 212000 | 2.15 | R-410A | 24.6667
213895943 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AATJ* | REYQ168AATJ* |  |  | REYQ336AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.9 | 18.5 | 310000 | 3.3 | 222000 | 2.1 | R-410A | 26.3333
213895902 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AATJ* | REYQ168AATJ* |  |  | REYQ336AATJ* | Non-Ducted Indoor Units | 316000 | 9.8 | 19.7 | 310000 | 3.4 | 222000 | 2.1 | R-410A | 26.3333
213895910 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AAYD* | REYQ144AAYD* |  |  | REYQ264AAYD* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.2 | 252000 | 3.7 | 168000 | 2.2 | R-410A | 21
213895950 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120AAYD* | REYQ144AAYD* |  |  | REYQ264AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.65 | 19.6 | 252000 | 3.45 | 168000 | 2.2 | R-410A | 21
213895951 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* | REYQ144AAYD* |  |  | REYQ288AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.9 | 19.25 | 274000 | 3.3 | 194000 | 2.15 | R-410A | 22.8333
213895952 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* | REYQ168AAYD* |  |  | REYQ312AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.55 | 19 | 296000 | 3.3 | 212000 | 2.15 | R-410A | 24.6667
213895911 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* | REYQ144AAYD* |  |  | REYQ288AAYD* | Non-Ducted Indoor Units | 274000 | 11.4 | 20.7 | 274000 | 3.4 | 194000 | 2.2 | R-410A | 22.8333
213895912 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144AAYD* | REYQ168AAYD* |  |  | REYQ312AAYD* | Non-Ducted Indoor Units | 296000 | 10.9 | 20.4 | 296000 | 3.4 | 212000 | 2.2 | R-410A | 24.6667
213895913 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AAYD* | REYQ168AAYD* |  |  | REYQ336AAYD* | Non-Ducted Indoor Units | 316000 | 9.8 | 19.7 | 310000 | 3.4 | 222000 | 2.1 | R-410A | 26.3333
213895953 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168AAYD* | REYQ168AAYD* |  |  | REYQ336AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.9 | 18.5 | 310000 | 3.3 | 222000 | 2.1 | R-410A | 26.3333
216602567 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC168S4M-4Y |  |  | VPC264S4M-4Y | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602573 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC192S4M-4Y |  |  | VPC288S4M-4Y | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602579 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC216S4M-4Y |  |  | VPC312S4M-4Y | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602585 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC240S4M-4Y |  |  | VPC336S4M-4Y | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216602497 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC168S4M-4Y |  |  | VPC264S4M-4Y | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602503 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC192S4M-4Y |  |  | VPC288S4M-4Y | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602510 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC216S4M-4Y |  |  | VPC312S4M-4Y | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602517 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC240S4M-4Y |  |  | VPC336S4M-4Y | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
216602380 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC168S4M-4Y |  |  | VPC264S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602389 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC192S4M-4Y |  |  | VPC288S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602398 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC216S4M-4Y |  |  | VPC312S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602407 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4Y | VPC240S4M-4Y |  |  | VPC336S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
213893897 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM168BXVGFH |  |  | AM264BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
213893901 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM192BXVGFH |  |  | AM288BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
213893905 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM216BXVGFH |  |  | AM312BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
213893909 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM240BXVGFH |  |  | AM336BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
213893957 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM168BXVGFH |  |  | AM264BXVGFH | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
213893961 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM192BXVGFH |  |  | AM288BXVGFH | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
213893965 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM216BXVGFH |  |  | AM312BXVGFH | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
213893969 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM240BXVGFH |  |  | AM336BXVGFH | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213893999 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM168BXVGFH |  |  | AM264BXVGFH | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
213894003 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM192BXVGFH |  |  | AM288BXVGFH | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
213894007 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM216BXVGFH |  |  | AM312BXVGFH | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
213894011 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGFH | AM240BXVGFH |  |  | AM336BXVGFH | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
213893973 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH | AM240BXVGFH |  |  | AM360BXVGFH | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
213893913 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH | AM240BXVGFH |  |  | AM360BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
213916436 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGFH | AM144BXVGFH | AM192BXVGFH |  | AM456BXVGFH | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602417 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC240S4M-4Y |  |  | VPC360S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602524 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC240S4M-4Y |  |  | VPC360S4M-4Y | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602612 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC120S4M-4Y | VPC192S4M-4Y |  | VPC432S4M-4Y | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602647 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC120S4M-4Y | VPC192S4M-4Y |  | VPC432S4M-4Y | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602654 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC144S4M-4Y | VPC192S4M-4Y |  | VPC456S4M-4Y | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602688 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4Y | VPC120S4M-4Y | VPC192S4M-4Y |  | VPC432S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602598 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC192S4M-4Y |  |  | VPC384S4M-4Y | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602605 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC216S4M-4Y |  |  | VPC408S4M-4Y | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602435 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC216S4M-4Y |  |  | VPC408S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602426 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC192S4M-4Y |  |  | VPC384S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602531 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC192S4M-4Y |  |  | VPC384S4M-4Y | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
216602537 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4Y | VPC216S4M-4Y |  |  | VPC408S4M-4Y | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
213893917 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM192BXVGFH |  |  | AM384BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
213893921 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM216BXVGFH |  |  | AM408BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
213894019 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM192BXVGFH |  |  | AM384BXVGFH | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
213893977 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM192BXVGFH |  |  | AM384BXVGFH | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213893981 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM216BXVGFH |  |  | AM408BXVGFH | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
213894023 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGFH | AM216BXVGFH |  |  | AM408BXVGFH | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602411 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC240S4M-4G |  |  | VPC336S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602403 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC216S4M-4G |  |  | VPC312S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602394 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC192S4M-4G |  |  | VPC288S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602384 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC168S4M-4G |  |  | VPC264S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602588 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC240S4M-4G |  |  | VPC336S4M-4G | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216602582 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC216S4M-4G |  |  | VPC312S4M-4G | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602576 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC192S4M-4G |  |  | VPC288S4M-4G | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602570 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC168S4M-4G |  |  | VPC264S4M-4G | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602500 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC168S4M-4G |  |  | VPC264S4M-4G | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602514 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC216S4M-4G |  |  | VPC312S4M-4G | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602507 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC192S4M-4G |  |  | VPC288S4M-4G | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602521 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC096S4M-4G | VPC240S4M-4G |  |  | VPC336S4M-4G | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213894001 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM168BXVGJH |  |  | AM264BXVGJH | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
213894013 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM240BXVGJH |  |  | AM336BXVGJH | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
213894009 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM216BXVGJH |  |  | AM312BXVGJH | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
213894005 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM192BXVGJH |  |  | AM288BXVGJH | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
213893971 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM240BXVGJH |  |  | AM336BXVGJH | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213893967 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM216BXVGJH |  |  | AM312BXVGJH | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
213893963 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM192BXVGJH |  |  | AM288BXVGJH | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
213893959 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM168BXVGJH |  |  | AM264BXVGJH | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
213893911 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM240BXVGJH |  |  | AM336BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
213893899 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM168BXVGJH |  |  | AM264BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
213893907 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM216BXVGJH |  |  | AM312BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
213893903 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVGJH | AM192BXVGJH |  |  | AM288BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
213893915 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH | AM240BXVGJH |  |  | AM360BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
213893975 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH | AM240BXVGJH |  |  | AM360BXVGJH | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
213916438 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVGJH | AM144BXVGJH | AM192BXVGJH |  | AM456BXVGJH | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602528 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC240S4M-4G |  |  | VPC360S4M-4G | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602421 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC240S4M-4G |  |  | VPC360S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602657 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC144S4M-4G | VPC192S4M-4G |  | VPC456S4M-4G | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602651 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC120S4M-4G | VPC192S4M-4G |  | VPC432S4M-4G | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602613 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC120S4M-4G | VPC192S4M-4G |  | VPC432S4M-4G | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602694 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC120S4M-4G | VPC120S4M-4G | VPC192S4M-4G |  | VPC432S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602608 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC216S4M-4G |  |  | VPC408S4M-4G | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602602 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC192S4M-4G |  |  | VPC384S4M-4G | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602438 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC216S4M-4G |  |  | VPC408S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602430 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC192S4M-4G |  |  | VPC384S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602540 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC216S4M-4G |  |  | VPC408S4M-4G | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602534 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC192S4M-4G | VPC192S4M-4G |  |  | VPC384S4M-4G | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213893923 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM216BXVGJH |  |  | AM408BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
213893919 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM192BXVGJH |  |  | AM384BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
213893979 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM192BXVGJH |  |  | AM384BXVGJH | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213893983 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM216BXVGJH |  |  | AM408BXVGJH | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
213894021 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM192BXVGJH |  |  | AM384BXVGJH | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
213894025 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192BXVGJH | AM216BXVGJH |  |  | AM408BXVGJH | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602400 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC216S4M-4Y |  |  | VRC312S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602409 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC240S4M-4Y |  |  | VRC336S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602382 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC168S4M-4Y |  |  | VRC264S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602391 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC192S4M-4Y |  |  | VRC288S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602568 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC168S4M-4Y |  |  | VRC264S4M-4Y | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602574 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC192S4M-4Y |  |  | VRC288S4M-4Y | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602580 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC216S4M-4Y |  |  | VRC312S4M-4Y | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602587 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC240S4M-4Y |  |  | VRC336S4M-4Y | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216602499 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC168S4M-4Y |  |  | VRC264S4M-4Y | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602505 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC192S4M-4Y |  |  | VRC288S4M-4Y | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602512 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC216S4M-4Y |  |  | VRC312S4M-4Y | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602519 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4Y | VRC240S4M-4Y |  |  | VRC336S4M-4Y | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213893958 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM168BXVGFR |  |  | AM264BXVGFR | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
213893962 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM192BXVGFR |  |  | AM288BXVGFR | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
213893966 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM216BXVGFR |  |  | AM312BXVGFR | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
213893970 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM240BXVGFR |  |  | AM336BXVGFR | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213894000 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM168BXVGFR |  |  | AM264BXVGFR | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
213894004 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM192BXVGFR |  |  | AM288BXVGFR | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
213894008 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM216BXVGFR |  |  | AM312BXVGFR | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
213894012 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM240BXVGFR |  |  | AM336BXVGFR | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
213893910 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM240BXVGFR |  |  | AM336BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
213893898 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM168BXVGFR |  |  | AM264BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
213893902 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM192BXVGFR |  |  | AM288BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
213893906 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGFR | AM216BXVGFR |  |  | AM312BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
213893914 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM240BXVGFR |  |  | AM360BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
213893985 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM120BXVGFR | AM192BXVGFR |  | AM432BXVGFR1 | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
213893974 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM240BXVGFR |  |  | AM360BXVGFR | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
213916437 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM144BXVGFR | AM192BXVGFR |  | AM456BXVGFR | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
213916433 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM120BXVGFR | AM192BXVGFR |  | AM432BXVGFR1 | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602526 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC240S4M-4Y |  |  | VRC360S4M-4Y | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602544 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC120S4M-4Y | VRC192S4M-4Y |  | VRC432S4M-4Y | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602419 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC240S4M-4Y |  |  | VRC360S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602691 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC120S4M-4Y | VRC192S4M-4Y |  | VRC432S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602649 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC120S4M-4Y | VRC192S4M-4Y |  | VRC432S4M-4Y | Non-Ducted Indoor Units | 412000 | 9.2 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602656 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4Y | VRC144S4M-4Y | VRC192S4M-4Y |  | VRC456S4M-4Y | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
213918753 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGFR | AM120BXVGFR | AM192BXVGFR |  | AM432BXVGFR1 | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.25 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602607 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC216S4M-4Y |  |  | VRC408S4M-4Y | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602600 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC192S4M-4Y |  |  | VRC384S4M-4Y | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602436 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC216S4M-4Y |  |  | VRC408S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602428 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC192S4M-4Y |  |  | VRC384S4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602532 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC192S4M-4Y |  |  | VRC384S4M-4Y | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
216602539 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4Y | VRC216S4M-4Y |  |  | VRC408S4M-4Y | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
213893918 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM192BXVGFR |  |  | AM384BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
213893922 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM216BXVGFR |  |  | AM408BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
213894020 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM192BXVGFR |  |  | AM384BXVGFR | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
213893978 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM192BXVGFR |  |  | AM384BXVGFR | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213893982 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM216BXVGFR |  |  | AM408BXVGFR | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
213894024 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGFR | AM216BXVGFR |  |  | AM408BXVGFR | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602414 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC240S4M-4G |  |  | VRC336S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
216602405 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC216S4M-4G |  |  | VRC312S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
216602396 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC192S4M-4G |  |  | VRC288S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
216602386 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC168S4M-4G |  |  | VRC264S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
216602590 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC240S4M-4G |  |  | VRC336S4M-4G | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
216602584 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC216S4M-4G |  |  | VRC312S4M-4G | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
216602578 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC192S4M-4G |  |  | VRC288S4M-4G | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
216602571 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC168S4M-4G |  |  | VRC264S4M-4G | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
216602502 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC168S4M-4G |  |  | VRC264S4M-4G | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
216602515 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC216S4M-4G |  |  | VRC312S4M-4G | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
216602508 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC192S4M-4G |  |  | VRC288S4M-4G | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
216602523 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC096S4M-4G | VRC240S4M-4G |  |  | VRC336S4M-4G | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213894002 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM168BXVGJR |  |  | AM264BXVGJR | Non-Ducted Indoor Units | 252000 | 10.9 | 22.4 | 282000 | 3.32 | 184000 | 2.32 | R-410A | 21
213894014 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM240BXVGJR |  |  | AM336BXVGJR | Non-Ducted Indoor Units | 320000 | 10 | 20.9 | 360000 | 3.25 | 234000 | 2.26 | R-410A | 26.6667
213894010 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM216BXVGJR |  |  | AM312BXVGJR | Non-Ducted Indoor Units | 298000 | 10.1 | 20.5 | 334000 | 3.28 | 218000 | 2.28 | R-410A | 24.8333
213894006 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM192BXVGJR |  |  | AM288BXVGJR | Non-Ducted Indoor Units | 274000 | 10.6 | 21.9 | 308000 | 3.3 | 200000 | 2.22 | R-410A | 22.8333
213893972 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM240BXVGJR |  |  | AM336BXVGJR | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.4 | 234000 | 2.3 | R-410A | 26.6667
213893968 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM216BXVGJR |  |  | AM312BXVGJR | Ducted Indoor Units | 298000 | 10.8 | 20 | 334000 | 3.45 | 218000 | 2.35 | R-410A | 24.8333
213893964 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM192BXVGJR |  |  | AM288BXVGJR | Ducted Indoor Units | 274000 | 11.1 | 20.5 | 308000 | 3.5 | 200000 | 2.4 | R-410A | 22.8333
213893960 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM168BXVGJR |  |  | AM264BXVGJR | Ducted Indoor Units | 252000 | 11.1 | 19.7 | 282000 | 3.55 | 184000 | 2.4 | R-410A | 21
213893912 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM240BXVGJR |  |  | AM336BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.35 | 360000 | 3.32 | 234000 | 2.28 | R-410A | 26.6667
213893900 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM168BXVGJR |  |  | AM264BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 21.05 | 282000 | 3.43 | 184000 | 2.36 | R-410A | 21
213893908 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM216BXVGJR |  |  | AM312BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 20.25 | 334000 | 3.36 | 218000 | 2.31 | R-410A | 24.8333
213893904 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVGJR | AM192BXVGJR |  |  | AM288BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 21.2 | 308000 | 3.4 | 200000 | 2.31 | R-410A | 22.8333
213893916 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR | AM240BXVGJR |  |  | AM360BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
213893976 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR | AM240BXVGJR |  |  | AM360BXVGJR | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
213916439 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVGJR | AM144BXVGJR | AM192BXVGJR |  | AM456BXVGJR | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602529 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC240S4M-4G |  |  | VRC360S4M-4G | Ducted Indoor Units | 342000 | 10 | 19.3 | 386000 | 3.4 | 250000 | 2.3 | R-410A | 28.5
216602546 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC120S4M-4G | VRC192S4M-4G |  | VRC432S4M-4G | Ducted Indoor Units | 412000 | 9.3 | 17.9 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
216602423 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC240S4M-4G |  |  | VRC360S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 19.95 | 386000 | 3.31 | 250000 | 2.24 | R-410A | 28.5
216602696 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC120S4M-4G | VRC192S4M-4G |  | VRC432S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.3 | 17.65 | 462000 | 3.27 | 300000 | 2.26 | R-410A | 34.3333
216602659 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC144S4M-4G | VRC192S4M-4G |  | VRC456S4M-4G | Non-Ducted Indoor Units | 436000 | 9.1 | 16.4 | 488000 | 3.25 | 320000 | 2.07 | R-410A | 36.3333
216602652 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC120S4M-4G | VRC120S4M-4G | VRC192S4M-4G |  | VRC432S4M-4G | Non-Ducted Indoor Units | 412000 | 9.3 | 17.4 | 462000 | 3.3 | 300000 | 2.17 | R-410A | 34.3333
216602610 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC216S4M-4G |  |  | VRC408S4M-4G | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
216602603 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC192S4M-4G |  |  | VRC384S4M-4G | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
216602441 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC216S4M-4G |  |  | VRC408S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
216602432 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC192S4M-4G |  |  | VRC384S4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
216602542 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC216S4M-4G |  |  | VRC408S4M-4G | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
216602535 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC192S4M-4G | VRC192S4M-4G |  |  | VRC384S4M-4G | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213893924 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM216BXVGJR |  |  | AM408BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.5 | 18.65 | 438000 | 3.27 | 284000 | 2.25 | R-410A | 32.3333
213893920 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM192BXVGJR |  |  | AM384BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 18.9 | 412000 | 3.3 | 268000 | 2.27 | R-410A | 30.5
213893980 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM192BXVGJR |  |  | AM384BXVGJR | Ducted Indoor Units | 366000 | 10.2 | 18.9 | 412000 | 3.3 | 268000 | 2.35 | R-410A | 30.5
213893984 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM216BXVGJR |  |  | AM408BXVGJR | Ducted Indoor Units | 388000 | 9.5 | 18.6 | 438000 | 3.3 | 284000 | 2.35 | R-410A | 32.3333
213894022 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM192BXVGJR |  |  | AM384BXVGJR | Non-Ducted Indoor Units | 366000 | 9.6 | 18.9 | 412000 | 3.3 | 268000 | 2.2 | R-410A | 30.5
213894026 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192BXVGJR | AM216BXVGJR |  |  | AM408BXVGJR | Non-Ducted Indoor Units | 388000 | 9.5 | 18.7 | 438000 | 3.25 | 284000 | 2.15 | R-410A | 32.3333
208931715 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA120ULBV5 |  |  | AOUA264ULBVG5 | Non-Ducted Indoor Units | 252000 | 11.7 | 22.9 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931718 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 |  |  | AOUA288ULBVG5 | Non-Ducted Indoor Units | 276000 | 9.8 | 22.4 | 308000 | 3.39 | 210000 | 2.16 | R-410A | 23
208931728 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA120ULBV5 |  | AOUA408ULBVG5 | Non-Ducted Indoor Units | 390000 | 11 | 22.7 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931729 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA144ULBV5 |  | AOUA432ULBVG5 | Non-Ducted Indoor Units | 412000 | 10.8 | 22.9 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931870 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA120ULBV5 |  |  | AOUA264ULBVG5 | Ducted Indoor Units | 252000 | 11.2 | 17.3 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931872 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 |  |  | AOUA288ULBVG5 | Ducted Indoor Units | 276000 | 10 | 17.2 | 308000 | 3.37 | 210000 | 2.16 | R-410A | 23
208931882 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA120ULBV5 |  | AOUA408ULBVG5 | Ducted Indoor Units | 390000 | 11 | 17.6 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931884 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA144ULBV5 |  | AOUA432ULBVG5 | Ducted Indoor Units | 412000 | 10.8 | 17.5 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931874 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA144ULBV5 |  |  | AOUA312ULBVG5 | Ducted Indoor Units | 298000 | 10 | 17.2 | 320000 | 3.37 | 214000 | 2.16 | R-410A | 24.8333
208931876 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA168ULBV5 |  |  | AOUA336ULBVG5 | Ducted Indoor Units | 320000 | 10 | 17.2 | 338000 | 3.37 | 224000 | 2.16 | R-410A | 26.6667
208931721 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA144ULBV5 |  |  | AOUA312ULBVG5 | Non-Ducted Indoor Units | 298000 | 9.8 | 22.4 | 320000 | 3.39 | 214000 | 2.16 | R-410A | 24.8333
208931723 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA168ULBV5 |  |  | AOUA336ULBVG5 | Non-Ducted Indoor Units | 320000 | 9.8 | 22.4 | 338000 | 3.39 | 224000 | 2.16 | R-410A | 26.6667
208931725 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA168ULBV5 |  |  | AOUA360ULBVG5 | Non-Ducted Indoor Units | 344000 | 9.8 | 22.4 | 346000 | 3.39 | 232000 | 2.16 | R-410A | 28.6667
208931726 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA192ULBV5 |  |  | AOUA384ULBVG5 | Non-Ducted Indoor Units | 366000 | 9.8 | 22.4 | 354000 | 3.39 | 240000 | 2.16 | R-410A | 30.5
208931878 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA168ULBV5 |  |  | AOUA360ULBVG5 | Ducted Indoor Units | 344000 | 10 | 17.2 | 346000 | 3.37 | 232000 | 2.16 | R-410A | 28.6667
208931880 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA192ULBV5 |  |  | AOUA384ULBVG5 | Ducted Indoor Units | 366000 | 10 | 17.2 | 354000 | 3.37 | 240000 | 2.16 | R-410A | 30.5
208931736 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA120ULCV5 |  |  | AOUA264ULCVG5 | Non-Ducted Indoor Units | 252000 | 11.7 | 22.9 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931738 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 |  |  | AOUA288ULCVG5 | Non-Ducted Indoor Units | 276000 | 9.8 | 22.4 | 308000 | 3.39 | 210000 | 2.16 | R-410A | 23
208931904 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA120ULCV5 |  | AOUA408ULCVG5 | Ducted Indoor Units | 390000 | 11 | 17.6 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931906 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA144ULCV5 |  | AOUA432ULCVG5 | Ducted Indoor Units | 412000 | 10.8 | 17.5 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931892 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA120ULCV5 |  |  | AOUA264ULCVG5 | Ducted Indoor Units | 252000 | 11.2 | 17.3 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931894 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 |  |  | AOUA288ULCVG5 | Ducted Indoor Units | 276000 | 10 | 17.2 | 308000 | 3.37 | 210000 | 2.16 | R-410A | 23
208931749 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA120ULCV5 |  | AOUA408ULCVG5 | Non-Ducted Indoor Units | 390000 | 11 | 22.7 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931751 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA144ULCV5 |  | AOUA432ULCVG5 | Non-Ducted Indoor Units | 412000 | 10.8 | 22.9 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931896 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA144ULCV5 |  |  | AOUA312ULCVG5 | Ducted Indoor Units | 298000 | 10 | 17.2 | 320000 | 3.37 | 214000 | 2.16 | R-410A | 24.8333
208931898 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA168ULCV5 |  |  | AOUA336ULCVG5 | Ducted Indoor Units | 320000 | 10 | 17.2 | 338000 | 3.37 | 224000 | 2.16 | R-410A | 26.6667
208931741 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA144ULCV5 |  |  | AOUA312ULCVG5 | Non-Ducted Indoor Units | 298000 | 9.8 | 22.4 | 320000 | 3.39 | 214000 | 2.16 | R-410A | 24.8333
208931743 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA168ULCV5 |  |  | AOUA336ULCVG5 | Non-Ducted Indoor Units | 320000 | 9.8 | 22.4 | 338000 | 3.39 | 224000 | 2.16 | R-410A | 26.6667
208931745 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA168ULCV5 |  |  | AOUA360ULCVG5 | Non-Ducted Indoor Units | 344000 | 9.8 | 22.4 | 346000 | 3.39 | 232000 | 2.16 | R-410A | 28.6667
208931747 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA192ULCV5 |  |  | AOUA384ULCVG5 | Non-Ducted Indoor Units | 366000 | 9.8 | 22.4 | 354000 | 3.39 | 240000 | 2.16 | R-410A | 30.5
208931900 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA168ULCV5 |  |  | AOUA360ULCVG5 | Ducted Indoor Units | 344000 | 10 | 17.2 | 346000 | 3.37 | 232000 | 2.16 | R-410A | 28.6667
208931902 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA192ULCV5 |  |  | AOUA384ULCVG5 | Ducted Indoor Units | 366000 | 10 | 17.2 | 354000 | 3.37 | 240000 | 2.16 | R-410A | 30.5
213896685 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ144XBTJ* |  |  | REYQ264XBTJ* | Non-Ducted Indoor Units | 252000 | 10.4 | 19.1 | 252000 | 3.41 | 176000 | 2.09 | R-410A | 21
213896688 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ120XBTJ* | REYQ120XBTJ* |  | REYQ360XBTJ* | Non-Ducted Indoor Units | 342000 | 10.2 | 18 | 330000 | 3.52 | 234000 | 2.15 | R-410A | 28.5
213896775 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ144XBTJ* |  |  | REYQ264XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.15 | 17.95 | 252000 | 3.3 | 176000 | 2.09 | R-410A | 21
213896776 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBTJ* | REYQ120XBTJ* | REYQ120XBTJ* |  | REYQ360XBTJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 17 | 330000 | 3.36 | 234000 | 2.15 | R-410A | 28.5
213896751 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ144XBYD* |  |  | REYQ264XBYD* | Non-Ducted Indoor Units | 252000 | 10.4 | 19.1 | 252000 | 3.41 | 176000 | 2.09 | R-410A | 21
213896752 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ120XBYD* | REYQ120XBYD* |  | REYQ360XBYD* | Non-Ducted Indoor Units | 342000 | 10.2 | 18 | 330000 | 3.52 | 234000 | 2.15 | R-410A | 28.5
213896779 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ144XBYD* |  |  | REYQ264XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.15 | 17.95 | 252000 | 3.3 | 176000 | 2.09 | R-410A | 21
213896780 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYD* | REYQ120XBYD* | REYQ120XBYD* |  | REYQ360XBYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 17 | 330000 | 3.36 | 234000 | 2.15 | R-410A | 28.5
213896755 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ144XBYC* |  |  | REYQ264XBYC* | Non-Ducted Indoor Units | 252000 | 10.4 | 19.1 | 252000 | 3.41 | 176000 | 2.09 | R-410A | 21
213896756 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ120XBYC* | REYQ120XBYC* |  | REYQ360XBYC* | Non-Ducted Indoor Units | 342000 | 10.2 | 18 | 330000 | 3.52 | 234000 | 2.15 | R-410A | 28.5
213896783 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ144XBYC* |  |  | REYQ264XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.15 | 17.95 | 252000 | 3.3 | 176000 | 2.09 | R-410A | 21
213896784 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XBYC* | REYQ120XBYC* | REYQ120XBYC* |  | REYQ360XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.85 | 17 | 330000 | 3.36 | 234000 | 2.15 | R-410A | 28.5
213896865 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* | RXYQ144XBYC* |  |  | RXYQ264XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.45 | 17 | 252000 | 3.3 | 176000 | 2.09 | R-410A | 21
213896869 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* | RXYQ120XBYC* | RXYQ120XBYC* |  | RXYQ360XBYC* | Mixed Ducted and Non-Ducted Indoor Units | 338000 | 9.1 | 16.4 | 330000 | 3.36 | 234000 | 2.15 | R-410A | 28.1667
213896748 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* | RXYQ144XBYC* |  |  | RXYQ264XBYC* | Non-Ducted Indoor Units | 252000 | 9.8 | 18.4 | 252000 | 3.41 | 176000 | 2.09 | R-410A | 21
213896813 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XBYC* | RXYQ120XBYC* | RXYQ120XBYC* |  | RXYQ360XBYC* | Non-Ducted Indoor Units | 338000 | 9.1 | 17.4 | 330000 | 3.52 | 234000 | 2.15 | R-410A | 28.1667
214608165 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME2CA* | MVHQ144ME2CA* |  |  | MVHQ264ME2CA* | Ducted Indoor Units | 252000 | 9.8 | 19.4 | 282000 | 3.3 | 192000 | 2.3 | R-410A | 21
214608166 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME2CA* | MVHQ144ME2CA* |  |  | MVHQ264ME2CA* | Non-Ducted Indoor Units | 252000 | 10.1 | 18.8 | 282000 | 3.3 | 192000 | 2.3 | R-410A | 21
214717494 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME2CA* | MVHQ192ME2CA* |  |  | MVHQ384ME2CA* | Ducted Indoor Units | 364000 | 9.4 | 18.5 | 384000 | 3.3 | 268000 | 2.3 | R-410A | 30.3333
214608167 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME4CA* | MVHQ144ME4CA* |  |  | MVHQ264ME4CA* | Ducted Indoor Units | 252000 | 9.8 | 19.4 | 282000 | 3.3 | 192000 | 2.3 | R-410A | 21
214608168 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ120ME4CA* | MVHQ144ME4CA* |  |  | MVHQ264ME4CA* | Non-Ducted Indoor Units | 252000 | 10.1 | 18.8 | 282000 | 3.3 | 192000 | 2.3 | R-410A | 21
214717496 | 1/1/2027 | HAIER | HMSR-A-CB | MVHQ192ME4CA* | MVHQ192ME4CA* |  |  | MVHQ384ME4CA* | Ducted Indoor Units | 364000 | 9.4 | 18.5 | 384000 | 3.3 | 268000 | 2.3 | R-410A | 30.3333
217190026 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
217190027 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B33CW | HVAHR144B33CW |  |  | HVAHR288B33CW* | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
217189688 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW* | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
217189689 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B33CW | HVAHR144B33CW |  |  | HVAHR288B33CW* | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
217189658 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW* | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
214295978 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
214296040 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
214296041 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B33CW | HVAHR144B33CW |  |  | HVAHR288B33CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
214296010 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B33CW | HVAHR120B33CW |  |  | HVAHR264B33CW | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
214296011 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B33CW | HVAHR144B33CW |  |  | HVAHR288B33CW | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
217189698 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW* | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
217189699 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B43CW | HVAHR144B43CW |  |  | HVAHR288B43CW* | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
217190036 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
217190037 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B43CW | HVAHR144B43CW |  |  | HVAHR288B43CW* | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
217189668 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW* | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
214296020 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
214296021 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B43CW | HVAHR144B43CW |  |  | HVAHR288B43CW | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
214295986 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
214296050 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B43CW | HVAHR120B43CW |  |  | HVAHR264B43CW | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
214296051 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B43CW | HVAHR144B43CW |  |  | HVAHR288B43CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
215828409 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
215828410 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW | HVAHR144B53CW |  |  | HVAHR288B53CW | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
215828399 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
215828419 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
215828420 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B53CW | HVAHR144B53CW |  |  | HVAHR288B53CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
217189708 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW* | Non-Ducted Indoor Units | 252000 | 11.8 | 19.2 | 282000 | 3.95 | 200000 | 2.5 | R-410A | 21
217189709 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW | HVAHR144B53CW |  |  | HVAHR288B53CW* | Non-Ducted Indoor Units | 276000 | 11.3 | 19.1 | 308000 | 3.95 | 214000 | 2.45 | R-410A | 23
217190046 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.25 | 18.05 | 282000 | 3.62 | 200000 | 2.37 | R-410A | 21
217190047 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW | HVAHR144B53CW |  |  | HVAHR288B53CW* | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.9 | 18 | 308000 | 3.57 | 214000 | 2.32 | R-410A | 23
217189678 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHR144B53CW | HVAHR120B53CW |  |  | HVAHR264B53CW* | Ducted Indoor Units | 252000 | 10.7 | 16.9 | 282000 | 3.3 | 200000 | 2.25 | R-410A | 21
217729768 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM121BTE6 |  |  | ZRUM265BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.95 | 21.15 | 282000 | 3.38 | 182000 | 2.36 | R-32 | 21
217729769 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM144BTE6 |  |  | ZRUM288BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11 | 21.5 | 308000 | 3.6 | 198000 | 2.54 | R-32 | 23
217729316 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM121BTE6 |  |  | ZRUM265BTE6 | Ducted Indoor Units | 252000 | 10.9 | 19.9 | 282000 | 3.3 | 182000 | 2.2 | R-32 | 21
217729334 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM121BTE6 |  |  | ZRUM265BTE6 | Non-Ducted Indoor Units | 252000 | 11 | 22.4 | 282000 | 3.46 | 182000 | 2.52 | R-32 | 21
217729335 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM144BTE6 |  |  | ZRUM288BTE6 | Non-Ducted Indoor Units | 276000 | 11.1 | 21.8 | 308000 | 3.66 | 198000 | 2.62 | R-32 | 23
217729336 | N/A | LG | HMSR-A-CB | ZRUM144BTE6 | ZRUM144BTE6 |  |  | ZRUM288BTE6 | Ducted Indoor Units | 276000 | 10.9 | 21.2 | 308000 | 3.54 | 198000 | 2.46 | R-32 | 23
217729337 | N/A | LG | HMSR-A-CB | ZRUM168BTE6 | ZRUM144BTE6 |  |  | ZRUM312BTE6 | Non-Ducted Indoor Units | 298000 | 10.8 | 21.2 | 332000 | 3.63 | 222000 | 2.55 | R-32 | 24.8333
217729338 | N/A | LG | HMSR-A-CB | ZRUM168BTE6 | ZRUM144BTE6 |  |  | ZRUM312BTE6 | Ducted Indoor Units | 298000 | 10.6 | 20.8 | 332000 | 3.47 | 222000 | 2.41 | R-32 | 24.8333
217729770 | N/A | LG | HMSR-A-CB | ZRUM168BTE6 | ZRUM144BTE6 |  |  | ZRUM312BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 21 | 332000 | 3.55 | 222000 | 2.48 | R-32 | 24.8333
217729771 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM144BTE6 |  |  | ZRUM336BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.5 | 358000 | 3.5 | 234000 | 2.42 | R-32 | 26.6667
217729778 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM192BTE6 | ZRUM121BTE6 |  | ZRUM504BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 480000 | 9.3 | 18.1 | 506000 | 3.37 | 348000 | 2.24 | R-32 | 40
217729317 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM144BTE6 |  |  | ZRUM336BTE6 | Ducted Indoor Units | 320000 | 10.3 | 20.4 | 358000 | 3.4 | 234000 | 2.36 | R-32 | 26.6667
217729339 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM144BTE6 |  |  | ZRUM336BTE6 | Non-Ducted Indoor Units | 320000 | 10.2 | 20.6 | 358000 | 3.61 | 234000 | 2.48 | R-32 | 26.6667
217729351 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM192BTE6 | ZRUM121BTE6 |  | ZRUM504BTE6 | Non-Ducted Indoor Units | 480000 | 9.3 | 18.4 | 506000 | 3.37 | 348000 | 2.33 | R-32 | 40
217729352 | N/A | LG | HMSR-A-CB | ZRUM192BTE6 | ZRUM192BTE6 | ZRUM121BTE6 |  | ZRUM504BTE6 | Ducted Indoor Units | 480000 | 9.3 | 17.8 | 506000 | 3.37 | 348000 | 2.15 | R-32 | 40
217729340 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM144BTE6 |  |  | ZRUM360BTE6 | Non-Ducted Indoor Units | 344000 | 10.5 | 21.2 | 364000 | 3.58 | 248000 | 2.37 | R-32 | 28.6667
217729341 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM168BTE6 |  |  | ZRUM384BTE6 | Non-Ducted Indoor Units | 366000 | 10.2 | 20.6 | 388000 | 3.5 | 266000 | 2.35 | R-32 | 30.5
217729342 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM168BTE6 |  |  | ZRUM384BTE6 | Ducted Indoor Units | 366000 | 10.1 | 19.5 | 388000 | 3.38 | 266000 | 2.34 | R-32 | 30.5
217729343 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM192BTE6 |  |  | ZRUM408BTE6 | Non-Ducted Indoor Units | 390000 | 9.9 | 20 | 412000 | 3.44 | 284000 | 2.32 | R-32 | 32.5
217729344 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM192BTE6 |  |  | ZRUM408BTE6 | Ducted Indoor Units | 390000 | 9.8 | 18.9 | 412000 | 3.38 | 284000 | 2.21 | R-32 | 32.5
217729345 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM216BTE6 |  |  | ZRUM432BTE6 | Non-Ducted Indoor Units | 410000 | 9.3 | 19.3 | 436000 | 3.44 | 298000 | 2.44 | R-32 | 34.1667
217729346 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM216BTE6 |  |  | ZRUM432BTE6 | Ducted Indoor Units | 410000 | 9.6 | 19.6 | 436000 | 3.38 | 298000 | 2.28 | R-32 | 34.1667
217729318 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM144BTE6 |  |  | ZRUM360BTE6 | Ducted Indoor Units | 344000 | 10.4 | 20.1 | 364000 | 3.39 | 248000 | 2.36 | R-32 | 28.6667
217729772 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM144BTE6 |  |  | ZRUM360BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.45 | 20.65 | 364000 | 3.48 | 248000 | 2.36 | R-32 | 28.6667
217729773 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM168BTE6 |  |  | ZRUM384BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.15 | 20.05 | 388000 | 3.44 | 266000 | 2.34 | R-32 | 30.5
217729774 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM192BTE6 |  |  | ZRUM408BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.85 | 19.45 | 412000 | 3.41 | 284000 | 2.26 | R-32 | 32.5
217729775 | N/A | LG | HMSR-A-CB | ZRUM216BTE6 | ZRUM216BTE6 |  |  | ZRUM432BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 19.45 | 436000 | 3.41 | 298000 | 2.36 | R-32 | 34.1667
217729776 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM216BTE6 |  |  | ZRUM456BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.45 | 18.8 | 458000 | 3.38 | 318000 | 2.34 | R-32 | 36.1667
217729777 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM241BTE6 |  |  | ZRUM480BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 454000 | 9.3 | 18.75 | 484000 | 3.37 | 332000 | 2.26 | R-32 | 37.8333
217729347 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM216BTE6 |  |  | ZRUM456BTE6 | Non-Ducted Indoor Units | 434000 | 9.3 | 19 | 458000 | 3.39 | 318000 | 2.42 | R-32 | 36.1667
217729348 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM216BTE6 |  |  | ZRUM456BTE6 | Ducted Indoor Units | 434000 | 9.6 | 18.6 | 458000 | 3.38 | 318000 | 2.26 | R-32 | 36.1667
217729349 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM241BTE6 |  |  | ZRUM480BTE6 | Non-Ducted Indoor Units | 454000 | 9.3 | 18.8 | 484000 | 3.37 | 332000 | 2.38 | R-32 | 37.8333
217729350 | N/A | LG | HMSR-A-CB | ZRUM241BTE6 | ZRUM241BTE6 |  |  | ZRUM480BTE6 | Ducted Indoor Units | 454000 | 9.3 | 18.7 | 484000 | 3.37 | 332000 | 2.15 | R-32 | 37.8333
217729314 | N/A | LG | HMSR-A-CB | ZRUM264BTE6 |  |  |  | ZRUM264BTE6 | Non-Ducted Indoor Units | 252000 | 11 | 22.4 | 256000 | 3.46 | 182000 | 2.52 | R-32 | 21
217729315 | N/A | LG | HMSR-A-CB | ZRUM264BTE6 |  |  |  | ZRUM264BTE6 | Ducted Indoor Units | 252000 | 10.9 | 19.9 | 256000 | 3.3 | 182000 | 2.2 | R-32 | 21
217729767 | N/A | LG | HMSR-A-CB | ZRUM264BTE6 |  |  |  | ZRUM264BTE6 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.95 | 21.15 | 256000 | 3.38 | 182000 | 2.36 | R-32 | 21
217729331 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM121DTE6 |  |  | ZRUM265DTE6 | Ducted Indoor Units | 252000 | 10.9 | 19.9 | 282000 | 3.3 | 182000 | 2.2 | R-32 | 21
217729353 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM121DTE6 |  |  | ZRUM265DTE6 | Non-Ducted Indoor Units | 252000 | 11 | 22.4 | 282000 | 3.46 | 182000 | 2.52 | R-32 | 21
217729354 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM144DTE6 |  |  | ZRUM288DTE6 | Non-Ducted Indoor Units | 276000 | 11.1 | 21.8 | 308000 | 3.66 | 198000 | 2.62 | R-32 | 23
217729355 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM144DTE6 |  |  | ZRUM288DTE6 | Ducted Indoor Units | 276000 | 10.9 | 21.2 | 308000 | 3.54 | 198000 | 2.46 | R-32 | 23
217729789 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM121DTE6 |  |  | ZRUM265DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.95 | 21.15 | 282000 | 3.38 | 182000 | 2.36 | R-32 | 21
217729790 | N/A | LG | HMSR-A-CB | ZRUM144DTE6 | ZRUM144DTE6 |  |  | ZRUM288DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11 | 21.5 | 308000 | 3.6 | 198000 | 2.54 | R-32 | 23
217729791 | N/A | LG | HMSR-A-CB | ZRUM168DTE6 | ZRUM144DTE6 |  |  | ZRUM312DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 21 | 332000 | 3.55 | 222000 | 2.48 | R-32 | 24.8333
217729356 | N/A | LG | HMSR-A-CB | ZRUM168DTE6 | ZRUM144DTE6 |  |  | ZRUM312DTE6 | Non-Ducted Indoor Units | 298000 | 10.8 | 21.2 | 332000 | 3.63 | 222000 | 2.55 | R-32 | 24.8333
217729357 | N/A | LG | HMSR-A-CB | ZRUM168DTE6 | ZRUM144DTE6 |  |  | ZRUM312DTE6 | Ducted Indoor Units | 298000 | 10.6 | 20.8 | 332000 | 3.47 | 222000 | 2.41 | R-32 | 24.8333
217729332 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM144DTE6 |  |  | ZRUM336DTE6 | Ducted Indoor Units | 320000 | 10.3 | 20.4 | 358000 | 3.4 | 234000 | 2.36 | R-32 | 26.6667
217729358 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM144DTE6 |  |  | ZRUM336DTE6 | Non-Ducted Indoor Units | 320000 | 10.2 | 20.6 | 358000 | 3.61 | 234000 | 2.48 | R-32 | 26.6667
217729792 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM144DTE6 |  |  | ZRUM336DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 20.5 | 358000 | 3.5 | 234000 | 2.42 | R-32 | 26.6667
217729799 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM192DTE6 | ZRUM121DTE6 |  | ZRUM504DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 480000 | 9.3 | 18.1 | 506000 | 3.37 | 348000 | 2.24 | R-32 | 40
217729370 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM192DTE6 | ZRUM121DTE6 |  | ZRUM504DTE6 | Non-Ducted Indoor Units | 480000 | 9.3 | 18.4 | 506000 | 3.37 | 348000 | 2.33 | R-32 | 40
217729371 | N/A | LG | HMSR-A-CB | ZRUM192DTE6 | ZRUM192DTE6 | ZRUM121DTE6 |  | ZRUM504DTE6 | Ducted Indoor Units | 480000 | 9.3 | 17.8 | 506000 | 3.37 | 348000 | 2.15 | R-32 | 40
217729793 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM144DTE6 |  |  | ZRUM360DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.45 | 20.65 | 364000 | 3.48 | 248000 | 2.36 | R-32 | 28.6667
217729794 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM168DTE6 |  |  | ZRUM384DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.15 | 20.05 | 388000 | 3.44 | 266000 | 2.34 | R-32 | 30.5
217729795 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM192DTE6 |  |  | ZRUM408DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.85 | 19.45 | 412000 | 3.41 | 284000 | 2.26 | R-32 | 32.5
217729796 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM216DTE6 |  |  | ZRUM432DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 19.45 | 436000 | 3.41 | 298000 | 2.36 | R-32 | 34.1667
217729359 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM144DTE6 |  |  | ZRUM360DTE6 | Non-Ducted Indoor Units | 344000 | 10.5 | 21.2 | 364000 | 3.58 | 248000 | 2.37 | R-32 | 28.6667
217729360 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM168DTE6 |  |  | ZRUM384DTE6 | Non-Ducted Indoor Units | 366000 | 10.2 | 20.6 | 388000 | 3.5 | 266000 | 2.35 | R-32 | 30.5
217729361 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM168DTE6 |  |  | ZRUM384DTE6 | Ducted Indoor Units | 366000 | 10.1 | 19.5 | 388000 | 3.38 | 266000 | 2.34 | R-32 | 30.5
217729362 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM192DTE6 |  |  | ZRUM408DTE6 | Non-Ducted Indoor Units | 390000 | 9.9 | 20 | 412000 | 3.44 | 284000 | 2.32 | R-32 | 32.5
217729363 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM192DTE6 |  |  | ZRUM408DTE6 | Ducted Indoor Units | 390000 | 9.8 | 18.9 | 412000 | 3.38 | 284000 | 2.21 | R-32 | 32.5
217729364 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM216DTE6 |  |  | ZRUM432DTE6 | Non-Ducted Indoor Units | 410000 | 9.3 | 19.3 | 436000 | 3.44 | 298000 | 2.44 | R-32 | 34.1667
217729365 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM216DTE6 |  |  | ZRUM432DTE6 | Ducted Indoor Units | 410000 | 9.6 | 19.6 | 436000 | 3.38 | 298000 | 2.28 | R-32 | 34.1667
217729333 | N/A | LG | HMSR-A-CB | ZRUM216DTE6 | ZRUM144DTE6 |  |  | ZRUM360DTE6 | Ducted Indoor Units | 344000 | 10.4 | 20.1 | 364000 | 3.39 | 248000 | 2.36 | R-32 | 28.6667
217729366 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM216DTE6 |  |  | ZRUM456DTE6 | Non-Ducted Indoor Units | 434000 | 9.3 | 19 | 458000 | 3.39 | 318000 | 2.42 | R-32 | 36.1667
217729367 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM216DTE6 |  |  | ZRUM456DTE6 | Ducted Indoor Units | 434000 | 9.6 | 18.6 | 458000 | 3.38 | 318000 | 2.26 | R-32 | 36.1667
217729368 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM241DTE6 |  |  | ZRUM480DTE6 | Non-Ducted Indoor Units | 454000 | 9.3 | 18.8 | 484000 | 3.37 | 332000 | 2.38 | R-32 | 37.8333
217729369 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM241DTE6 |  |  | ZRUM480DTE6 | Ducted Indoor Units | 454000 | 9.3 | 18.7 | 484000 | 3.37 | 332000 | 2.15 | R-32 | 37.8333
217729797 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM216DTE6 |  |  | ZRUM456DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.45 | 18.8 | 458000 | 3.38 | 318000 | 2.34 | R-32 | 36.1667
217729798 | N/A | LG | HMSR-A-CB | ZRUM241DTE6 | ZRUM241DTE6 |  |  | ZRUM480DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 454000 | 9.3 | 18.75 | 484000 | 3.37 | 332000 | 2.26 | R-32 | 37.8333
217729788 | N/A | LG | HMSR-A-CB | ZRUM264DTE6 |  |  |  | ZRUM264DTE6 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.95 | 21.15 | 256000 | 3.38 | 182000 | 2.36 | R-32 | 21
217729329 | N/A | LG | HMSR-A-CB | ZRUM264DTE6 |  |  |  | ZRUM264DTE6 | Non-Ducted Indoor Units | 252000 | 11 | 22.4 | 256000 | 3.46 | 182000 | 2.52 | R-32 | 21
217729330 | N/A | LG | HMSR-A-CB | ZRUM264DTE6 |  |  |  | ZRUM264DTE6 | Ducted Indoor Units | 252000 | 10.9 | 19.9 | 256000 | 3.3 | 182000 | 2.2 | R-32 | 21
217734398 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB2881FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.55 | 21.9 | 308000 | 3.52 | 200000 | 2.38 | R-454B | 23
217734341 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB2881FT6P-UL | Ducted Indoor Units | 276000 | 10.5 | 21 | 308000 | 3.26 | 200000 | 2.38 | R-454B | 23
217734274 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB2881FT6P-UL | Non-Ducted Indoor Units | 276000 | 10.6 | 22.8 | 308000 | 3.78 | 200000 | 2.38 | R-454B | 23
217734273 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB2641FT6P-UL | Non-Ducted Indoor Units | 252000 | 10.6 | 22.8 | 284000 | 3.78 | 196000 | 2.31 | R-454B | 21
217734275 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB3121FT6P-UL | Non-Ducted Indoor Units | 298000 | 10.5 | 22.2 | 334000 | 3.78 | 222000 | 2.38 | R-454B | 24.8333
217734276 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL |  |  | MMY-UB3361FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.5 | 21.4 | 360000 | 3.53 | 244000 | 2.36 | R-454B | 26.6667
217734277 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB3601FT6P-UL | Non-Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.42 | 270000 | 2.36 | R-454B | 28.6667
217734278 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  | MMY-UB3841FT6P-UL | Non-Ducted Indoor Units | 366000 | 10.1 | 20.4 | 412000 | 3.46 | 278000 | 2.5 | R-454B | 30.5
217734279 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4081FT6P-UL | Non-Ducted Indoor Units | 390000 | 10 | 20.2 | 438000 | 3.49 | 296000 | 2.45 | R-454B | 32.5
217734280 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4321FT6P-UL | Non-Ducted Indoor Units | 412000 | 9.9 | 20 | 462000 | 3.41 | 318000 | 2.39 | R-454B | 34.3333
217734281 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB1441FT6P-UL |  | MMY-UB4561FT6P-UL | Non-Ducted Indoor Units | 436000 | 9.9 | 19.8 | 488000 | 3.33 | 322000 | 2.38 | R-454B | 36.3333
217734282 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL |  | MMY-UB4801FT6P-UL | Non-Ducted Indoor Units | 458000 | 9.4 | 19.8 | 514000 | 3.3 | 344000 | 2.37 | R-454B | 38.1667
217734343 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB3121FT6P-UL | Ducted Indoor Units | 298000 | 10.4 | 20.1 | 334000 | 3.25 | 222000 | 2.38 | R-454B | 24.8333
217734347 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB3601FT6P-UL | Ducted Indoor Units | 344000 | 9.6 | 18.2 | 386000 | 3.26 | 270000 | 2.39 | R-454B | 28.6667
217734349 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  | MMY-UB3841FT6P-UL | Ducted Indoor Units | 366000 | 9.6 | 17.7 | 412000 | 3.26 | 278000 | 2.39 | R-454B | 30.5
217734351 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4081FT6P-UL | Ducted Indoor Units | 390000 | 9.6 | 17.4 | 438000 | 3.26 | 296000 | 2.38 | R-454B | 32.5
217734353 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4321FT6P-UL | Ducted Indoor Units | 412000 | 9.5 | 16.9 | 462000 | 3.26 | 318000 | 2.35 | R-454B | 34.3333
217734396 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL |  |  | MMY-UB2641FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.95 | 284000 | 3.49 | 196000 | 2.34 | R-454B | 21
217734400 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL |  |  | MMY-UB3121FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 21.15 | 334000 | 3.51 | 222000 | 2.38 | R-454B | 24.8333
217734402 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL |  |  | MMY-UB3361FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.4 | 20.55 | 360000 | 3.38 | 244000 | 2.37 | R-454B | 26.6667
217734404 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB3601FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 19.35 | 386000 | 3.34 | 270000 | 2.37 | R-454B | 28.6667
217734406 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0721FT6P-UL |  | MMY-UB3841FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.85 | 19.05 | 412000 | 3.36 | 278000 | 2.44 | R-454B | 30.5
217734408 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4081FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.8 | 18.8 | 438000 | 3.37 | 296000 | 2.41 | R-454B | 32.5
217734410 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL | MMY-MUB0961FT6P-UL |  | MMY-UB4321FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.7 | 18.45 | 462000 | 3.33 | 318000 | 2.37 | R-454B | 34.3333
217734412 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL | MMY-MUB1441FT6P-UL |  | MMY-UB4561FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 436000 | 9.7 | 17.8 | 488000 | 3.29 | 322000 | 2.36 | R-454B | 36.3333
217734414 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT6P-UL | MMY-MUB1681FT6P-UL | MMY-MUB1441FT6P-UL |  | MMY-UB4801FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 458000 | 9.4 | 17.8 | 514000 | 3.26 | 344000 | 2.35 | R-454B | 38.1667
217734319 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  | MMY-UB288H1FT6PUL | Non-Ducted Indoor Units | 276000 | 11 | 21 | 308000 | 3.8 | 258000 | 2.36 | R-454B | 23
217734430 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  | MMY-UB288H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.3 | 20.4 | 308000 | 3.53 | 258000 | 2.29 | R-454B | 23
217734373 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL | MMY-MUB096H1FT6PUL |  | MMY-UB288H1FT6PUL | Ducted Indoor Units | 276000 | 11.6 | 19.8 | 308000 | 3.26 | 258000 | 2.23 | R-454B | 23
217734375 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  | MMY-UB360H1FT6PUL | Ducted Indoor Units | 344000 | 10.8 | 19 | 386000 | 3.26 | 330000 | 2.21 | R-454B | 28.6667
217734432 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  | MMY-UB360H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.9 | 19.95 | 386000 | 3.38 | 330000 | 2.27 | R-454B | 28.6667
217734321 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL | MMY-MUB120H1FT6PUL |  | MMY-UB360H1FT6PUL | Non-Ducted Indoor Units | 344000 | 11 | 20.9 | 386000 | 3.51 | 330000 | 2.33 | R-454B | 28.6667
217734399 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB2881FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.55 | 21.9 | 308000 | 3.52 | 200000 | 2.38 | R-454B | 23
217734297 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB2881FT9P-UL | Non-Ducted Indoor Units | 276000 | 10.6 | 22.8 | 308000 | 3.78 | 200000 | 2.38 | R-454B | 23
217734342 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1441FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB2881FT9P-UL | Ducted Indoor Units | 276000 | 10.5 | 21 | 308000 | 3.26 | 200000 | 2.38 | R-454B | 23
217734344 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB3121FT9P-UL | Ducted Indoor Units | 298000 | 10.4 | 20.1 | 334000 | 3.25 | 222000 | 2.38 | R-454B | 24.8333
217734352 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4081FT9P-UL | Ducted Indoor Units | 390000 | 9.6 | 17.4 | 438000 | 3.26 | 296000 | 2.38 | R-454B | 32.5
217734350 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  | MMY-UB3841FT9P-UL | Ducted Indoor Units | 366000 | 9.6 | 17.7 | 412000 | 3.26 | 278000 | 2.39 | R-454B | 30.5
217734348 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB3601FT9P-UL | Ducted Indoor Units | 344000 | 9.6 | 18.2 | 386000 | 3.26 | 270000 | 2.39 | R-454B | 28.6667
217734354 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4321FT9P-UL | Ducted Indoor Units | 412000 | 9.5 | 16.9 | 462000 | 3.26 | 318000 | 2.35 | R-454B | 34.3333
217734298 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB3121FT9P-UL | Non-Ducted Indoor Units | 298000 | 10.5 | 22.2 | 334000 | 3.78 | 222000 | 2.38 | R-454B | 24.8333
217734299 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL |  |  | MMY-UB3361FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.5 | 21.4 | 360000 | 3.53 | 244000 | 2.36 | R-454B | 26.6667
217734300 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB3601FT9P-UL | Non-Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.42 | 270000 | 2.36 | R-454B | 28.6667
217734301 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  | MMY-UB3841FT9P-UL | Non-Ducted Indoor Units | 366000 | 10.1 | 20.4 | 412000 | 3.46 | 278000 | 2.5 | R-454B | 30.5
217734302 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4081FT9P-UL | Non-Ducted Indoor Units | 390000 | 10 | 20.2 | 438000 | 3.49 | 296000 | 2.45 | R-454B | 32.5
217734303 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4321FT9P-UL | Non-Ducted Indoor Units | 412000 | 9.9 | 20 | 462000 | 3.41 | 318000 | 2.39 | R-454B | 34.3333
217734304 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB1441FT9P-UL |  | MMY-UB4561FT9P-UL | Non-Ducted Indoor Units | 436000 | 9.9 | 19.8 | 488000 | 3.33 | 322000 | 2.38 | R-454B | 36.3333
217734305 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL |  | MMY-UB4801FT9P-UL | Non-Ducted Indoor Units | 458000 | 9.4 | 19.8 | 514000 | 3.3 | 344000 | 2.37 | R-454B | 38.1667
217734296 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB2641FT9P-UL | Non-Ducted Indoor Units | 252000 | 10.6 | 22.8 | 284000 | 3.78 | 196000 | 2.31 | R-454B | 21
217734397 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL |  |  | MMY-UB2641FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.95 | 284000 | 3.49 | 196000 | 2.34 | R-454B | 21
217734403 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL |  |  | MMY-UB3361FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.4 | 20.55 | 360000 | 3.38 | 244000 | 2.37 | R-454B | 26.6667
217734401 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL |  |  | MMY-UB3121FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.45 | 21.15 | 334000 | 3.51 | 222000 | 2.38 | R-454B | 24.8333
217734415 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL |  | MMY-UB4801FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 458000 | 9.4 | 17.8 | 514000 | 3.26 | 344000 | 2.35 | R-454B | 38.1667
217734413 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB1441FT9P-UL |  | MMY-UB4561FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 436000 | 9.7 | 17.8 | 488000 | 3.29 | 322000 | 2.36 | R-454B | 36.3333
217734411 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4321FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.7 | 18.45 | 462000 | 3.33 | 318000 | 2.37 | R-454B | 34.3333
217734409 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB4081FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.8 | 18.8 | 438000 | 3.37 | 296000 | 2.41 | R-454B | 32.5
217734407 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB1441FT9P-UL | MMY-MUB0721FT9P-UL |  | MMY-UB3841FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.85 | 19.05 | 412000 | 3.36 | 278000 | 2.44 | R-454B | 30.5
217734405 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB1681FT9P-UL | MMY-MUB0961FT9P-UL | MMY-MUB0961FT9P-UL |  | MMY-UB3601FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 19.35 | 386000 | 3.34 | 270000 | 2.37 | R-454B | 28.6667
217734320 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  | MMY-UB288H1FT9PUL | Non-Ducted Indoor Units | 276000 | 11 | 21 | 308000 | 3.8 | 258000 | 2.36 | R-454B | 23
217734431 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  | MMY-UB288H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.3 | 20.4 | 308000 | 3.53 | 258000 | 2.29 | R-454B | 23
217734374 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL | MMY-MUB096H1FT9PUL |  | MMY-UB288H1FT9PUL | Ducted Indoor Units | 276000 | 11.6 | 19.8 | 308000 | 3.26 | 258000 | 2.23 | R-454B | 23
217734376 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  | MMY-UB360H1FT9PUL | Ducted Indoor Units | 344000 | 10.8 | 19 | 386000 | 3.26 | 330000 | 2.21 | R-454B | 28.6667
217734433 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  | MMY-UB360H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.9 | 19.95 | 386000 | 3.38 | 330000 | 2.27 | R-454B | 28.6667
217734322 | N/A | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL | MMY-MUB120H1FT9PUL |  | MMY-UB360H1FT9PUL | Non-Ducted Indoor Units | 344000 | 11 | 20.9 | 386000 | 3.51 | 330000 | 2.33 | R-454B | 28.6667
217735112 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB2881HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 21.45 | 308000 | 3.52 | 200000 | 2.38 | R-454B | 23
217735034 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB2881HT6P-UL | Ducted Indoor Units | 276000 | 9.8 | 20.6 | 308000 | 3.26 | 200000 | 2.38 | R-454B | 23
217735035 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB2881HT6P-UL | Non-Ducted Indoor Units | 276000 | 9.7 | 22.3 | 308000 | 3.78 | 200000 | 2.38 | R-454B | 23
217735031 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB2641HT6P-UL | Non-Ducted Indoor Units | 252000 | 9.7 | 22.3 | 284000 | 3.78 | 196000 | 2.31 | R-454B | 21
217735042 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB3121HT6P-UL | Ducted Indoor Units | 298000 | 9.7 | 19.7 | 334000 | 3.25 | 222000 | 2.38 | R-454B | 24.8333
217735043 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB3121HT6P-UL | Non-Ducted Indoor Units | 298000 | 9.4 | 21.7 | 334000 | 3.78 | 222000 | 2.38 | R-454B | 24.8333
217735110 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL |  |  | MMY-UB2641HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.75 | 21.5 | 284000 | 3.49 | 196000 | 2.34 | R-454B | 21
217735116 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL |  |  | MMY-UB3121HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.55 | 20.7 | 334000 | 3.51 | 222000 | 2.38 | R-454B | 24.8333
217735118 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL |  |  | MMY-UB3361HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.5 | 20.25 | 360000 | 3.38 | 244000 | 2.37 | R-454B | 26.6667
217735120 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB3601HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.1 | 18.95 | 386000 | 3.34 | 270000 | 2.37 | R-454B | 28.6667
217735124 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  | MMY-UB3841HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.1 | 18.85 | 412000 | 3.36 | 278000 | 2.44 | R-454B | 30.5
217735126 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4081HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.1 | 18.45 | 438000 | 3.37 | 296000 | 2.41 | R-454B | 32.5
217735128 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4321HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 18.05 | 462000 | 3.33 | 318000 | 2.37 | R-454B | 34.3333
217735130 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB1441HT6P-UL |  | MMY-UB4561HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 436000 | 9.1 | 17.4 | 488000 | 3.29 | 322000 | 2.36 | R-454B | 36.3333
217735132 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL |  | MMY-UB4801HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 458000 | 9.1 | 17.4 | 514000 | 3.26 | 344000 | 2.35 | R-454B | 38.1667
217735047 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL |  |  | MMY-UB3361HT6P-UL | Non-Ducted Indoor Units | 320000 | 9.4 | 21.2 | 360000 | 3.53 | 244000 | 2.36 | R-454B | 26.6667
217735050 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB3601HT6P-UL | Ducted Indoor Units | 344000 | 9.1 | 17.8 | 386000 | 3.26 | 270000 | 2.39 | R-454B | 28.6667
217735051 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB3601HT6P-UL | Non-Ducted Indoor Units | 344000 | 9.1 | 20.1 | 386000 | 3.42 | 270000 | 2.36 | R-454B | 28.6667
217735058 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  | MMY-UB3841HT6P-UL | Ducted Indoor Units | 366000 | 9.1 | 17.6 | 412000 | 3.26 | 278000 | 2.39 | R-454B | 30.5
217735059 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0721HT6P-UL |  | MMY-UB3841HT6P-UL | Non-Ducted Indoor Units | 366000 | 9.1 | 20.1 | 412000 | 3.46 | 278000 | 2.5 | R-454B | 30.5
217735062 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4081HT6P-UL | Ducted Indoor Units | 390000 | 9.1 | 17.2 | 438000 | 3.26 | 296000 | 2.38 | R-454B | 32.5
217735063 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4081HT6P-UL | Non-Ducted Indoor Units | 390000 | 9.1 | 19.7 | 438000 | 3.49 | 296000 | 2.45 | R-454B | 32.5
217735066 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4321HT6P-UL | Ducted Indoor Units | 412000 | 9.1 | 16.6 | 462000 | 3.26 | 318000 | 2.35 | R-454B | 34.3333
217735067 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL | MMY-MUB0961HT6P-UL |  | MMY-UB4321HT6P-UL | Non-Ducted Indoor Units | 412000 | 9.1 | 19.5 | 462000 | 3.41 | 318000 | 2.39 | R-454B | 34.3333
217735071 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL | MMY-MUB1441HT6P-UL |  | MMY-UB4561HT6P-UL | Non-Ducted Indoor Units | 436000 | 9.1 | 19.3 | 488000 | 3.33 | 322000 | 2.38 | R-454B | 36.3333
217735075 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT6P-UL | MMY-MUB1681HT6P-UL | MMY-MUB1441HT6P-UL |  | MMY-UB4801HT6P-UL | Non-Ducted Indoor Units | 458000 | 9.1 | 19.3 | 514000 | 3.3 | 344000 | 2.37 | R-454B | 38.1667
217735038 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  | MMY-UB288H1HT6PUL | Ducted Indoor Units | 276000 | 10.9 | 19.6 | 308000 | 3.26 | 258000 | 2.23 | R-454B | 23
217735039 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  | MMY-UB288H1HT6PUL | Non-Ducted Indoor Units | 276000 | 10.3 | 20.9 | 308000 | 3.8 | 258000 | 2.36 | R-454B | 23
217735114 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL | MMY-MUB096H1HT6PUL |  | MMY-UB288H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.6 | 20.25 | 308000 | 3.53 | 258000 | 2.29 | R-454B | 23
217735122 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  | MMY-UB360H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 19.85 | 386000 | 3.38 | 330000 | 2.27 | R-454B | 28.6667
217735054 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  | MMY-UB360H1HT6PUL | Ducted Indoor Units | 344000 | 10.3 | 18.8 | 386000 | 3.26 | 330000 | 2.21 | R-454B | 28.6667
217735055 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL | MMY-MUB120H1HT6PUL |  | MMY-UB360H1HT6PUL | Non-Ducted Indoor Units | 344000 | 10 | 20.9 | 386000 | 3.51 | 330000 | 2.33 | R-454B | 28.6667
217735113 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB2881HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 21.45 | 308000 | 3.52 | 200000 | 2.38 | R-454B | 23
217735036 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB2881HT9P-UL | Ducted Indoor Units | 276000 | 9.8 | 20.6 | 308000 | 3.26 | 200000 | 2.38 | R-454B | 23
217735037 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1441HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB2881HT9P-UL | Non-Ducted Indoor Units | 276000 | 9.7 | 22.3 | 308000 | 3.78 | 200000 | 2.38 | R-454B | 23
217735033 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB2641HT9P-UL | Non-Ducted Indoor Units | 252000 | 9.7 | 22.3 | 284000 | 3.78 | 196000 | 2.31 | R-454B | 21
217735044 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB3121HT9P-UL | Ducted Indoor Units | 298000 | 9.7 | 19.7 | 334000 | 3.25 | 222000 | 2.38 | R-454B | 24.8333
217735045 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB3121HT9P-UL | Non-Ducted Indoor Units | 298000 | 9.4 | 21.7 | 334000 | 3.78 | 222000 | 2.38 | R-454B | 24.8333
217735111 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL |  |  | MMY-UB2641HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.75 | 21.5 | 284000 | 3.49 | 196000 | 2.34 | R-454B | 21
217735121 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB3601HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.1 | 18.95 | 386000 | 3.34 | 270000 | 2.37 | R-454B | 28.6667
217735119 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL |  |  | MMY-UB3361HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.5 | 20.25 | 360000 | 3.38 | 244000 | 2.37 | R-454B | 26.6667
217735117 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL |  |  | MMY-UB3121HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.55 | 20.7 | 334000 | 3.51 | 222000 | 2.38 | R-454B | 24.8333
217735131 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB1441HT9P-UL |  | MMY-UB4561HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 436000 | 9.1 | 17.4 | 488000 | 3.29 | 322000 | 2.36 | R-454B | 36.3333
217735129 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4321HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 18.05 | 462000 | 3.33 | 318000 | 2.37 | R-454B | 34.3333
217735127 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4081HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.1 | 18.45 | 438000 | 3.37 | 296000 | 2.41 | R-454B | 32.5
217735125 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  | MMY-UB3841HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.1 | 18.85 | 412000 | 3.36 | 278000 | 2.44 | R-454B | 30.5
217735133 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL |  | MMY-UB4801HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 458000 | 9.1 | 17.4 | 514000 | 3.26 | 344000 | 2.35 | R-454B | 38.1667
217735060 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  | MMY-UB3841HT9P-UL | Ducted Indoor Units | 366000 | 9.1 | 17.6 | 412000 | 3.26 | 278000 | 2.39 | R-454B | 30.5
217735061 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0721HT9P-UL |  | MMY-UB3841HT9P-UL | Non-Ducted Indoor Units | 366000 | 9.1 | 20.1 | 412000 | 3.46 | 278000 | 2.5 | R-454B | 30.5
217735052 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB3601HT9P-UL | Ducted Indoor Units | 344000 | 9.1 | 17.8 | 386000 | 3.26 | 270000 | 2.39 | R-454B | 28.6667
217735053 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB3601HT9P-UL | Non-Ducted Indoor Units | 344000 | 9.1 | 20.1 | 386000 | 3.42 | 270000 | 2.36 | R-454B | 28.6667
217735049 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL |  |  | MMY-UB3361HT9P-UL | Non-Ducted Indoor Units | 320000 | 9.4 | 21.2 | 360000 | 3.53 | 244000 | 2.36 | R-454B | 26.6667
217735077 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL |  | MMY-UB4801HT9P-UL | Non-Ducted Indoor Units | 458000 | 9.1 | 19.3 | 514000 | 3.3 | 344000 | 2.37 | R-454B | 38.1667
217735073 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB1441HT9P-UL |  | MMY-UB4561HT9P-UL | Non-Ducted Indoor Units | 436000 | 9.1 | 19.3 | 488000 | 3.33 | 322000 | 2.38 | R-454B | 36.3333
217735068 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4321HT9P-UL | Ducted Indoor Units | 412000 | 9.1 | 16.6 | 462000 | 3.26 | 318000 | 2.35 | R-454B | 34.3333
217735069 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1681HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4321HT9P-UL | Non-Ducted Indoor Units | 412000 | 9.1 | 19.5 | 462000 | 3.41 | 318000 | 2.39 | R-454B | 34.3333
217735064 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4081HT9P-UL | Ducted Indoor Units | 390000 | 9.1 | 17.2 | 438000 | 3.26 | 296000 | 2.38 | R-454B | 32.5
217735065 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB1681HT9P-UL | MMY-MUB1441HT9P-UL | MMY-MUB0961HT9P-UL |  | MMY-UB4081HT9P-UL | Non-Ducted Indoor Units | 390000 | 9.1 | 19.7 | 438000 | 3.49 | 296000 | 2.45 | R-454B | 32.5
217735040 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  | MMY-UB288H1HT9PUL | Ducted Indoor Units | 276000 | 10.9 | 19.6 | 308000 | 3.26 | 258000 | 2.23 | R-454B | 23
217735041 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  | MMY-UB288H1HT9PUL | Non-Ducted Indoor Units | 276000 | 10.3 | 20.9 | 308000 | 3.8 | 258000 | 2.36 | R-454B | 23
217735115 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL | MMY-MUB096H1HT9PUL |  | MMY-UB288H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.6 | 20.25 | 308000 | 3.53 | 258000 | 2.29 | R-454B | 23
217735123 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  | MMY-UB360H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 19.85 | 386000 | 3.38 | 330000 | 2.27 | R-454B | 28.6667
217735056 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  | MMY-UB360H1HT9PUL | Ducted Indoor Units | 344000 | 10.3 | 18.8 | 386000 | 3.26 | 330000 | 2.21 | R-454B | 28.6667
217735057 | N/A | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL | MMY-MUB120H1HT9PUL |  | MMY-UB360H1HT9PUL | Non-Ducted Indoor Units | 344000 | 10 | 20.9 | 386000 | 3.51 | 330000 | 2.33 | R-454B | 28.6667
217902163 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120TXU-A | PURY-EM144TXU-A |  |  | PURY-EM264TSXU-A | Non-Ducted Indoor Units | 250000 | 12.3 | 23.4 | 280000 | 3.67 | 172000 | 2.31 | R-32 | 20.8333
217902165 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120TXU-A | PURY-EM144TXU-A |  |  | PURY-EM264TSXU-A | Ducted Indoor Units | 250000 | 11.9 | 21.5 | 280000 | 3.55 | 172000 | 2.28 | R-32 | 20.8333
217902167 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A | PURY-EM144TXU-A |  |  | PURY-EM288TSXU-A | Non-Ducted Indoor Units | 276000 | 11.9 | 22.4 | 304000 | 3.57 | 180000 | 2.3 | R-32 | 23
217902168 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A | PURY-EM144TXU-A |  |  | PURY-EM288TSXU-A | Ducted Indoor Units | 276000 | 11.6 | 20.6 | 304000 | 3.51 | 180000 | 2.25 | R-32 | 23
217902171 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A | PURY-EM168TXU-A |  |  | PURY-EM312TSXU-A | Non-Ducted Indoor Units | 298000 | 11.2 | 22.2 | 334000 | 3.52 | 196000 | 2.23 | R-32 | 24.8333
217902172 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144TXU-A | PURY-EM168TXU-A |  |  | PURY-EM312TSXU-A | Ducted Indoor Units | 298000 | 11.2 | 20.1 | 334000 | 3.38 | 196000 | 2.18 | R-32 | 24.8333
217902175 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A | PURY-EM168TXU-A |  |  | PURY-EM336TSXU-A | Non-Ducted Indoor Units | 320000 | 10.6 | 21.9 | 360000 | 3.33 | 210000 | 2.18 | R-32 | 26.6667
217902176 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A | PURY-EM168TXU-A |  |  | PURY-EM336TSXU-A | Ducted Indoor Units | 320000 | 10.8 | 19.6 | 360000 | 3.35 | 210000 | 2.21 | R-32 | 26.6667
217902179 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A | PURY-EM192TXU-A |  |  | PURY-EM360TSXU-A | Non-Ducted Indoor Units | 344000 | 10.2 | 22 | 362000 | 3.33 | 220000 | 2.15 | R-32 | 28.6667
217902180 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168TXU-A | PURY-EM192TXU-A |  |  | PURY-EM360TSXU-A | Ducted Indoor Units | 344000 | 10.2 | 19.2 | 362000 | 3.33 | 220000 | 2.18 | R-32 | 28.6667
217902183 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192TXU-A | PURY-EM192TXU-A |  |  | PURY-EM384TSXU-A | Non-Ducted Indoor Units | 368000 | 9.9 | 20.9 | 368000 | 3.31 | 258000 | 2.11 | R-32 | 30.6667
217902184 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192TXU-A | PURY-EM192TXU-A |  |  | PURY-EM384TSXU-A | Ducted Indoor Units | 368000 | 9.7 | 18.9 | 368000 | 3.29 | 258000 | 2.15 | R-32 | 30.6667
217902164 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120YXU-A | PURY-EM144YXU-A |  |  | PURY-EM264YSXU-A | Non-Ducted Indoor Units | 250000 | 12.3 | 23.4 | 280000 | 3.67 | 172000 | 2.31 | R-32 | 20.8333
217902166 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM120YXU-A | PURY-EM144YXU-A |  |  | PURY-EM264YSXU-A | Ducted Indoor Units | 250000 | 11.9 | 21.5 | 280000 | 3.55 | 172000 | 2.28 | R-32 | 20.8333
217902173 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A | PURY-EM168YXU-A |  |  | PURY-EM312YSXU-A | Non-Ducted Indoor Units | 298000 | 11.2 | 22.2 | 334000 | 3.52 | 196000 | 2.23 | R-32 | 24.8333
217902174 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A | PURY-EM168YXU-A |  |  | PURY-EM312YSXU-A | Ducted Indoor Units | 298000 | 11.2 | 20.1 | 334000 | 3.38 | 196000 | 2.18 | R-32 | 24.8333
217902169 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A | PURY-EM144YXU-A |  |  | PURY-EM288YSXU-A | Non-Ducted Indoor Units | 276000 | 11.9 | 22.4 | 304000 | 3.57 | 180000 | 2.3 | R-32 | 23
217902170 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM144YXU-A | PURY-EM144YXU-A |  |  | PURY-EM288YSXU-A | Ducted Indoor Units | 276000 | 11.6 | 20.6 | 304000 | 3.51 | 180000 | 2.25 | R-32 | 23
217902181 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A | PURY-EM192YXU-A |  |  | PURY-EM360YSXU-A | Non-Ducted Indoor Units | 344000 | 10.2 | 22 | 362000 | 3.33 | 220000 | 2.15 | R-32 | 28.6667
217902182 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A | PURY-EM192YXU-A |  |  | PURY-EM360YSXU-A | Ducted Indoor Units | 344000 | 10.2 | 19.2 | 362000 | 3.33 | 220000 | 2.18 | R-32 | 28.6667
217902177 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A | PURY-EM168YXU-A |  |  | PURY-EM336YSXU-A | Non-Ducted Indoor Units | 320000 | 10.6 | 21.9 | 360000 | 3.33 | 210000 | 2.18 | R-32 | 26.6667
217902178 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM168YXU-A | PURY-EM168YXU-A |  |  | PURY-EM336YSXU-A | Ducted Indoor Units | 320000 | 10.8 | 19.6 | 360000 | 3.35 | 210000 | 2.21 | R-32 | 26.6667
217902185 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192YXU-A | PURY-EM192YXU-A |  |  | PURY-EM384YSXU-A | Non-Ducted Indoor Units | 368000 | 9.9 | 20.9 | 368000 | 3.31 | 258000 | 2.11 | R-32 | 30.6667
217902186 | N/A | Mitsubishi Electric | HMSR-A-CB | PURY-EM192YXU-A | PURY-EM192YXU-A |  |  | PURY-EM384YSXU-A | Ducted Indoor Units | 368000 | 9.7 | 18.9 | 368000 | 3.29 | 258000 | 2.15 | R-32 | 30.6667
217902307 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AMM0AN | TURYE1443AMM0AN |  |  | TURYE2643BMM0AN | Ducted Indoor Units | 252000 | 11.9 | 21.5 | 280000 | 3.55 | 172000 | 2.28 | R-32 | 21
217902308 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1203AMM0AN | TURYE1443AMM0AN |  |  | TURYE2643BMM0AN | Non-Ducted Indoor Units | 252000 | 12.3 | 23.4 | 280000 | 3.67 | 172000 | 2.31 | R-32 | 21
217902311 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN | TURYE1443AMM0AN |  |  | TURYE2883BMM0AN | Ducted Indoor Units | 276000 | 11.6 | 20.6 | 304000 | 3.51 | 180000 | 2.25 | R-32 | 23
217902312 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN | TURYE1443AMM0AN |  |  | TURYE2883BMM0AN | Non-Ducted Indoor Units | 276000 | 11.9 | 22.4 | 304000 | 3.57 | 180000 | 2.3 | R-32 | 23
217902315 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN | TURYE1683AMM0AN |  |  | TURYE3123BMM0AN | Ducted Indoor Units | 298000 | 11.2 | 20.1 | 334000 | 3.38 | 196000 | 2.18 | R-32 | 24.8333
217902316 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AMM0AN | TURYE1683AMM0AN |  |  | TURYE3123BMM0AN | Non-Ducted Indoor Units | 298000 | 11.2 | 22.2 | 334000 | 3.52 | 196000 | 2.23 | R-32 | 24.8333
217902319 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN | TURYE1683AMM0AN |  |  | TURYE3363BMM0AN | Ducted Indoor Units | 320000 | 10.8 | 19.6 | 360000 | 3.35 | 210000 | 2.21 | R-32 | 26.6667
217902320 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN | TURYE1683AMM0AN |  |  | TURYE3363BMM0AN | Non-Ducted Indoor Units | 320000 | 10.6 | 21.9 | 360000 | 3.33 | 210000 | 2.18 | R-32 | 26.6667
217902323 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN | TURYE1923AMM0AN |  |  | TURYE3603BMM0AN | Ducted Indoor Units | 344000 | 10.2 | 19.2 | 362000 | 3.33 | 220000 | 2.18 | R-32 | 28.6667
217902324 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AMM0AN | TURYE1923AMM0AN |  |  | TURYE3603BMM0AN | Non-Ducted Indoor Units | 344000 | 10.2 | 22 | 362000 | 3.33 | 220000 | 2.15 | R-32 | 28.6667
217902327 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AMM0AN | TURYE1923AMM0AN |  |  | TURYE3843BMM0AN | Ducted Indoor Units | 368000 | 9.7 | 18.9 | 368000 | 3.29 | 258000 | 2.15 | R-32 | 30.6667
217902328 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1923AMM0AN | TURYE1923AMM0AN |  |  | TURYE3843BMM0AN | Non-Ducted Indoor Units | 368000 | 9.9 | 20.9 | 368000 | 3.31 | 258000 | 2.11 | R-32 | 30.6667
217902309 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AMM0AN | TURYE1444AMM0AN |  |  | TURYE2644BMM0AN | Ducted Indoor Units | 252000 | 11.9 | 21.5 | 280000 | 3.55 | 172000 | 2.28 | R-32 | 21
217902310 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1204AMM0AN | TURYE1444AMM0AN |  |  | TURYE2644BMM0AN | Non-Ducted Indoor Units | 252000 | 12.3 | 23.4 | 280000 | 3.67 | 172000 | 2.31 | R-32 | 21
217902317 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN | TURYE1684AMM0AN |  |  | TURYE3124BMM0AN | Ducted Indoor Units | 298000 | 11.2 | 20.1 | 334000 | 3.38 | 196000 | 2.18 | R-32 | 24.8333
217902318 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN | TURYE1684AMM0AN |  |  | TURYE3124BMM0AN | Non-Ducted Indoor Units | 298000 | 11.2 | 22.2 | 334000 | 3.52 | 196000 | 2.23 | R-32 | 24.8333
217902313 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN | TURYE1444AMM0AN |  |  | TURYE2884BMM0AN | Ducted Indoor Units | 276000 | 11.6 | 20.6 | 304000 | 3.51 | 180000 | 2.25 | R-32 | 23
217902314 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AMM0AN | TURYE1444AMM0AN |  |  | TURYE2884BMM0AN | Non-Ducted Indoor Units | 276000 | 11.9 | 22.4 | 304000 | 3.57 | 180000 | 2.3 | R-32 | 23
217902325 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN | TURYE1924AMM0AN |  |  | TURYE3604BMM0AN | Ducted Indoor Units | 344000 | 10.2 | 19.2 | 362000 | 3.33 | 220000 | 2.18 | R-32 | 28.6667
217902326 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN | TURYE1924AMM0AN |  |  | TURYE3604BMM0AN | Non-Ducted Indoor Units | 344000 | 10.2 | 22 | 362000 | 3.33 | 220000 | 2.15 | R-32 | 28.6667
217902321 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN | TURYE1684AMM0AN |  |  | TURYE3364BMM0AN | Ducted Indoor Units | 320000 | 10.8 | 19.6 | 360000 | 3.35 | 210000 | 2.21 | R-32 | 26.6667
217902322 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AMM0AN | TURYE1684AMM0AN |  |  | TURYE3364BMM0AN | Non-Ducted Indoor Units | 320000 | 10.6 | 21.9 | 360000 | 3.33 | 210000 | 2.18 | R-32 | 26.6667
217902329 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AMM0AN | TURYE1924AMM0AN |  |  | TURYE3844BMM0AN | Ducted Indoor Units | 368000 | 9.7 | 18.9 | 368000 | 3.29 | 258000 | 2.15 | R-32 | 30.6667
217902330 | N/A | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1924AMM0AN | TURYE1924AMM0AN |  |  | TURYE3844BMM0AN | Non-Ducted Indoor Units | 368000 | 9.9 | 20.9 | 368000 | 3.31 | 258000 | 2.11 | R-32 | 30.6667
217902131 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120TXU-A | PUHY-EM144TXU-A |  |  | PUHY-EM264TSXU-A | Ducted Indoor Units | 250000 | 12.2 | 22.2 | 280000 | 3.61 | 172000 | 2.33 | R-32 | 20.8333
217902132 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120TXU-A | PUHY-EM144TXU-A |  |  | PUHY-EM264TSXU-A | Non-Ducted Indoor Units | 250000 | 12.7 | 24.5 | 280000 | 3.81 | 172000 | 2.4 | R-32 | 20.8333
217902135 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A | PUHY-EM144TXU-A |  |  | PUHY-EM288TSXU-A | Ducted Indoor Units | 276000 | 12 | 21.2 | 304000 | 3.52 | 180000 | 2.3 | R-32 | 23
217902136 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A | PUHY-EM144TXU-A |  |  | PUHY-EM288TSXU-A | Non-Ducted Indoor Units | 276000 | 12.4 | 23.2 | 304000 | 3.71 | 180000 | 2.33 | R-32 | 23
217902139 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A | PUHY-EM168TXU-A |  |  | PUHY-EM312TSXU-A | Ducted Indoor Units | 298000 | 11.4 | 20.7 | 334000 | 3.42 | 196000 | 2.25 | R-32 | 24.8333
217902140 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144TXU-A | PUHY-EM168TXU-A |  |  | PUHY-EM312TSXU-A | Non-Ducted Indoor Units | 298000 | 11.7 | 22.6 | 334000 | 3.64 | 196000 | 2.31 | R-32 | 24.8333
217902143 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A | PUHY-EM168TXU-A |  |  | PUHY-EM336TSXU-A | Ducted Indoor Units | 320000 | 10.9 | 20.2 | 360000 | 3.34 | 210000 | 2.2 | R-32 | 26.6667
217902144 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A | PUHY-EM168TXU-A |  |  | PUHY-EM336TSXU-A | Non-Ducted Indoor Units | 320000 | 11.1 | 22.5 | 360000 | 3.44 | 210000 | 2.19 | R-32 | 26.6667
217902147 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A | PUHY-EM192TXU-A |  |  | PUHY-EM360TSXU-A | Ducted Indoor Units | 344000 | 10.7 | 19.9 | 362000 | 3.34 | 220000 | 2.18 | R-32 | 28.6667
217902148 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168TXU-A | PUHY-EM192TXU-A |  |  | PUHY-EM360TSXU-A | Non-Ducted Indoor Units | 344000 | 10.7 | 21.8 | 362000 | 3.51 | 220000 | 2.17 | R-32 | 28.6667
217902151 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192TXU-A | PUHY-EM192TXU-A |  |  | PUHY-EM384TSXU-A | Ducted Indoor Units | 368000 | 10.4 | 19.7 | 368000 | 3.4 | 258000 | 2.2 | R-32 | 30.6667
217902152 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192TXU-A | PUHY-EM192TXU-A |  |  | PUHY-EM384TSXU-A | Non-Ducted Indoor Units | 368000 | 10.3 | 21.2 | 368000 | 3.49 | 258000 | 2.18 | R-32 | 30.6667
217902133 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120YXU-A | PUHY-EM144YXU-A |  |  | PUHY-EM264YSXU-A | Ducted Indoor Units | 250000 | 12.2 | 22.2 | 280000 | 3.61 | 172000 | 2.33 | R-32 | 20.8333
217902134 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM120YXU-A | PUHY-EM144YXU-A |  |  | PUHY-EM264YSXU-A | Non-Ducted Indoor Units | 250000 | 12.7 | 24.5 | 280000 | 3.81 | 172000 | 2.4 | R-32 | 20.8333
217902141 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A | PUHY-EM168YXU-A |  |  | PUHY-EM312YSXU-A | Ducted Indoor Units | 298000 | 11.4 | 20.7 | 334000 | 3.42 | 196000 | 2.25 | R-32 | 24.8333
217902142 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A | PUHY-EM168YXU-A |  |  | PUHY-EM312YSXU-A | Non-Ducted Indoor Units | 298000 | 11.7 | 22.6 | 334000 | 3.64 | 196000 | 2.31 | R-32 | 24.8333
217902137 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A | PUHY-EM144YXU-A |  |  | PUHY-EM288YSXU-A | Ducted Indoor Units | 276000 | 12 | 21.2 | 304000 | 3.52 | 180000 | 2.3 | R-32 | 23
217902138 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM144YXU-A | PUHY-EM144YXU-A |  |  | PUHY-EM288YSXU-A | Non-Ducted Indoor Units | 276000 | 12.4 | 23.2 | 304000 | 3.71 | 180000 | 2.33 | R-32 | 23
217902149 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A | PUHY-EM192YXU-A |  |  | PUHY-EM360YSXU-A | Ducted Indoor Units | 344000 | 10.7 | 19.9 | 362000 | 3.34 | 220000 | 2.18 | R-32 | 28.6667
217902150 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A | PUHY-EM192YXU-A |  |  | PUHY-EM360YSXU-A | Non-Ducted Indoor Units | 344000 | 10.7 | 21.8 | 362000 | 3.51 | 220000 | 2.17 | R-32 | 28.6667
217902145 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A | PUHY-EM168YXU-A |  |  | PUHY-EM336YSXU-A | Ducted Indoor Units | 320000 | 10.9 | 20.2 | 360000 | 3.34 | 210000 | 2.2 | R-32 | 26.6667
217902146 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM168YXU-A | PUHY-EM168YXU-A |  |  | PUHY-EM336YSXU-A | Non-Ducted Indoor Units | 320000 | 11.1 | 22.5 | 360000 | 3.44 | 210000 | 2.19 | R-32 | 26.6667
217902153 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192YXU-A | PUHY-EM192YXU-A |  |  | PUHY-EM384YSXU-A | Ducted Indoor Units | 368000 | 10.4 | 19.7 | 368000 | 3.4 | 258000 | 2.2 | R-32 | 30.6667
217902154 | N/A | Mitsubishi Electric | HMSV-A-CB | PUHY-EM192YXU-A | PUHY-EM192YXU-A |  |  | PUHY-EM384YSXU-A | Non-Ducted Indoor Units | 368000 | 10.3 | 21.2 | 368000 | 3.49 | 258000 | 2.18 | R-32 | 30.6667
217902235 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AMM0AN | TUHYE1443AMM0AN |  |  | TUHYE2643BMM0AN | Ducted Indoor Units | 252000 | 12.2 | 22.2 | 280000 | 3.61 | 172000 | 2.33 | R-32 | 21
217902236 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AMM0AN | TUHYE1443AMM0AN |  |  | TUHYE2643BMM0AN | Non-Ducted Indoor Units | 252000 | 12.7 | 24.5 | 280000 | 3.81 | 172000 | 2.4 | R-32 | 21
217902239 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN | TUHYE1443AMM0AN |  |  | TUHYE2883BMM0AN | Ducted Indoor Units | 276000 | 12 | 21.2 | 304000 | 3.52 | 180000 | 2.3 | R-32 | 23
217902240 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN | TUHYE1443AMM0AN |  |  | TUHYE2883BMM0AN | Non-Ducted Indoor Units | 276000 | 12.4 | 23.2 | 304000 | 3.71 | 180000 | 2.33 | R-32 | 23
217902243 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN | TUHYE1683AMM0AN |  |  | TUHYE3123BMM0AN | Ducted Indoor Units | 298000 | 11.4 | 20.7 | 334000 | 3.42 | 196000 | 2.25 | R-32 | 24.8333
217902244 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AMM0AN | TUHYE1683AMM0AN |  |  | TUHYE3123BMM0AN | Non-Ducted Indoor Units | 298000 | 11.7 | 22.6 | 334000 | 3.64 | 196000 | 2.31 | R-32 | 24.8333
217902247 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN | TUHYE1683AMM0AN |  |  | TUHYE3363BMM0AN | Ducted Indoor Units | 320000 | 10.9 | 20.2 | 360000 | 3.34 | 210000 | 2.2 | R-32 | 26.6667
217902248 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN | TUHYE1683AMM0AN |  |  | TUHYE3363BMM0AN | Non-Ducted Indoor Units | 320000 | 11.1 | 22.5 | 360000 | 3.44 | 210000 | 2.19 | R-32 | 26.6667
217902251 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN | TUHYE1923AMM0AN |  |  | TUHYE3603BMM0AN | Ducted Indoor Units | 344000 | 10.7 | 19.9 | 362000 | 3.34 | 220000 | 2.18 | R-32 | 28.6667
217902252 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1683AMM0AN | TUHYE1923AMM0AN |  |  | TUHYE3603BMM0AN | Non-Ducted Indoor Units | 344000 | 10.7 | 21.8 | 362000 | 3.51 | 220000 | 2.17 | R-32 | 28.6667
217902255 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AMM0AN | TUHYE1923AMM0AN |  |  | TUHYE3843BMM0AN | Ducted Indoor Units | 368000 | 10.4 | 19.7 | 368000 | 3.4 | 258000 | 2.2 | R-32 | 30.6667
217902256 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AMM0AN | TUHYE1923AMM0AN |  |  | TUHYE3843BMM0AN | Non-Ducted Indoor Units | 368000 | 10.3 | 21.2 | 368000 | 3.49 | 258000 | 2.18 | R-32 | 30.6667
217902237 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AMM0AN | TUHYE1444AMM0AN |  |  | TUHYE2644BMM0AN | Ducted Indoor Units | 252000 | 12.2 | 22.2 | 280000 | 3.61 | 172000 | 2.33 | R-32 | 21
217902238 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AMM0AN | TUHYE1444AMM0AN |  |  | TUHYE2644BMM0AN | Non-Ducted Indoor Units | 252000 | 12.7 | 24.5 | 280000 | 3.81 | 172000 | 2.4 | R-32 | 21
217902245 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN | TUHYE1684AMM0AN |  |  | TUHYE3124BMM0AN | Ducted Indoor Units | 298000 | 11.4 | 20.7 | 334000 | 3.42 | 196000 | 2.25 | R-32 | 24.8333
217902246 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN | TUHYE1684AMM0AN |  |  | TUHYE3124BMM0AN | Non-Ducted Indoor Units | 298000 | 11.7 | 22.6 | 334000 | 3.64 | 196000 | 2.31 | R-32 | 24.8333
217902241 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN | TUHYE1444AMM0AN |  |  | TUHYE2884BMM0AN | Ducted Indoor Units | 276000 | 12 | 21.2 | 304000 | 3.52 | 180000 | 2.3 | R-32 | 23
217902242 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AMM0AN | TUHYE1444AMM0AN |  |  | TUHYE2884BMM0AN | Non-Ducted Indoor Units | 276000 | 12.4 | 23.2 | 304000 | 3.71 | 180000 | 2.33 | R-32 | 23
217902253 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN | TUHYE1924AMM0AN |  |  | TUHYE3604BMM0AN | Ducted Indoor Units | 344000 | 10.7 | 19.9 | 362000 | 3.34 | 220000 | 2.18 | R-32 | 28.6667
217902254 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN | TUHYE1924AMM0AN |  |  | TUHYE3604BMM0AN | Non-Ducted Indoor Units | 344000 | 10.7 | 21.8 | 362000 | 3.51 | 220000 | 2.17 | R-32 | 28.6667
217902249 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN | TUHYE1684AMM0AN |  |  | TUHYE3364BMM0AN | Ducted Indoor Units | 320000 | 10.9 | 20.2 | 360000 | 3.34 | 210000 | 2.2 | R-32 | 26.6667
217902250 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1684AMM0AN | TUHYE1684AMM0AN |  |  | TUHYE3364BMM0AN | Non-Ducted Indoor Units | 320000 | 11.1 | 22.5 | 360000 | 3.44 | 210000 | 2.19 | R-32 | 26.6667
217902257 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AMM0AN | TUHYE1924AMM0AN |  |  | TUHYE3844BMM0AN | Ducted Indoor Units | 368000 | 10.4 | 19.7 | 368000 | 3.4 | 258000 | 2.2 | R-32 | 30.6667
217902258 | N/A | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AMM0AN | TUHYE1924AMM0AN |  |  | TUHYE3844BMM0AN | Non-Ducted Indoor Units | 368000 | 10.3 | 21.2 | 368000 | 3.49 | 258000 | 2.18 | R-32 | 30.6667
218043891 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD168S6M-5Y |  |  | VPD264S6M-5Y | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218043895 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD192S6M-5Y |  |  | VPD288S6M-5Y | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218043899 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD216S6M-5Y |  |  | VPD312S6M-5Y | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218043903 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD240S6M-5Y |  |  | VPD336S6M-5Y | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218043955 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD168S6M-5Y |  |  | VPD264S6M-5Y | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218043959 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD192S6M-5Y |  |  | VPD288S6M-5Y | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218043963 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD216S6M-5Y |  |  | VPD312S6M-5Y | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218043967 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD240S6M-5Y |  |  | VPD336S6M-5Y | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218044027 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD168S6M-5Y |  |  | VPD264S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218044031 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD192S6M-5Y |  |  | VPD288S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218044035 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD216S6M-5Y |  |  | VPD312S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218044039 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5Y | VPD240S6M-5Y |  |  | VPD336S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218004919 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM168HCVGFG |  |  | AM264HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218004923 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM192HCVGFG |  |  | AM288HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218004927 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM216HCVGFG |  |  | AM312HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218004931 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM240HCVGFG |  |  | AM336HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218003148 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM216HCVGFG |  |  | AM312HCVGFG | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218003152 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM240HCVGFG |  |  | AM336HCVGFG | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218003140 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM168HCVGFG |  |  | AM264HCVGFG | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218003144 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM192HCVGFG |  |  | AM288HCVGFG | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218003080 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM192HCVGFG |  |  | AM288HCVGFG | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218003084 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM216HCVGFG |  |  | AM312HCVGFG | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218003088 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM240HCVGFG |  |  | AM336HCVGFG | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218003076 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGFG | AM168HCVGFG |  |  | AM264HCVGFG | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218003092 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGFG | AM240HCVGFG |  |  | AM360HCVGFG | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218003172 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGFG | AM144HCVGFG | AM192HCVGFG |  | AM456HCVGFG | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218004935 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGFG | AM240HCVGFG |  |  | AM360HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218044043 | N/A | LENNOX | HMSV-A-CB | VPD120S6M-5Y | VPD240S6M-5Y |  |  | VPD360S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218043987 | N/A | LENNOX | HMSV-A-CB | VPD120S6M-5Y | VPD144S6M-5Y | VPD192S6M-5Y |  | VPD456S6M-5Y | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218043907 | N/A | LENNOX | HMSV-A-CB | VPD120S6M-5Y | VPD240S6M-5Y |  |  | VPD360S6M-5Y | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218043919 | N/A | LENNOX | HMSV-A-CB | VPD120S6M-5Y | VPD120S6M-5Y | VPD192S6M-5Y |  | VPD432S6M-5Y | Ducted Indoor Units | 412000 | 9.15 | 17.84 | 462000 | 3.25 | 300000 | 2.35 | R-32 | 34.3333
218043911 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5Y | VPD192S6M-5Y |  |  | VPD384S6M-5Y | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218043915 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5Y | VPD216S6M-5Y |  |  | VPD408S6M-5Y | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218043975 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5Y | VPD192S6M-5Y |  |  | VPD384S6M-5Y | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218043979 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5Y | VPD216S6M-5Y |  |  | VPD408S6M-5Y | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218044047 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5Y | VPD192S6M-5Y |  |  | VPD384S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218044051 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5Y | VPD216S6M-5Y |  |  | VPD408S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218004939 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM192HCVGFG |  |  | AM384HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218004943 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM216HCVGFG |  |  | AM408HCVGFG | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218003164 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM216HCVGFG |  |  | AM408HCVGFG | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218003160 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM192HCVGFG |  |  | AM384HCVGFG | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218003096 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM192HCVGFG |  |  | AM384HCVGFG | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218003100 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGFG | AM216HCVGFG |  |  | AM408HCVGFG | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218043904 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD240S6M-5Y |  |  | VRD336S6M-5Y | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218043900 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD216S6M-5Y |  |  | VRD312S6M-5Y | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218043896 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD192S6M-5Y |  |  | VRD288S6M-5Y | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218043892 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD168S6M-5Y |  |  | VRD264S6M-5Y | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218043968 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD240S6M-5Y |  |  | VRD336S6M-5Y | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218043964 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD216S6M-5Y |  |  | VRD312S6M-5Y | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218043960 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD192S6M-5Y |  |  | VRD288S6M-5Y | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218043956 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD168S6M-5Y |  |  | VRD264S6M-5Y | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218044028 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD168S6M-5Y |  |  | VRD264S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218044040 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD240S6M-5Y |  |  | VRD336S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218044036 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD216S6M-5Y |  |  | VRD312S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218044032 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5Y | VRD192S6M-5Y |  |  | VRD288S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218004932 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM240HCVGFS |  |  | AM336HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218004928 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM216HCVGFS |  |  | AM312HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218004924 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM192HCVGFS |  |  | AM288HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218004920 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM168HCVGFS |  |  | AM264HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218003153 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM240HCVGFS |  |  | AM336HCVGFS | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218003149 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM216HCVGFS |  |  | AM312HCVGFS | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218003145 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM192HCVGFS |  |  | AM288HCVGFS | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218003141 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM168HCVGFS |  |  | AM264HCVGFS | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218003089 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM240HCVGFS |  |  | AM336HCVGFS | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218003085 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM216HCVGFS |  |  | AM312HCVGFS | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218003081 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM192HCVGFS |  |  | AM288HCVGFS | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218003077 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGFS | AM168HCVGFS |  |  | AM264HCVGFS | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218003093 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGFS | AM240HCVGFS |  |  | AM360HCVGFS | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218003173 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGFS | AM144HCVGFS | AM192HCVGFS |  | AM456HCVGFS | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218004936 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGFS | AM240HCVGFS |  |  | AM360HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218044044 | N/A | LENNOX | HMSR-A-CB | VRD120S6M-5Y | VRD240S6M-5Y |  |  | VRD360S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218043988 | N/A | LENNOX | HMSR-A-CB | VRD120S6M-5Y | VRD144S6M-5Y | VRD192S6M-5Y |  | VRD456S6M-5Y | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218043908 | N/A | LENNOX | HMSR-A-CB | VRD120S6M-5Y | VRD240S6M-5Y |  |  | VRD360S6M-5Y | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218043920 | N/A | LENNOX | HMSR-A-CB | VRD120S6M-5Y | VRD120S6M-5Y | VRD192S6M-5Y |  | VRD432S6M-5Y | Ducted Indoor Units | 412000 | 9.15 | 17.84 | 462000 | 3.25 | 300000 | 2.35 | R-32 | 34.3333
218043916 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5Y | VRD216S6M-5Y |  |  | VRD408S6M-5Y | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218043912 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5Y | VRD192S6M-5Y |  |  | VRD384S6M-5Y | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218043980 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5Y | VRD216S6M-5Y |  |  | VRD408S6M-5Y | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218043976 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5Y | VRD192S6M-5Y |  |  | VRD384S6M-5Y | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218044052 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5Y | VRD216S6M-5Y |  |  | VRD408S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218044048 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5Y | VRD192S6M-5Y |  |  | VRD384S6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218004944 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM216HCVGFS |  |  | AM408HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218004940 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM192HCVGFS |  |  | AM384HCVGFS | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218003165 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM216HCVGFS |  |  | AM408HCVGFS | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218003161 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM192HCVGFS |  |  | AM384HCVGFS | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218003101 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM216HCVGFS |  |  | AM408HCVGFS | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218003097 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGFS | AM192HCVGFS |  |  | AM384HCVGFS | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218043905 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD240S6M-5G |  |  | VPD336S6M-5G | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218043893 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD168S6M-5G |  |  | VPD264S6M-5G | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218043897 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD192S6M-5G |  |  | VPD288S6M-5G | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218043901 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD216S6M-5G |  |  | VPD312S6M-5G | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218043969 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD240S6M-5G |  |  | VPD336S6M-5G | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218043957 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD168S6M-5G |  |  | VPD264S6M-5G | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218043961 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD192S6M-5G |  |  | VPD288S6M-5G | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218043965 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD216S6M-5G |  |  | VPD312S6M-5G | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218044029 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD168S6M-5G |  |  | VPD264S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218044041 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD240S6M-5G |  |  | VPD336S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218044033 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD192S6M-5G |  |  | VPD288S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218044037 | N/A | LENNOX | HMSV-A-CB | VPD096S6M-5G | VPD216S6M-5G |  |  | VPD312S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218004933 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM240HCVGJG |  |  | AM336HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218004925 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM192HCVGJG |  |  | AM288HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218004929 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM216HCVGJG |  |  | AM312HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218004921 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM168HCVGJG |  |  | AM264HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218003150 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM216HCVGJG |  |  | AM312HCVGJG | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218003154 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM240HCVGJG |  |  | AM336HCVGJG | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218003142 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM168HCVGJG |  |  | AM264HCVGJG | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218003146 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM192HCVGJG |  |  | AM288HCVGJG | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218003090 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM240HCVGJG |  |  | AM336HCVGJG | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218003082 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM192HCVGJG |  |  | AM288HCVGJG | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218003086 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM216HCVGJG |  |  | AM312HCVGJG | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218003078 | N/A | SAMSUNG | HMSV-A-CB | AM096HCVGJG | AM168HCVGJG |  |  | AM264HCVGJG | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218003094 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGJG | AM240HCVGJG |  |  | AM360HCVGJG | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218003174 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGJG | AM144HCVGJG | AM192HCVGJG |  | AM456HCVGJG | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218004937 | N/A | SAMSUNG | HMSV-A-CB | AM120HCVGJG | AM240HCVGJG |  |  | AM360HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218044045 | N/A | LENNOX | HMSV-A-CB | VPD120S6M-5G | VPD240S6M-5G |  |  | VPD360S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218043989 | N/A | LENNOX | HMSV-A-CB | VPD120S6M-5G | VPD144S6M-5G | VPD192S6M-5G |  | VPD456S6M-5G | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218043909 | N/A | LENNOX | HMSV-A-CB | VPD120S6M-5G | VPD240S6M-5G |  |  | VPD360S6M-5G | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218043921 | N/A | LENNOX | HMSV-A-CB | VPD120S6M-5G | VPD120S6M-5G | VPD192S6M-5G |  | VPD432S6M-5G | Ducted Indoor Units | 412000 | 9.15 | 17.84 | 462000 | 3.25 | 300000 | 2.35 | R-32 | 34.3333
218043913 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5G | VPD192S6M-5G |  |  | VPD384S6M-5G | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218043917 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5G | VPD216S6M-5G |  |  | VPD408S6M-5G | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218043977 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5G | VPD192S6M-5G |  |  | VPD384S6M-5G | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218043981 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5G | VPD216S6M-5G |  |  | VPD408S6M-5G | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218044049 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5G | VPD192S6M-5G |  |  | VPD384S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218044053 | N/A | LENNOX | HMSV-A-CB | VPD192S6M-5G | VPD216S6M-5G |  |  | VPD408S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218004941 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM192HCVGJG |  |  | AM384HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218004945 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM216HCVGJG |  |  | AM408HCVGJG | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218003166 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM216HCVGJG |  |  | AM408HCVGJG | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218003162 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM192HCVGJG |  |  | AM384HCVGJG | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218003098 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM192HCVGJG |  |  | AM384HCVGJG | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218003102 | N/A | SAMSUNG | HMSV-A-CB | AM192HCVGJG | AM216HCVGJG |  |  | AM408HCVGJG | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218043906 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD240S6M-5G |  |  | VRD336S6M-5G | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218043902 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD216S6M-5G |  |  | VRD312S6M-5G | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218043898 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD192S6M-5G |  |  | VRD288S6M-5G | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218043894 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD168S6M-5G |  |  | VRD264S6M-5G | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218043970 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD240S6M-5G |  |  | VRD336S6M-5G | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218043966 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD216S6M-5G |  |  | VRD312S6M-5G | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218043962 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD192S6M-5G |  |  | VRD288S6M-5G | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218043958 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD168S6M-5G |  |  | VRD264S6M-5G | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218044030 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD168S6M-5G |  |  | VRD264S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218044042 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD240S6M-5G |  |  | VRD336S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218044038 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD216S6M-5G |  |  | VRD312S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218044034 | N/A | LENNOX | HMSR-A-CB | VRD096S6M-5G | VRD192S6M-5G |  |  | VRD288S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218004934 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM240HCVGJS |  |  | AM336HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.92 | 20.73 | 360000 | 3.37 | 234000 | 2.38 | R-32 | 26.6667
218004930 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM216HCVGJS |  |  | AM312HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.1 | 20.38 | 334000 | 3.4 | 218000 | 2.34 | R-32 | 24.8333
218004926 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM192HCVGJS |  |  | AM288HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 21.37 | 308000 | 3.44 | 200000 | 2.33 | R-32 | 22.8333
218004922 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM168HCVGJS |  |  | AM264HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20.47 | 282000 | 3.55 | 184000 | 2.42 | R-32 | 21
218003155 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM240HCVGJS |  |  | AM336HCVGJS | Non-Ducted Indoor Units | 320000 | 9.65 | 22.05 | 360000 | 3.3 | 234000 | 2.46 | R-32 | 26.6667
218003151 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM216HCVGJS |  |  | AM312HCVGJS | Non-Ducted Indoor Units | 298000 | 9.75 | 21.15 | 334000 | 3.31 | 218000 | 2.32 | R-32 | 24.8333
218003147 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM192HCVGJS |  |  | AM288HCVGJS | Non-Ducted Indoor Units | 274000 | 10.25 | 22.7 | 308000 | 3.33 | 200000 | 2.26 | R-32 | 22.8333
218003143 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM168HCVGJS |  |  | AM264HCVGJS | Non-Ducted Indoor Units | 252000 | 10.55 | 21.76 | 282000 | 3.49 | 184000 | 2.44 | R-32 | 21
218003091 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM240HCVGJS |  |  | AM336HCVGJS | Ducted Indoor Units | 320000 | 10.2 | 19.42 | 360000 | 3.45 | 234000 | 2.31 | R-32 | 26.6667
218003087 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM216HCVGJS |  |  | AM312HCVGJS | Ducted Indoor Units | 298000 | 10.45 | 19.62 | 334000 | 3.5 | 218000 | 2.36 | R-32 | 24.8333
218003083 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM192HCVGJS |  |  | AM288HCVGJS | Ducted Indoor Units | 274000 | 10.75 | 20.04 | 308000 | 3.55 | 200000 | 2.41 | R-32 | 22.8333
218003079 | N/A | SAMSUNG | HMSR-A-CB | AM096HCVGJS | AM168HCVGJS |  |  | AM264HCVGJS | Ducted Indoor Units | 252000 | 10.85 | 19.18 | 282000 | 3.61 | 184000 | 2.41 | R-32 | 21
218003095 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGJS | AM240HCVGJS |  |  | AM360HCVGJS | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218003175 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGJS | AM144HCVGJS | AM192HCVGJS |  | AM456HCVGJS | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218004938 | N/A | SAMSUNG | HMSR-A-CB | AM120HCVGJS | AM240HCVGJS |  |  | AM360HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218044046 | N/A | LENNOX | HMSR-A-CB | VRD120S6M-5G | VRD240S6M-5G |  |  | VRD360S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.55 | 20.39 | 386000 | 3.32 | 250000 | 2.31 | R-32 | 28.5
218043990 | N/A | LENNOX | HMSR-A-CB | VRD120S6M-5G | VRD144S6M-5G | VRD192S6M-5G |  | VRD456S6M-5G | Non-Ducted Indoor Units | 436000 | 9.1 | 18.02 | 488000 | 3.29 | 320000 | 2.1 | R-32 | 36.3333
218043910 | N/A | LENNOX | HMSR-A-CB | VRD120S6M-5G | VRD240S6M-5G |  |  | VRD360S6M-5G | Ducted Indoor Units | 342000 | 9.65 | 18.93 | 386000 | 3.4 | 250000 | 2.3 | R-32 | 28.5
218043922 | N/A | LENNOX | HMSR-A-CB | VRD120S6M-5G | VRD120S6M-5G | VRD192S6M-5G |  | VRD432S6M-5G | Ducted Indoor Units | 412000 | 9.15 | 17.84 | 462000 | 3.25 | 300000 | 2.35 | R-32 | 34.3333
218043918 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5G | VRD216S6M-5G |  |  | VRD408S6M-5G | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218043914 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5G | VRD192S6M-5G |  |  | VRD384S6M-5G | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218043982 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5G | VRD216S6M-5G |  |  | VRD408S6M-5G | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218043978 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5G | VRD192S6M-5G |  |  | VRD384S6M-5G | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218044054 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5G | VRD216S6M-5G |  |  | VRD408S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218044050 | N/A | LENNOX | HMSR-A-CB | VRD192S6M-5G | VRD192S6M-5G |  |  | VRD384S6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218004946 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM216HCVGJS |  |  | AM408HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.35 | 18.36 | 438000 | 3.27 | 284000 | 2.25 | R-32 | 32.3333
218004942 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM192HCVGJS |  |  | AM384HCVGJS | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 18.57 | 412000 | 3.3 | 268000 | 2.27 | R-32 | 30.5
218003167 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM216HCVGJS |  |  | AM408HCVGJS | Non-Ducted Indoor Units | 388000 | 9.5 | 19.26 | 438000 | 3.25 | 284000 | 2.15 | R-32 | 32.3333
218003163 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM192HCVGJS |  |  | AM384HCVGJS | Non-Ducted Indoor Units | 366000 | 9.6 | 19.47 | 412000 | 3.3 | 268000 | 2.2 | R-32 | 30.5
218003103 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM216HCVGJS |  |  | AM408HCVGJS | Ducted Indoor Units | 388000 | 9.2 | 17.46 | 438000 | 3.3 | 284000 | 2.35 | R-32 | 32.3333
218003099 | N/A | SAMSUNG | HMSR-A-CB | AM192HCVGJS | AM192HCVGJS |  |  | AM384HCVGJS | Ducted Indoor Units | 366000 | 9.6 | 17.68 | 412000 | 3.3 | 268000 | 2.35 | R-32 | 30.5
218005691 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG | AM120HCVTFG |  | AM264HCVTFG | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218005695 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG | AM120HCVTFG |  | AM288HCVTFG | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218005731 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG | AM120HCVTFG |  | AM264HCVTFG | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218005735 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG | AM120HCVTFG |  | AM288HCVTFG | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218005767 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM096HCVTFG | AM120HCVTFG |  | AM288HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218005763 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTFG | AM072HCVTFG | AM120HCVTFG |  | AM264HCVTFG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218044087 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD120L6M-5Y |  | VPD264L6M-5Y | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218044091 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD096L6M-5Y | VPD120L6M-5Y |  | VPD288L6M-5Y | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218044127 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD120L6M-5Y |  | VPD264L6M-5Y | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218044131 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD096L6M-5Y | VPD120L6M-5Y |  | VPD288L6M-5Y | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218044159 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD072L6M-5Y | VPD120L6M-5Y |  | VPD264L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218044163 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5Y | VPD096L6M-5Y | VPD120L6M-5Y |  | VPD288L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218044164 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD096L6M-5Y | VRD120L6M-5Y |  | VRD288L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218044160 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD120L6M-5Y |  | VRD264L6M-5Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218044092 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD096L6M-5Y | VRD120L6M-5Y |  | VRD288L6M-5Y | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218044088 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD120L6M-5Y |  | VRD264L6M-5Y | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218044132 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD096L6M-5Y | VRD120L6M-5Y |  | VRD288L6M-5Y | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218044128 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5Y | VRD072L6M-5Y | VRD120L6M-5Y |  | VRD264L6M-5Y | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218005732 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS | AM120HCVTFS |  | AM264HCVTFS | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218005736 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS | AM120HCVTFS |  | AM288HCVTFS | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218005696 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS | AM120HCVTFS |  | AM288HCVTFS | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218005692 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS | AM120HCVTFS |  | AM264HCVTFS | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218005764 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM072HCVTFS | AM120HCVTFS |  | AM264HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218005768 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTFS | AM096HCVTFS | AM120HCVTFS |  | AM288HCVTFS | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218005693 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG | AM120HCVTJG |  | AM264HCVTJG | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218005697 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG | AM120HCVTJG |  | AM288HCVTJG | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218005733 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG | AM120HCVTJG |  | AM264HCVTJG | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218005737 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG | AM120HCVTJG |  | AM288HCVTJG | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218005769 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM096HCVTJG | AM120HCVTJG |  | AM288HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218005765 | N/A | SAMSUNG | HMSV-A-CB | AM072HCVTJG | AM072HCVTJG | AM120HCVTJG |  | AM264HCVTJG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218044089 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD120L6M-5G |  | VPD264L6M-5G | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218044093 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD096L6M-5G | VPD120L6M-5G |  | VPD288L6M-5G | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218044129 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD120L6M-5G |  | VPD264L6M-5G | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218044133 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD096L6M-5G | VPD120L6M-5G |  | VPD288L6M-5G | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218044161 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD072L6M-5G | VPD120L6M-5G |  | VPD264L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218044165 | N/A | LENNOX | HMSV-A-CB | VPD072L6M-5G | VPD096L6M-5G | VPD120L6M-5G |  | VPD288L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218044166 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD096L6M-5G | VRD120L6M-5G |  | VRD288L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218044162 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD120L6M-5G |  | VRD264L6M-5G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218044094 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD096L6M-5G | VRD120L6M-5G |  | VRD288L6M-5G | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218044090 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD120L6M-5G |  | VRD264L6M-5G | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218044134 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD096L6M-5G | VRD120L6M-5G |  | VRD288L6M-5G | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218044130 | N/A | LENNOX | HMSR-A-CB | VRD072L6M-5G | VRD072L6M-5G | VRD120L6M-5G |  | VRD264L6M-5G | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218005734 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS | AM120HCVTJS |  | AM264HCVTJS | Non-Ducted Indoor Units | 252000 | 11 | 24.41 | 282000 | 3.36 | 282000 | 2.12 | R-32 | 21
218005738 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS | AM120HCVTJS |  | AM288HCVTJS | Non-Ducted Indoor Units | 274000 | 10.9 | 24.03 | 308000 | 3.28 | 308000 | 2.1 | R-32 | 22.8333
218005698 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS | AM120HCVTJS |  | AM288HCVTJS | Ducted Indoor Units | 274000 | 11 | 21.58 | 308000 | 3.62 | 308000 | 2.19 | R-32 | 22.8333
218005694 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS | AM120HCVTJS |  | AM264HCVTJS | Ducted Indoor Units | 252000 | 11 | 22.25 | 282000 | 3.77 | 282000 | 2.25 | R-32 | 21
218005766 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM072HCVTJS | AM120HCVTJS |  | AM264HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 23.33 | 282000 | 3.56 | 282000 | 2.18 | R-32 | 21
218005770 | N/A | SAMSUNG | HMSR-A-CB | AM072HCVTJS | AM096HCVTJS | AM120HCVTJS |  | AM288HCVTJS | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.95 | 22.8 | 308000 | 3.45 | 308000 | 2.14 | R-32 | 22.8333
218036909 | N/A | DAIKIN | HMSV-A-CB | RXYA120AATJ* | RXYA144AATJ* |  |  | RXYA264AATJ* | Non-Ducted Indoor Units | 252000 | 11 | 21.6 | 252000 | 3.4 | 168000 | 2.2 | R-32 | 21
218036981 | N/A | DAIKIN | HMSV-A-CB | RXYA120AATJ* | RXYA144AATJ* |  |  | RXYA264AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.6 | 19.95 | 252000 | 3.3 | 168000 | 2.2 | R-32 | 21
218036982 | N/A | DAIKIN | HMSV-A-CB | RXYA144AATJ* | RXYA144AATJ* |  |  | RXYA288AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 19.6 | 274000 | 3.37 | 194000 | 2.15 | R-32 | 22.8333
218036983 | N/A | DAIKIN | HMSV-A-CB | RXYA144AATJ* | RXYA168AATJ* |  |  | RXYA312AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.2 | 19.15 | 296000 | 3.35 | 212000 | 2.15 | R-32 | 24.6667
218036946 | N/A | DAIKIN | HMSV-A-CB | RXYA144AATJ* | RXYA144AATJ* |  |  | RXYA288AATJ* | Ducted Indoor Units | 274000 | 10.4 | 18.2 | 274000 | 3.25 | 194000 | 2.1 | R-32 | 22.8333
218036910 | N/A | DAIKIN | HMSV-A-CB | RXYA144AATJ* | RXYA144AATJ* |  |  | RXYA288AATJ* | Non-Ducted Indoor Units | 274000 | 10.8 | 21 | 274000 | 3.5 | 194000 | 2.2 | R-32 | 22.8333
218036911 | N/A | DAIKIN | HMSV-A-CB | RXYA144AATJ* | RXYA168AATJ* |  |  | RXYA312AATJ* | Non-Ducted Indoor Units | 296000 | 10.3 | 20.6 | 296000 | 3.5 | 212000 | 2.2 | R-32 | 24.6667
218036912 | N/A | DAIKIN | HMSV-A-CB | RXYA168AATJ* | RXYA168AATJ* |  |  | RXYA336AATJ* | Non-Ducted Indoor Units | 316000 | 9.4 | 19 | 310000 | 3.5 | 222000 | 2.1 | R-32 | 26.3333
218036913 | N/A | DAIKIN | HMSV-A-CB | RXYA168AATJ* | RXYA192AATJ* |  |  | RXYA360AATJ* | Non-Ducted Indoor Units | 342000 | 10.4 | 19.8 | 342000 | 3.5 | 244000 | 2.1 | R-32 | 28.5
218036949 | N/A | DAIKIN | HMSV-A-CB | RXYA168AATJ* | RXYA192AATJ* |  |  | RXYA360AATJ* | Ducted Indoor Units | 342000 | 9.4 | 17.4 | 342000 | 3.25 | 244000 | 2.1 | R-32 | 28.5
218036984 | N/A | DAIKIN | HMSV-A-CB | RXYA168AATJ* | RXYA168AATJ* |  |  | RXYA336AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.4 | 18.15 | 310000 | 3.35 | 222000 | 2.1 | R-32 | 26.3333
218036985 | N/A | DAIKIN | HMSV-A-CB | RXYA168AATJ* | RXYA192AATJ* |  |  | RXYA360AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.9 | 18.6 | 342000 | 3.37 | 244000 | 2.1 | R-32 | 28.5
218036986 | N/A | DAIKIN | HMSV-A-CB | RXYA192AATJ* | RXYA192AATJ* |  |  | RXYA384AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 10.2 | 19.1 | 364000 | 3.35 | 264000 | 2.1 | R-32 | 30.3333
218036987 | N/A | DAIKIN | HMSV-A-CB | RXYA192AATJ* | RXYA216AATJ* |  |  | RXYA408AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.7 | 18.55 | 388000 | 3.35 | 288000 | 2.1 | R-32 | 32.3333
218036950 | N/A | DAIKIN | HMSV-A-CB | RXYA192AATJ* | RXYA192AATJ* |  |  | RXYA384AATJ* | Ducted Indoor Units | 364000 | 9.9 | 17.8 | 364000 | 3.25 | 264000 | 2.1 | R-32 | 30.3333
218036951 | N/A | DAIKIN | HMSV-A-CB | RXYA192AATJ* | RXYA216AATJ* |  |  | RXYA408AATJ* | Ducted Indoor Units | 388000 | 9.3 | 17.2 | 388000 | 3.25 | 288000 | 2.1 | R-32 | 32.3333
218036914 | N/A | DAIKIN | HMSV-A-CB | RXYA192AATJ* | RXYA192AATJ* |  |  | RXYA384AATJ* | Non-Ducted Indoor Units | 364000 | 10.5 | 20.4 | 364000 | 3.45 | 264000 | 2.1 | R-32 | 30.3333
218036915 | N/A | DAIKIN | HMSV-A-CB | RXYA192AATJ* | RXYA216AATJ* |  |  | RXYA408AATJ* | Non-Ducted Indoor Units | 388000 | 10.1 | 19.9 | 388000 | 3.45 | 288000 | 2.1 | R-32 | 32.3333
218036916 | N/A | DAIKIN | HMSV-A-CB | RXYA216AATJ* | RXYA216AATJ* |  |  | RXYA432AATJ* | Non-Ducted Indoor Units | 410000 | 9.6 | 19 | 404000 | 3.3 | 312000 | 2.1 | R-32 | 34.1667
218036917 | N/A | DAIKIN | HMSV-A-CB | RXYA216AATJ* | RXYA240AATJ* |  |  | RXYA456AATJ* | Non-Ducted Indoor Units | 424000 | 9.4 | 19 | 414000 | 3.3 | 314000 | 2.1 | R-32 | 35.3333
218036952 | N/A | DAIKIN | HMSV-A-CB | RXYA216AATJ* | RXYA216AATJ* |  |  | RXYA432AATJ* | Ducted Indoor Units | 410000 | 9.2 | 16.8 | 404000 | 3.25 | 312000 | 2.1 | R-32 | 34.1667
218036953 | N/A | DAIKIN | HMSV-A-CB | RXYA216AATJ* | RXYA240AATJ* |  |  | RXYA456AATJ* | Ducted Indoor Units | 424000 | 9.2 | 17 | 414000 | 3.25 | 314000 | 2.1 | R-32 | 35.3333
218036988 | N/A | DAIKIN | HMSV-A-CB | RXYA216AATJ* | RXYA216AATJ* |  |  | RXYA432AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 17.9 | 404000 | 3.27 | 312000 | 2.1 | R-32 | 34.1667
218036989 | N/A | DAIKIN | HMSV-A-CB | RXYA216AATJ* | RXYA240AATJ* |  |  | RXYA456AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 424000 | 9.3 | 18 | 414000 | 3.27 | 314000 | 2.1 | R-32 | 35.3333
218036918 | N/A | DAIKIN | HMSV-A-CB | RXYA240AATJ* | RXYA240AATJ* |  |  | RXYA480AATJ* | Non-Ducted Indoor Units | 436000 | 9.4 | 18.4 | 418000 | 3.25 | 320000 | 2.1 | R-32 | 36.3333
218036927 | N/A | DAIKIN | HMSV-A-CB | RXYA120AAYD* | RXYA144AAYD* |  |  | RXYA264AAYD* | Non-Ducted Indoor Units | 252000 | 11 | 21.6 | 252000 | 3.4 | 168000 | 2.2 | R-32 | 21
218036999 | N/A | DAIKIN | HMSV-A-CB | RXYA120AAYD* | RXYA144AAYD* |  |  | RXYA264AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.6 | 19.95 | 252000 | 3.3 | 168000 | 2.2 | R-32 | 21
218037000 | N/A | DAIKIN | HMSV-A-CB | RXYA144AAYD* | RXYA144AAYD* |  |  | RXYA288AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 19.6 | 274000 | 3.37 | 194000 | 2.15 | R-32 | 22.8333
218037001 | N/A | DAIKIN | HMSV-A-CB | RXYA144AAYD* | RXYA168AAYD* |  |  | RXYA312AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.2 | 19.15 | 296000 | 3.35 | 212000 | 2.15 | R-32 | 24.6667
218036964 | N/A | DAIKIN | HMSV-A-CB | RXYA144AAYD* | RXYA144AAYD* |  |  | RXYA288AAYD* | Ducted Indoor Units | 274000 | 10.4 | 18.2 | 274000 | 3.25 | 194000 | 2.1 | R-32 | 22.8333
218036928 | N/A | DAIKIN | HMSV-A-CB | RXYA144AAYD* | RXYA144AAYD* |  |  | RXYA288AAYD* | Non-Ducted Indoor Units | 274000 | 10.8 | 21 | 274000 | 3.5 | 194000 | 2.2 | R-32 | 22.8333
218036929 | N/A | DAIKIN | HMSV-A-CB | RXYA144AAYD* | RXYA168AAYD* |  |  | RXYA312AAYD* | Non-Ducted Indoor Units | 296000 | 10.3 | 20.6 | 296000 | 3.5 | 212000 | 2.2 | R-32 | 24.6667
218036930 | N/A | DAIKIN | HMSV-A-CB | RXYA168AAYD* | RXYA168AAYD* |  |  | RXYA336AAYD* | Non-Ducted Indoor Units | 316000 | 9.4 | 19 | 310000 | 3.5 | 222000 | 2.1 | R-32 | 26.3333
218036931 | N/A | DAIKIN | HMSV-A-CB | RXYA168AAYD* | RXYA192AAYD* |  |  | RXYA360AAYD* | Non-Ducted Indoor Units | 342000 | 10.4 | 19.8 | 342000 | 3.5 | 244000 | 2.1 | R-32 | 28.5
218036967 | N/A | DAIKIN | HMSV-A-CB | RXYA168AAYD* | RXYA192AAYD* |  |  | RXYA360AAYD* | Ducted Indoor Units | 342000 | 9.4 | 17.4 | 342000 | 3.25 | 244000 | 2.1 | R-32 | 28.5
218037002 | N/A | DAIKIN | HMSV-A-CB | RXYA168AAYD* | RXYA168AAYD* |  |  | RXYA336AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.4 | 18.15 | 310000 | 3.35 | 222000 | 2.1 | R-32 | 26.3333
218037003 | N/A | DAIKIN | HMSV-A-CB | RXYA168AAYD* | RXYA192AAYD* |  |  | RXYA360AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.9 | 18.6 | 342000 | 3.37 | 244000 | 2.1 | R-32 | 28.5
218037004 | N/A | DAIKIN | HMSV-A-CB | RXYA192AAYD* | RXYA192AAYD* |  |  | RXYA384AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 10.2 | 19.1 | 364000 | 3.35 | 264000 | 2.1 | R-32 | 30.3333
218037005 | N/A | DAIKIN | HMSV-A-CB | RXYA192AAYD* | RXYA216AAYD* |  |  | RXYA408AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.7 | 18.55 | 388000 | 3.35 | 288000 | 2.1 | R-32 | 32.3333
218036968 | N/A | DAIKIN | HMSV-A-CB | RXYA192AAYD* | RXYA192AAYD* |  |  | RXYA384AAYD* | Ducted Indoor Units | 364000 | 9.9 | 17.8 | 364000 | 3.25 | 264000 | 2.1 | R-32 | 30.3333
218036969 | N/A | DAIKIN | HMSV-A-CB | RXYA192AAYD* | RXYA216AAYD* |  |  | RXYA408AAYD* | Ducted Indoor Units | 388000 | 9.3 | 17.2 | 388000 | 3.25 | 288000 | 2.1 | R-32 | 32.3333
218036932 | N/A | DAIKIN | HMSV-A-CB | RXYA192AAYD* | RXYA192AAYD* |  |  | RXYA384AAYD* | Non-Ducted Indoor Units | 364000 | 10.5 | 20.4 | 364000 | 3.45 | 264000 | 2.1 | R-32 | 30.3333
218036933 | N/A | DAIKIN | HMSV-A-CB | RXYA192AAYD* | RXYA216AAYD* |  |  | RXYA408AAYD* | Non-Ducted Indoor Units | 388000 | 10.1 | 19.9 | 388000 | 3.45 | 288000 | 2.1 | R-32 | 32.3333
218036934 | N/A | DAIKIN | HMSV-A-CB | RXYA216AAYD* | RXYA216AAYD* |  |  | RXYA432AAYD* | Non-Ducted Indoor Units | 410000 | 9.6 | 19 | 404000 | 3.3 | 312000 | 2.1 | R-32 | 34.1667
218036935 | N/A | DAIKIN | HMSV-A-CB | RXYA216AAYD* | RXYA240AAYD* |  |  | RXYA456AAYD* | Non-Ducted Indoor Units | 424000 | 9.4 | 19 | 414000 | 3.3 | 314000 | 2.1 | R-32 | 35.3333
218036970 | N/A | DAIKIN | HMSV-A-CB | RXYA216AAYD* | RXYA216AAYD* |  |  | RXYA432AAYD* | Ducted Indoor Units | 410000 | 9.2 | 16.8 | 404000 | 3.25 | 312000 | 2.1 | R-32 | 34.1667
218036971 | N/A | DAIKIN | HMSV-A-CB | RXYA216AAYD* | RXYA240AAYD* |  |  | RXYA456AAYD* | Ducted Indoor Units | 424000 | 9.2 | 17 | 414000 | 3.25 | 314000 | 2.1 | R-32 | 35.3333
218037006 | N/A | DAIKIN | HMSV-A-CB | RXYA216AAYD* | RXYA216AAYD* |  |  | RXYA432AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 17.9 | 404000 | 3.27 | 312000 | 2.1 | R-32 | 34.1667
218037007 | N/A | DAIKIN | HMSV-A-CB | RXYA216AAYD* | RXYA240AAYD* |  |  | RXYA456AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 424000 | 9.3 | 18 | 414000 | 3.27 | 314000 | 2.1 | R-32 | 35.3333
218036936 | N/A | DAIKIN | HMSV-A-CB | RXYA240AAYD* | RXYA240AAYD* |  |  | RXYA480AAYD* | Non-Ducted Indoor Units | 436000 | 9.4 | 18.4 | 418000 | 3.25 | 320000 | 2.1 | R-32 | 36.3333
218037053 | N/A | DAIKIN | HMSR-A-CB | REYA120AATJ* | REYA144AATJ* |  |  | REYA264AATJ* | Ducted Indoor Units | 252000 | 10.2 | 18.4 | 252000 | 3.25 | 168000 | 2.2 | R-32 | 21
218037017 | N/A | DAIKIN | HMSR-A-CB | REYA120AATJ* | REYA144AATJ* |  |  | REYA264AATJ* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.6 | 252000 | 3.7 | 168000 | 2.2 | R-32 | 21
218037089 | N/A | DAIKIN | HMSR-A-CB | REYA120AATJ* | REYA144AATJ* |  |  | REYA264AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20 | 252000 | 3.47 | 168000 | 2.2 | R-32 | 21
218037090 | N/A | DAIKIN | HMSR-A-CB | REYA144AATJ* | REYA144AATJ* |  |  | REYA288AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.9 | 19.7 | 274000 | 3.35 | 194000 | 2.15 | R-32 | 22.8333
218037091 | N/A | DAIKIN | HMSR-A-CB | REYA144AATJ* | REYA168AATJ* |  |  | REYA312AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.55 | 19.3 | 296000 | 3.3 | 212000 | 2.15 | R-32 | 24.6667
218037018 | N/A | DAIKIN | HMSR-A-CB | REYA144AATJ* | REYA144AATJ* |  |  | REYA288AATJ* | Non-Ducted Indoor Units | 274000 | 11.4 | 21 | 274000 | 3.45 | 194000 | 2.2 | R-32 | 22.8333
218037019 | N/A | DAIKIN | HMSR-A-CB | REYA144AATJ* | REYA168AATJ* |  |  | REYA312AATJ* | Non-Ducted Indoor Units | 296000 | 10.9 | 20.6 | 296000 | 3.4 | 212000 | 2.2 | R-32 | 24.6667
218037054 | N/A | DAIKIN | HMSR-A-CB | REYA144AATJ* | REYA144AATJ* |  |  | REYA288AATJ* | Ducted Indoor Units | 274000 | 10.4 | 18.4 | 274000 | 3.25 | 194000 | 2.1 | R-32 | 22.8333
218037020 | N/A | DAIKIN | HMSR-A-CB | REYA168AATJ* | REYA168AATJ* |  |  | REYA336AATJ* | Non-Ducted Indoor Units | 316000 | 9.8 | 19.8 | 310000 | 3.4 | 222000 | 2.1 | R-32 | 26.3333
218037021 | N/A | DAIKIN | HMSR-A-CB | REYA168AATJ* | REYA192AATJ* |  |  | REYA360AATJ* | Non-Ducted Indoor Units | 342000 | 10.5 | 18.9 | 342000 | 3.4 | 244000 | 2.1 | R-32 | 28.5
218037092 | N/A | DAIKIN | HMSR-A-CB | REYA168AATJ* | REYA168AATJ* |  |  | REYA336AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.9 | 18.75 | 310000 | 3.3 | 222000 | 2.1 | R-32 | 26.3333
218037093 | N/A | DAIKIN | HMSR-A-CB | REYA168AATJ* | REYA192AATJ* |  |  | REYA360AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.1 | 18.15 | 342000 | 3.3 | 244000 | 2.1 | R-32 | 28.5
218037094 | N/A | DAIKIN | HMSR-A-CB | REYA192AATJ* | REYA192AATJ* |  |  | REYA384AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 10.2 | 19.35 | 364000 | 3.27 | 264000 | 2.1 | R-32 | 30.3333
218037095 | N/A | DAIKIN | HMSR-A-CB | REYA192AATJ* | REYA216AATJ* |  |  | REYA408AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.85 | 18.55 | 388000 | 3.27 | 288000 | 2.1 | R-32 | 32.3333
218037022 | N/A | DAIKIN | HMSR-A-CB | REYA192AATJ* | REYA192AATJ* |  |  | REYA384AATJ* | Non-Ducted Indoor Units | 364000 | 10.5 | 20.7 | 364000 | 3.35 | 264000 | 2.1 | R-32 | 30.3333
218037023 | N/A | DAIKIN | HMSR-A-CB | REYA192AATJ* | REYA216AATJ* |  |  | REYA408AATJ* | Non-Ducted Indoor Units | 388000 | 10 | 19.9 | 388000 | 3.35 | 288000 | 2.1 | R-32 | 32.3333
218037024 | N/A | DAIKIN | HMSR-A-CB | REYA216AATJ* | REYA216AATJ* |  |  | REYA432AATJ* | Non-Ducted Indoor Units | 410000 | 9.8 | 18.8 | 404000 | 3.3 | 312000 | 2.1 | R-32 | 34.1667
218037025 | N/A | DAIKIN | HMSR-A-CB | REYA216AATJ* | REYA240AATJ* |  |  | REYA456AATJ* | Non-Ducted Indoor Units | 434000 | 9.4 | 18.3 | 414000 | 3.3 | 314000 | 2.1 | R-32 | 36.1667
218037096 | N/A | DAIKIN | HMSR-A-CB | REYA216AATJ* | REYA216AATJ* |  |  | REYA432AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.55 | 17.8 | 404000 | 3.25 | 312000 | 2.1 | R-32 | 34.1667
218037097 | N/A | DAIKIN | HMSR-A-CB | REYA216AATJ* | REYA240AATJ* |  |  | REYA456AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.2 | 17.25 | 414000 | 3.25 | 314000 | 2.1 | R-32 | 36.1667
218037071 | N/A | DAIKIN | HMSR-A-CB | REYA120AAYD* | REYA144AAYD* |  |  | REYA264AAYD* | Ducted Indoor Units | 252000 | 10.2 | 18.4 | 252000 | 3.25 | 168000 | 2.2 | R-32 | 21
218037035 | N/A | DAIKIN | HMSR-A-CB | REYA120AAYD* | REYA144AAYD* |  |  | REYA264AAYD* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.6 | 252000 | 3.7 | 168000 | 2.2 | R-32 | 21
218037107 | N/A | DAIKIN | HMSR-A-CB | REYA120AAYD* | REYA144AAYD* |  |  | REYA264AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 20 | 252000 | 3.47 | 168000 | 2.2 | R-32 | 21
218037108 | N/A | DAIKIN | HMSR-A-CB | REYA144AAYD* | REYA144AAYD* |  |  | REYA288AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.9 | 19.7 | 274000 | 3.35 | 194000 | 2.15 | R-32 | 22.8333
218037109 | N/A | DAIKIN | HMSR-A-CB | REYA144AAYD* | REYA168AAYD* |  |  | REYA312AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.55 | 19.3 | 296000 | 3.3 | 212000 | 2.15 | R-32 | 24.6667
218037036 | N/A | DAIKIN | HMSR-A-CB | REYA144AAYD* | REYA144AAYD* |  |  | REYA288AAYD* | Non-Ducted Indoor Units | 274000 | 11.4 | 21 | 274000 | 3.45 | 194000 | 2.2 | R-32 | 22.8333
218037037 | N/A | DAIKIN | HMSR-A-CB | REYA144AAYD* | REYA168AAYD* |  |  | REYA312AAYD* | Non-Ducted Indoor Units | 296000 | 10.9 | 20.6 | 296000 | 3.4 | 212000 | 2.2 | R-32 | 24.6667
218037072 | N/A | DAIKIN | HMSR-A-CB | REYA144AAYD* | REYA144AAYD* |  |  | REYA288AAYD* | Ducted Indoor Units | 274000 | 10.4 | 18.4 | 274000 | 3.25 | 194000 | 2.1 | R-32 | 22.8333
218037038 | N/A | DAIKIN | HMSR-A-CB | REYA168AAYD* | REYA168AAYD* |  |  | REYA336AAYD* | Non-Ducted Indoor Units | 316000 | 9.8 | 19.8 | 310000 | 3.4 | 222000 | 2.1 | R-32 | 26.3333
218037039 | N/A | DAIKIN | HMSR-A-CB | REYA168AAYD* | REYA192AAYD* |  |  | REYA360AAYD* | Non-Ducted Indoor Units | 342000 | 10.5 | 18.9 | 342000 | 3.4 | 244000 | 2.1 | R-32 | 28.5
218037110 | N/A | DAIKIN | HMSR-A-CB | REYA168AAYD* | REYA168AAYD* |  |  | REYA336AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.9 | 18.75 | 310000 | 3.3 | 222000 | 2.1 | R-32 | 26.3333
218037111 | N/A | DAIKIN | HMSR-A-CB | REYA168AAYD* | REYA192AAYD* |  |  | REYA360AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.1 | 18.15 | 342000 | 3.3 | 244000 | 2.1 | R-32 | 28.5
218037112 | N/A | DAIKIN | HMSR-A-CB | REYA192AAYD* | REYA192AAYD* |  |  | REYA384AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 10.2 | 19.35 | 364000 | 3.27 | 264000 | 2.1 | R-32 | 30.3333
218037113 | N/A | DAIKIN | HMSR-A-CB | REYA192AAYD* | REYA216AAYD* |  |  | REYA408AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.85 | 18.55 | 388000 | 3.27 | 288000 | 2.1 | R-32 | 32.3333
218037040 | N/A | DAIKIN | HMSR-A-CB | REYA192AAYD* | REYA192AAYD* |  |  | REYA384AAYD* | Non-Ducted Indoor Units | 364000 | 10.5 | 20.7 | 364000 | 3.35 | 264000 | 2.1 | R-32 | 30.3333
218037041 | N/A | DAIKIN | HMSR-A-CB | REYA192AAYD* | REYA216AAYD* |  |  | REYA408AAYD* | Non-Ducted Indoor Units | 388000 | 10 | 19.9 | 388000 | 3.35 | 288000 | 2.1 | R-32 | 32.3333
218037042 | N/A | DAIKIN | HMSR-A-CB | REYA216AAYD* | REYA216AAYD* |  |  | REYA432AAYD* | Non-Ducted Indoor Units | 410000 | 9.8 | 18.8 | 404000 | 3.3 | 312000 | 2.1 | R-32 | 34.1667
218037043 | N/A | DAIKIN | HMSR-A-CB | REYA216AAYD* | REYA240AAYD* |  |  | REYA456AAYD* | Non-Ducted Indoor Units | 434000 | 9.4 | 18.3 | 414000 | 3.3 | 314000 | 2.1 | R-32 | 36.1667
218037114 | N/A | DAIKIN | HMSR-A-CB | REYA216AAYD* | REYA216AAYD* |  |  | REYA432AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.55 | 17.8 | 404000 | 3.25 | 312000 | 2.1 | R-32 | 34.1667
218037115 | N/A | DAIKIN | HMSR-A-CB | REYA216AAYD* | REYA240AAYD* |  |  | REYA456AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.2 | 17.25 | 414000 | 3.25 | 314000 | 2.1 | R-32 | 36.1667
213886458 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM096BXVTJH | AM120BXVTJH |  | AM288BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886454 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM120BXVTJH |  | AM264BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
213886382 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM120BXVTJH |  | AM264BXVTJH | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
213886386 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM096BXVTJH | AM120BXVTJH |  | AM288BXVTJH | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
216602294 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC120L4M-4G |  | VPC264L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
216602303 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC096L4M-4G | VPC120L4M-4G |  | VPC288L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
216602154 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC072L4M-4G | VPC120L4M-4G |  | VPC264L4M-4G | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602161 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4G | VPC096L4M-4G | VPC120L4M-4G |  | VPC288L4M-4G | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
216602152 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC120L4M-4Y |  | VRC264L4M-4Y | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602159 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC096L4M-4Y | VRC120L4M-4Y |  | VRC288L4M-4Y | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
216602292 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC072L4M-4Y | VRC120L4M-4Y |  | VRC264L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
216602301 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4Y | VRC096L4M-4Y | VRC120L4M-4Y |  | VRC288L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886385 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM096BXVTFR | AM120BXVTFR |  | AM288BXVTFR | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
213886381 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM120BXVTFR |  | AM264BXVTFR | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
213886453 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM072BXVTFR | AM120BXVTFR |  | AM264BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
213886457 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM096BXVTFR | AM120BXVTFR |  | AM288BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886455 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM120BXVTJR |  | AM264BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
213886459 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM096BXVTJR | AM120BXVTJR |  | AM288BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886387 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM096BXVTJR | AM120BXVTJR |  | AM288BXVTJR | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
213886383 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM120BXVTJR |  | AM264BXVTJR | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602305 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC096L4M-4G | VRC120L4M-4G |  | VRC288L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
216602297 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC120L4M-4G |  | VRC264L4M-4G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
216602162 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC096L4M-4G | VRC120L4M-4G |  | VRC288L4M-4G | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
216602155 | 1/1/2027 | LENNOX | HMSR-A-CB | VRC072L4M-4G | VRC072L4M-4G | VRC120L4M-4G |  | VRC264L4M-4G | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602150 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC120L4M-4Y |  | VPC264L4M-4Y | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
216602157 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC096L4M-4Y | VPC120L4M-4Y |  | VPC288L4M-4Y | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
216602290 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC072L4M-4Y | VPC120L4M-4Y |  | VPC264L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
216602299 | 1/1/2027 | LENNOX | HMSV-A-CB | VPC072L4M-4Y | VPC096L4M-4Y | VPC120L4M-4Y |  | VPC288L4M-4Y | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886384 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM096BXVTFH | AM120BXVTFH |  | AM288BXVTFH | Ducted Indoor Units | 274000 | 11.5 | 21.3 | 308000 | 3.6 | 308000 | 2.13 | R-410A | 22.8333
213886380 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM120BXVTFH |  | AM264BXVTFH | Ducted Indoor Units | 252000 | 11.6 | 21.7 | 282000 | 3.74 | 282000 | 2.15 | R-410A | 21
213886456 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM096BXVTFH | AM120BXVTFH |  | AM288BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.5 | 23.05 | 308000 | 3.44 | 308000 | 2.09 | R-410A | 22.8333
213886452 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM120BXVTFH |  | AM264BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.6 | 23.5 | 282000 | 3.54 | 282000 | 2.1 | R-410A | 21
213897021 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AATJ* | RXYQ144AATJ* |  |  | RXYQ264AATJ* | Non-Ducted Indoor Units | 252000 | 11 | 21.6 | 252000 | 3.4 | 168000 | 2.2 | R-410A | 21
213897064 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AATJ* | RXYQ144AATJ* |  |  | RXYQ264AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 19.9 | 252000 | 3.3 | 168000 | 2.2 | R-410A | 21
213897065 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* | RXYQ144AATJ* |  |  | RXYQ288AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 19.35 | 274000 | 3.37 | 194000 | 2.15 | R-410A | 22.8333
213897066 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* | RXYQ168AATJ* |  |  | RXYQ312AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.1 | 19 | 296000 | 3.35 | 212000 | 2.13 | R-410A | 24.6667
213897047 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* | RXYQ144AATJ* |  |  | RXYQ288AATJ* | Ducted Indoor Units | 274000 | 10.4 | 18 | 274000 | 3.25 | 194000 | 2.1 | R-410A | 22.8333
213897022 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* | RXYQ144AATJ* |  |  | RXYQ288AATJ* | Non-Ducted Indoor Units | 274000 | 10.8 | 20.7 | 274000 | 3.5 | 194000 | 2.2 | R-410A | 22.8333
213897023 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AATJ* | RXYQ168AATJ* |  |  | RXYQ312AATJ* | Non-Ducted Indoor Units | 296000 | 10.2 | 20.6 | 296000 | 3.5 | 212000 | 2.2 | R-410A | 24.6667
213897024 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* | RXYQ192AATJ* |  |  | RXYQ360AATJ* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.8 | 342000 | 3.5 | 244000 | 2.1 | R-410A | 28.5
213897087 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* | RXYQ168AATJ* |  |  | RXYQ336AATJ* | Non-Ducted Indoor Units | 316000 | 9.3 | 18.4 | 310000 | 3.5 | 222000 | 2.1 | R-410A | 26.3333
213897098 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* | RXYQ192AATJ* |  |  | RXYQ360AATJ* | Ducted Indoor Units | 342000 | 9.3 | 17.4 | 342000 | 3.25 | 244000 | 2.1 | R-410A | 28.5
213897114 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* | RXYQ168AATJ* |  |  | RXYQ336AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.3 | 17.8 | 310000 | 3.35 | 222000 | 2.08 | R-410A | 26.3333
213897115 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AATJ* | RXYQ192AATJ* |  |  | RXYQ360AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.8 | 18.6 | 342000 | 3.37 | 244000 | 2.1 | R-410A | 28.5
213897116 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ216AATJ* |  |  | RXYQ408AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.6 | 18.3 | 388000 | 3.35 | 276000 | 2.1 | R-410A | 32.3333
213897099 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ216AATJ* |  |  | RXYQ408AATJ* | Ducted Indoor Units | 388000 | 9.2 | 17 | 388000 | 3.25 | 276000 | 2.1 | R-410A | 32.3333
213897067 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ192AATJ* |  |  | RXYQ384AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 10.1 | 18.8 | 364000 | 3.35 | 264000 | 2.1 | R-410A | 30.3333
213897049 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ192AATJ* |  |  | RXYQ384AATJ* | Ducted Indoor Units | 364000 | 9.8 | 17.6 | 364000 | 3.25 | 264000 | 2.1 | R-410A | 30.3333
213897025 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ192AATJ* |  |  | RXYQ384AATJ* | Non-Ducted Indoor Units | 364000 | 10.4 | 20 | 364000 | 3.45 | 264000 | 2.1 | R-410A | 30.3333
213897026 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AATJ* | RXYQ216AATJ* |  |  | RXYQ408AATJ* | Non-Ducted Indoor Units | 388000 | 10 | 19.6 | 388000 | 3.45 | 276000 | 2.1 | R-410A | 32.3333
213897027 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ216AATJ* |  |  | RXYQ432AATJ* | Non-Ducted Indoor Units | 404000 | 9.6 | 19 | 404000 | 3.3 | 278000 | 2.07 | R-410A | 33.6667
213897088 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ240AATJ* |  |  | RXYQ456AATJ* | Non-Ducted Indoor Units | 424000 | 9.4 | 18.4 | 414000 | 3.3 | 280000 | 2.1 | R-410A | 35.3333
213897100 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ216AATJ* |  |  | RXYQ432AATJ* | Ducted Indoor Units | 404000 | 9.1 | 16.5 | 404000 | 3.25 | 278000 | 2.1 | R-410A | 33.6667
213897101 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ240AATJ* |  |  | RXYQ456AATJ* | Ducted Indoor Units | 424000 | 9.1 | 16.4 | 414000 | 3.25 | 280000 | 2.1 | R-410A | 35.3333
213897117 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ216AATJ* |  |  | RXYQ432AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 404000 | 9.35 | 17.75 | 404000 | 3.27 | 278000 | 2.08 | R-410A | 33.6667
213897118 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AATJ* | RXYQ240AATJ* |  |  | RXYQ456AATJ* | Mixed Ducted and Non-Ducted Indoor Units | 424000 | 9.25 | 17.4 | 414000 | 3.27 | 280000 | 2.1 | R-410A | 35.3333
213897089 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AATJ* | RXYQ240AATJ* |  |  | RXYQ480AATJ* | Non-Ducted Indoor Units | 436000 | 9.4 | 18.2 | 424000 | 3.25 | 282000 | 2.1 | R-410A | 36.3333
213897034 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AAYD* | RXYQ144AAYD* |  |  | RXYQ264AAYD* | Non-Ducted Indoor Units | 252000 | 11 | 21.6 | 252000 | 3.4 | 168000 | 2.2 | R-410A | 21
213897073 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120AAYD* | RXYQ144AAYD* |  |  | RXYQ264AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 19.9 | 252000 | 3.3 | 168000 | 2.2 | R-410A | 21
213897056 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* | RXYQ144AAYD* |  |  | RXYQ288AAYD* | Ducted Indoor Units | 274000 | 10.4 | 18 | 274000 | 3.25 | 194000 | 2.1 | R-410A | 22.8333
213897074 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* | RXYQ144AAYD* |  |  | RXYQ288AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 19.35 | 274000 | 3.37 | 194000 | 2.15 | R-410A | 22.8333
213897075 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* | RXYQ168AAYD* |  |  | RXYQ312AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.1 | 19 | 296000 | 3.35 | 212000 | 2.13 | R-410A | 24.6667
213897035 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* | RXYQ144AAYD* |  |  | RXYQ288AAYD* | Non-Ducted Indoor Units | 274000 | 10.8 | 20.7 | 274000 | 3.5 | 194000 | 2.2 | R-410A | 22.8333
213897036 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144AAYD* | RXYQ168AAYD* |  |  | RXYQ312AAYD* | Non-Ducted Indoor Units | 296000 | 10.2 | 20.6 | 296000 | 3.5 | 212000 | 2.2 | R-410A | 24.6667
213897037 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* | RXYQ192AAYD* |  |  | RXYQ360AAYD* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.8 | 342000 | 3.5 | 244000 | 2.1 | R-410A | 28.5
213897092 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* | RXYQ168AAYD* |  |  | RXYQ336AAYD* | Non-Ducted Indoor Units | 316000 | 9.3 | 18.4 | 310000 | 3.5 | 222000 | 2.1 | R-410A | 26.3333
213897106 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* | RXYQ192AAYD* |  |  | RXYQ360AAYD* | Ducted Indoor Units | 342000 | 9.3 | 17.4 | 342000 | 3.25 | 244000 | 2.1 | R-410A | 28.5
213897123 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* | RXYQ168AAYD* |  |  | RXYQ336AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 316000 | 9.3 | 17.8 | 310000 | 3.35 | 222000 | 2.08 | R-410A | 26.3333
213897124 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168AAYD* | RXYQ192AAYD* |  |  | RXYQ360AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.8 | 18.6 | 342000 | 3.37 | 244000 | 2.1 | R-410A | 28.5
213897125 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ216AAYD* |  |  | RXYQ408AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 9.6 | 18.3 | 388000 | 3.35 | 276000 | 2.1 | R-410A | 32.3333
213897107 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ216AAYD* |  |  | RXYQ408AAYD* | Ducted Indoor Units | 388000 | 9.2 | 17 | 388000 | 3.25 | 276000 | 2.1 | R-410A | 32.3333
213897076 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ192AAYD* |  |  | RXYQ384AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 10.1 | 18.8 | 364000 | 3.35 | 264000 | 2.1 | R-410A | 30.3333
213897058 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ192AAYD* |  |  | RXYQ384AAYD* | Ducted Indoor Units | 364000 | 9.8 | 17.6 | 364000 | 3.25 | 264000 | 2.1 | R-410A | 30.3333
213897038 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ192AAYD* |  |  | RXYQ384AAYD* | Non-Ducted Indoor Units | 364000 | 10.4 | 20 | 364000 | 3.45 | 264000 | 2.1 | R-410A | 30.3333
213897039 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ192AAYD* | RXYQ216AAYD* |  |  | RXYQ408AAYD* | Non-Ducted Indoor Units | 388000 | 10 | 19.6 | 388000 | 3.45 | 276000 | 2.1 | R-410A | 32.3333
213897040 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ216AAYD* |  |  | RXYQ432AAYD* | Non-Ducted Indoor Units | 404000 | 9.6 | 19 | 404000 | 3.3 | 278000 | 2.07 | R-410A | 33.6667
213897108 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ216AAYD* |  |  | RXYQ432AAYD* | Ducted Indoor Units | 404000 | 9.1 | 16.5 | 404000 | 3.25 | 278000 | 2.1 | R-410A | 33.6667
213897109 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ240AAYD* |  |  | RXYQ456AAYD* | Ducted Indoor Units | 424000 | 9.1 | 16.4 | 414000 | 3.25 | 280000 | 2.1 | R-410A | 35.3333
213897093 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ240AAYD* |  |  | RXYQ456AAYD* | Non-Ducted Indoor Units | 424000 | 9.4 | 18.4 | 414000 | 3.3 | 280000 | 2.1 | R-410A | 35.3333
213897126 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ216AAYD* |  |  | RXYQ432AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 404000 | 9.35 | 17.75 | 404000 | 3.27 | 278000 | 2.08 | R-410A | 33.6667
213897127 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ216AAYD* | RXYQ240AAYD* |  |  | RXYQ456AAYD* | Mixed Ducted and Non-Ducted Indoor Units | 424000 | 9.25 | 17.4 | 414000 | 3.27 | 280000 | 2.1 | R-410A | 35.3333
213897094 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ240AAYD* | RXYQ240AAYD* |  |  | RXYQ480AAYD* | Non-Ducted Indoor Units | 436000 | 9.4 | 18.2 | 424000 | 3.25 | 282000 | 2.1 | R-410A | 36.3333
213893598 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P312TSNU-A1 | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893599 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P312TSNU-A1 | Non-Ducted Indoor Units | 298000 | 9.5 | 19.9 | 334000 | 3.63 | 216000 | 2.38 | R-410A | 24.8333
213893582 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  | PUHY-P264TSNU-A1 | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893583 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  | PUHY-P264TSNU-A1 | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893590 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P288TSNU-A1 | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893591 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P288TSNU-A1 | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213916547 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P96TNU-A1 |  | PUHY-P264TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916548 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P288TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916549 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P312TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213916562 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  | PUHY-P264YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916563 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P288YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916564 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P312YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213893586 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  | PUHY-P264YSNU-A1 | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893587 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P96YNU-A1 |  | PUHY-P264YSNU-A1 | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893594 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P288YSNU-A1 | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893595 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P288YSNU-A1 | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893602 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P312YSNU-A1 | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893603 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P312YSNU-A1 | Non-Ducted Indoor Units | 298000 | 9.5 | 19.9 | 334000 | 3.63 | 216000 | 2.38 | R-410A | 24.8333
213893606 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P336TSNU-A1 | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893607 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P336TSNU-A1 | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213916550 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P336TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213916565 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P336YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213893610 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P336YSNU-A1 | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893611 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P336YSNU-A1 | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213893613 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P360TSNU-A1 | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893617 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P384TSNU-A1 | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893621 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P408TSNU-A1 | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213894847 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P408TSNU-A1 | Non-Ducted Indoor Units | 390000 | 9.1 | 16.4 | 430000 | 3.38 | 278000 | 2.24 | R-410A | 32.5
213894835 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P360TSNU-A1 | Non-Ducted Indoor Units | 344000 | 9.4 | 18.3 | 386000 | 3.51 | 248000 | 2.24 | R-410A | 28.6667
213894839 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P384TSNU-A1 | Non-Ducted Indoor Units | 364000 | 9.1 | 16.7 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 30.3333
213916551 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 |  | PUHY-P360TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213916552 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P384TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.4 | 16.95 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 30.3333
213916553 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P408TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.4 | 16.8 | 430000 | 3.36 | 278000 | 2.18 | R-410A | 32.5
213916566 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P360YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213916567 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P384YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.4 | 16.95 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 30.3333
213916568 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P408YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.4 | 16.8 | 430000 | 3.36 | 278000 | 2.18 | R-410A | 32.5
213894841 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P384YSNU-A1 | Non-Ducted Indoor Units | 364000 | 9.1 | 16.7 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 30.3333
213894837 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P360YSNU-A1 | Non-Ducted Indoor Units | 344000 | 9.4 | 18.3 | 386000 | 3.51 | 248000 | 2.24 | R-410A | 28.6667
213894849 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P408YSNU-A1 | Non-Ducted Indoor Units | 390000 | 9.1 | 16.4 | 430000 | 3.38 | 278000 | 2.24 | R-410A | 32.5
213893623 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P408YSNU-A1 | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893619 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P384YSNU-A1 | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893615 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 | PUHY-P120YNU-A1 |  | PUHY-P360YSNU-A1 | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893625 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P432TSNU-A1 | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213894855 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P432TSNU-A1 | Non-Ducted Indoor Units | 410000 | 9.1 | 16.5 | 454000 | 3.32 | 292000 | 2.24 | R-410A | 34.1667
213916554 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 | PUHY-P144TNU-A1 |  | PUHY-P432TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 16.85 | 454000 | 3.31 | 292000 | 2.17 | R-410A | 34.1667
213916569 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P432YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 16.85 | 454000 | 3.31 | 292000 | 2.17 | R-410A | 34.1667
213894857 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P432YSNU-A1 | Non-Ducted Indoor Units | 410000 | 9.1 | 16.5 | 454000 | 3.32 | 292000 | 2.24 | R-410A | 34.1667
213893627 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 | PUHY-P144YNU-A1 |  | PUHY-P432YSNU-A1 | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213893476 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  | PUHY-EP264TSNU-A1 | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893477 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  | PUHY-EP264TSNU-A1 | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893484 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP288TSNU-A1 | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893485 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP288TSNU-A1 | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893492 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP312TSNU-A1 | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893493 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP312TSNU-A1 | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213916501 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP96TNU-A1 |  | PUHY-EP264TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916502 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP288TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916503 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP312TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213916520 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  | PUHY-EP264YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916521 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP288YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916522 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP312YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213893488 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP288YSNU-A1 | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893489 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP288YSNU-A1 | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893480 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  | PUHY-EP264YSNU-A1 | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893481 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP96YNU-A1 | PUHY-EP96YNU-A1 |  | PUHY-EP264YSNU-A1 | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893496 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP312YSNU-A1 | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893497 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP312YSNU-A1 | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893500 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP336TSNU-A1 | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893501 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP336TSNU-A1 | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213916504 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP336TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213916523 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP336YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213893504 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP336YSNU-A1 | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893505 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP336YSNU-A1 | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213893508 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP360TSNU-A1 | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893509 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP360TSNU-A1 | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893519 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP408TSNU-A1 | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893515 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP384TSNU-A1 | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213916505 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 |  | PUHY-EP360TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213916506 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP384TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.55 | 19.6 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 30.3333
213916507 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP408TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.45 | 18.9 | 430000 | 3.47 | 346000 | 2.18 | R-410A | 32.5
213894851 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP408TSNU-A1 | Non-Ducted Indoor Units | 390000 | 9.1 | 18.7 | 430000 | 3.49 | 346000 | 2.2 | R-410A | 32.5
213894843 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A1 | PUHY-EP120TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP384TSNU-A1 | Non-Ducted Indoor Units | 364000 | 9.2 | 19.5 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 30.3333
213894845 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP384YSNU-A1 | Non-Ducted Indoor Units | 364000 | 9.2 | 19.5 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 30.3333
213894853 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP408YSNU-A1 | Non-Ducted Indoor Units | 390000 | 9.1 | 18.7 | 430000 | 3.49 | 346000 | 2.2 | R-410A | 32.5
213916524 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP360YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213916525 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP384YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.55 | 19.6 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 30.3333
213916526 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP408YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.45 | 18.9 | 430000 | 3.47 | 346000 | 2.18 | R-410A | 32.5
213893517 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP384YSNU-A1 | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893512 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP360YSNU-A1 | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893513 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 | PUHY-EP120YNU-A1 |  | PUHY-EP360YSNU-A1 | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893521 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP408YSNU-A1 | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213916508 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP432TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 18.5 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213894861 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP432TSNU-A1 | Non-Ducted Indoor Units | 410000 | 9.1 | 18.2 | 454000 | 3.41 | 362000 | 2.22 | R-410A | 34.1667
213893837 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 | PUHY-EP144TNU-A1 |  | PUHY-EP432TSNU-A1 | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213893839 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP432YSNU-A1 | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213894860 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP432YSNU-A1 | Non-Ducted Indoor Units | 410000 | 9.1 | 18.2 | 454000 | 3.41 | 362000 | 2.22 | R-410A | 34.1667
213916527 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 | PUHY-EP144YNU-A1 |  | PUHY-EP432YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 18.5 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213893746 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE0963AN41AN |  | TUHYE2643BN41AN | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893747 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE0963AN41AN |  | TUHYE2643BN41AN | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893754 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3123BN41AN | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893755 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3123BN41AN | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893750 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE1203AN41AN |  | TUHYE2883BN41AN | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893751 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE1203AN41AN |  | TUHYE2883BN41AN | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213916741 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE0963AN41AN |  | TUHYE2643BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916745 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE0963AN41AN | TUHYE1203AN41AN |  | TUHYE2883BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916749 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3123BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213916751 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3124BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213916747 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE1204AN41AN |  | TUHYE2884BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916743 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE0964AN41AN |  | TUHYE2644BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213893752 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE1204AN41AN |  | TUHYE2884BN41AN | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893753 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE1204AN41AN |  | TUHYE2884BN41AN | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893756 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3124BN41AN | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893757 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3124BN41AN | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893748 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE0964AN41AN |  | TUHYE2644BN41AN | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893749 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN41AN | TUHYE0964AN41AN | TUHYE0964AN41AN |  | TUHYE2644BN41AN | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893758 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3363BN41AN | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893759 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3363BN41AN | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213916753 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3363BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213916755 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3364BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213893760 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3364BN41AN | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893761 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3364BN41AN | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213893762 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3603BN41AN | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893763 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3603BN41AN | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893766 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1443AN41AN |  | TUHYE3843BN41AN | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893768 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4083BN41AN | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213894936 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1443AN41AN |  | TUHYE3843BN41AN | Non-Ducted Indoor Units | 364000 | 9.2 | 19.5 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 30.3333
213894944 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4083BN41AN | Non-Ducted Indoor Units | 390000 | 9.1 | 18.7 | 430000 | 3.49 | 346000 | 2.2 | R-410A | 32.5
213916757 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1203AN41AN |  | TUHYE3603BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213916761 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1203AN41AN | TUHYE1443AN41AN |  | TUHYE3843BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.55 | 19.6 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 30.3333
213916765 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4083BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.45 | 18.9 | 430000 | 3.47 | 346000 | 2.18 | R-410A | 32.5
213916767 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4084BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.45 | 18.9 | 430000 | 3.47 | 346000 | 2.18 | R-410A | 32.5
213916763 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1444AN41AN |  | TUHYE3844BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.55 | 19.6 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 30.3333
213916759 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3604BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213894945 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4084BN41AN | Non-Ducted Indoor Units | 390000 | 9.1 | 18.7 | 430000 | 3.49 | 346000 | 2.2 | R-410A | 32.5
213894937 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1444AN41AN |  | TUHYE3844BN41AN | Non-Ducted Indoor Units | 364000 | 9.2 | 19.5 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 30.3333
213893769 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4084BN41AN | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893767 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1444AN41AN |  | TUHYE3844BN41AN | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893764 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3604BN41AN | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893765 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN41AN | TUHYE1204AN41AN | TUHYE1204AN41AN |  | TUHYE3604BN41AN | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893849 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4323BN41AN | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213894953 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4323BN41AN | Non-Ducted Indoor Units | 410000 | 9.1 | 18.2 | 454000 | 3.41 | 362000 | 2.22 | R-410A | 34.1667
213916769 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN41AN | TUHYE1443AN41AN | TUHYE1443AN41AN |  | TUHYE4323BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 18.5 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213916771 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4324BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.45 | 18.5 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213894954 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4324BN41AN | Non-Ducted Indoor Units | 410000 | 9.1 | 18.2 | 454000 | 3.41 | 362000 | 2.22 | R-410A | 34.1667
213893850 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN41AN | TUHYE1444AN41AN | TUHYE1444AN41AN |  | TUHYE4324BN41AN | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213893797 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP0963AN41AN |  | TUHYP2643BN41AN | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893798 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP0963AN41AN |  | TUHYP2643BN41AN | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893805 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3123BN41AN | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893806 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3123BN41AN | Non-Ducted Indoor Units | 298000 | 9.5 | 19.9 | 334000 | 3.63 | 216000 | 2.38 | R-410A | 24.8333
213893801 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP1203AN41AN |  | TUHYP2883BN41AN | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893802 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP1203AN41AN |  | TUHYP2883BN41AN | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213916822 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP0963AN41AN |  | TUHYP2643BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916826 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP0963AN41AN | TUHYP1203AN41AN |  | TUHYP2883BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916830 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3123BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213916832 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3124BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213916828 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP1204AN41AN |  | TUHYP2884BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916824 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP0964AN41AN |  | TUHYP2644BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213893803 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP1204AN41AN |  | TUHYP2884BN41AN | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893804 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP1204AN41AN |  | TUHYP2884BN41AN | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893807 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3124BN41AN | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893808 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3124BN41AN | Non-Ducted Indoor Units | 298000 | 9.5 | 19.9 | 334000 | 3.63 | 216000 | 2.38 | R-410A | 24.8333
213893799 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP0964AN41AN |  | TUHYP2644BN41AN | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893800 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN41AN | TUHYP0964AN41AN | TUHYP0964AN41AN |  | TUHYP2644BN41AN | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893809 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3363BN41AN | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893810 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3363BN41AN | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213916834 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3363BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213916836 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3364BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213893811 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3364BN41AN | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893812 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3364BN41AN | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213893813 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3603BN41AN | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893815 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1443AN41AN |  | TUHYP3843BN41AN | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893817 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4083BN41AN | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213894938 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1443AN41AN |  | TUHYP3843BN41AN | Non-Ducted Indoor Units | 364000 | 9.1 | 16.7 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 30.3333
213894930 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3603BN41AN | Non-Ducted Indoor Units | 344000 | 9.4 | 18.3 | 386000 | 3.51 | 248000 | 2.24 | R-410A | 28.6667
213894946 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4083BN41AN | Non-Ducted Indoor Units | 390000 | 9.1 | 16.4 | 430000 | 3.38 | 278000 | 2.24 | R-410A | 32.5
213916838 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1203AN41AN |  | TUHYP3603BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213916842 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1203AN41AN | TUHYP1443AN41AN |  | TUHYP3843BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.4 | 16.95 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 30.3333
213916846 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4083BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.4 | 16.8 | 430000 | 3.36 | 278000 | 2.18 | R-410A | 32.5
213916848 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4084BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.4 | 16.8 | 430000 | 3.36 | 278000 | 2.18 | R-410A | 32.5
213916844 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1444AN41AN |  | TUHYP3844BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.4 | 16.95 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 30.3333
213916840 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3604BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213894947 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4084BN41AN | Non-Ducted Indoor Units | 390000 | 9.1 | 16.4 | 430000 | 3.38 | 278000 | 2.24 | R-410A | 32.5
213894931 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3604BN41AN | Non-Ducted Indoor Units | 344000 | 9.4 | 18.3 | 386000 | 3.51 | 248000 | 2.24 | R-410A | 28.6667
213894939 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1444AN41AN |  | TUHYP3844BN41AN | Non-Ducted Indoor Units | 364000 | 9.1 | 16.7 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 30.3333
213893818 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4084BN41AN | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893816 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1444AN41AN |  | TUHYP3844BN41AN | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893814 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN41AN | TUHYP1204AN41AN | TUHYP1204AN41AN |  | TUHYP3604BN41AN | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893819 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4323BN41AN | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213894948 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4323BN41AN | Non-Ducted Indoor Units | 410000 | 9.1 | 16.5 | 454000 | 3.32 | 292000 | 2.24 | R-410A | 34.1667
213916850 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN41AN | TUHYP1443AN41AN | TUHYP1443AN41AN |  | TUHYP4323BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 16.85 | 454000 | 3.31 | 292000 | 2.17 | R-410A | 34.1667
213916852 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4324BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 9.4 | 16.85 | 454000 | 3.31 | 292000 | 2.17 | R-410A | 34.1667
213894882 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4324BN41AN | Non-Ducted Indoor Units | 410000 | 9.1 | 16.5 | 454000 | 3.32 | 292000 | 2.24 | R-410A | 34.1667
213893820 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN41AN | TUHYP1444AN41AN | TUHYP1444AN41AN |  | TUHYP4324BN41AN | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213896090 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144YNU-A1 | PURY-EP144YNU-A1 |  |  | PURY-EP288YSNU-A1 | Non-Ducted Indoor Units | 276000 | 9.4 | 20.8 | 304000 | 3.46 | 196000 | 2.08 | R-410A | 23
213895970 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144YNU-A1 | PURY-EP120YNU-A1 |  |  | PURY-EP264YSNU-A1 | Ducted Indoor Units | 252000 | 9.5 | 19.4 | 280000 | 3.36 | 180000 | 2.07 | R-410A | 21
214050126 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168YNU-A1 | PURY-EP168YNU-A1 |  |  | PURY-EP336YSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.25 | 18.95 | 360000 | 3.25 | 220000 | 2.08 | R-410A | 26.6667
213896088 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144TNU-A1 | PURY-EP144TNU-A1 |  |  | PURY-EP288TSNU-A1 | Non-Ducted Indoor Units | 276000 | 9.4 | 20.8 | 304000 | 3.46 | 196000 | 2.08 | R-410A | 23
213895968 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP144TNU-A1 | PURY-EP120TNU-A1 |  |  | PURY-EP264TSNU-A1 | Ducted Indoor Units | 252000 | 9.5 | 19.4 | 280000 | 3.36 | 180000 | 2.07 | R-410A | 21
214050124 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP168TNU-A1 | PURY-EP168TNU-A1 |  |  | PURY-EP336TSNU-A1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.25 | 18.95 | 360000 | 3.25 | 220000 | 2.08 | R-410A | 26.6667
213896178 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AN41AN | TURYE1444AN41AN |  |  | TURYE2884BN41AN | Non-Ducted Indoor Units | 276000 | 9.4 | 20.8 | 304000 | 3.46 | 196000 | 2.08 | R-410A | 23
213896034 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1444AN41AN | TURYE1204AN41AN |  |  | TURYE2644BN41AN | Ducted Indoor Units | 252000 | 9.5 | 19.4 | 280000 | 3.36 | 180000 | 2.07 | R-410A | 21
214050340 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1684AN41AN | TURYE1684AN41AN |  |  | TURYE3364BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.25 | 18.95 | 360000 | 3.25 | 220000 | 2.08 | R-410A | 26.6667
213896176 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AN41AN | TURYE1443AN41AN |  |  | TURYE2883BN41AN | Non-Ducted Indoor Units | 276000 | 9.4 | 20.8 | 304000 | 3.46 | 196000 | 2.08 | R-410A | 23
213896032 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1443AN41AN | TURYE1203AN41AN |  |  | TURYE2643BN41AN | Ducted Indoor Units | 252000 | 9.5 | 19.4 | 280000 | 3.36 | 180000 | 2.07 | R-410A | 21
214050338 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE1683AN41AN | TURYE1683AN41AN |  |  | TURYE3363BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.25 | 18.95 | 360000 | 3.25 | 220000 | 2.08 | R-410A | 26.6667
9990285 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA72RLBV1 |  | AOUA264RLBVG1 | Non-Ducted Indoor Units | 252000 | 10.9 | 20.8 | 282000 | 3.45 | 194000 | 2.29 | R-410A | 21
9990286 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA96RLBV1 |  | AOUA288RLBVG1 | Non-Ducted Indoor Units | 274000 | 10.6 | 20.8 | 308000 | 3.36 | 210000 | 2.29 | R-410A | 22.8333
213916337 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Non-Ducted Indoor Units | 252000 | 10.2 | 21.2 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
213916344 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Ducted Indoor Units | 252000 | 10 | 21 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
213916869 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.1 | 21.1 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
213916870 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.9 | 20.65 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
213916345 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
213916338 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Non-Ducted Indoor Units | 276000 | 9.9 | 20.6 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
213916339 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Non-Ducted Indoor Units | 298000 | 9.1 | 20.2 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
213916365 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Ducted Indoor Units | 298000 | 9.6 | 20.1 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
213916871 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.4 | 20.15 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
213916873 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM144BTE5 |  |  | ARUM360BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.1 | 19.25 | 364000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
213916875 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM192BTE5 |  |  | ARUM408BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.1 | 17.7 | 412000 | 3.28 | 284000 | 2.16 | R-410A | 32.5
213916372 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Non-Ducted Indoor Units | 252000 | 10.2 | 21.2 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
213916383 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Ducted Indoor Units | 252000 | 10 | 21 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
213916880 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.1 | 21.1 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
213916881 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.9 | 20.65 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
213916384 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
213916373 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Non-Ducted Indoor Units | 276000 | 9.9 | 20.6 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
213916374 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Non-Ducted Indoor Units | 298000 | 9.1 | 20.2 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
213916385 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Ducted Indoor Units | 298000 | 9.6 | 20.1 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
213916882 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.4 | 20.15 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
213916884 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM144DTE5 |  |  | ARUM360DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.1 | 19.25 | 364000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
213916886 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM192DTE5 |  |  | ARUM408DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.1 | 17.7 | 412000 | 3.28 | 284000 | 2.16 | R-410A | 32.5
214091739 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S | TVAHP144B32S |  | TVAHP432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091591 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP192B32S | TVAHP144B32S |  |  | TVAHP336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091755 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S | TVAHP144B42S |  | TVAHP432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091607 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP192B42S | TVAHP144B42S |  |  | TVAHP336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091691 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S | HVAHP144B32S |  | HVAHP432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091543 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S | HVAHP144B32S |  |  | HVAHP336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091707 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S | HVAHP144B42S |  | HVAHP432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091559 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S | HVAHP144B42S |  |  | HVAHP336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091787 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S | YVAHP144B32S |  | YVAHP432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091639 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S | YVAHP144B32S |  |  | YVAHP336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091803 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S | YVAHP144B42S |  | YVAHP432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091655 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S | YVAHP144B42S |  |  | YVAHP336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094489 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S | HVAHR144B42S |  | HVAHR432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094341 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S | HVAHR144B42S |  |  | HVAHR336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094569 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S | YVAHR144B32S |  | YVAHR432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094421 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S | YVAHR144B32S |  |  | YVAHR336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094585 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S | YVAHR144B42S |  | YVAHR432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094521 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S | TVAHR144B32S |  | TVAHR432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094373 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR192B32S | TVAHR144B32S |  |  | TVAHR336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094537 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S | TVAHR144B42S |  | TVAHR432B42S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094389 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR192B42S | TVAHR144B42S |  |  | TVAHR336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094473 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S | HVAHR144B32S |  | HVAHR432B32S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094325 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S | HVAHR144B32S |  |  | HVAHR336B32S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094437 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S | YVAHR144B42S |  |  | YVAHR336B42S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
213894856 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A | PUHY-P144YNU-A | PUHY-P144YNU-A |  | PUHY-P432YSNU-A | Non-Ducted Indoor Units | 410000 | 9.1 | 16.5 | 454000 | 3.32 | 292000 | 2.24 | R-410A | 34.1667
214094553 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR144B52S | TVAHR144B52S | TVAHR144B52S |  | TVAHR432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094405 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSR-A-CB | TVAHR192B52S | TVAHR144B52S |  |  | TVAHR336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094505 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR144B52S | HVAHR144B52S |  | HVAHR432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094357 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B52S | HVAHR144B52S |  |  | HVAHR336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214094601 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR144B52S | YVAHR144B52S |  | YVAHR432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214094453 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B52S | YVAHR144B52S |  |  | YVAHR336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091771 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP144B52S | TVAHP144B52S | TVAHP144B52S |  | TVAHP432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091623 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP192B52S | TVAHP144B52S |  |  | TVAHP336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091723 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP144B52S | HVAHP144B52S |  | HVAHP432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091575 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B52S | HVAHP144B52S |  |  | HVAHP336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
214091819 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP144B52S | YVAHP144B52S |  | YVAHP432B52S | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.1 | 16.55 | 460000 | 3.28 | 300000 | 2.12 | R-410A | 34.3333
214091671 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B52S | YVAHP144B52S |  |  | YVAHP336B52S | Non-Ducted Indoor Units | 320000 | 9.5 | 17.2 | 360000 | 3.27 | 232000 | 2.31 | R-410A | 26.6667
213916355 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Ducted Indoor Units | 252000 | 10 | 21 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
213916348 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Non-Ducted Indoor Units | 252000 | 10.2 | 21.2 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
213916891 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.1 | 21.1 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
213916892 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.9 | 20.65 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
213916349 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Non-Ducted Indoor Units | 276000 | 9.9 | 20.6 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
213916356 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
213916398 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Ducted Indoor Units | 298000 | 9.6 | 20.1 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
213916350 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Non-Ducted Indoor Units | 298000 | 9.1 | 20.2 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
213916893 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.4 | 20.15 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
213916895 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM144CTE5 |  |  | ARUM360CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.1 | 19.25 | 364000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
213916897 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM192CTE5 |  |  | ARUM408CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.1 | 17.7 | 412000 | 3.28 | 284000 | 2.16 | R-410A | 32.5
213896288 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P264ZSKMU-B | Non-Ducted Indoor Units | 252000 | 10.8 | 19 | 280000 | 3.62 | 200000 | 2.16 | R-410A | 21
213896289 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P288ZSKMU-B | Non-Ducted Indoor Units | 276000 | 10.6 | 18.9 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 23
213896290 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P312ZSKMU-B | Non-Ducted Indoor Units | 298000 | 10 | 17.5 | 334000 | 3.59 | 236000 | 2.22 | R-410A | 24.8333
213896330 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P312ZSKMU-B | Ducted Indoor Units | 298000 | 11 | 17.3 | 334000 | 3.46 | 236000 | 2.43 | R-410A | 24.8333
213896328 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P288ZSKMU-B | Ducted Indoor Units | 276000 | 11.1 | 18.1 | 308000 | 3.49 | 216000 | 2.53 | R-410A | 23
213896326 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P264ZSKMU-B | Ducted Indoor Units | 252000 | 11.3 | 18.2 | 280000 | 3.47 | 200000 | 2.52 | R-410A | 21
213916485 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P264ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.05 | 18.6 | 280000 | 3.54 | 200000 | 2.34 | R-410A | 21
213916486 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P288ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.85 | 18.5 | 308000 | 3.54 | 216000 | 2.37 | R-410A | 23
213916487 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P312ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.5 | 17.4 | 334000 | 3.52 | 236000 | 2.32 | R-410A | 24.8333
213916488 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P336ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 17.65 | 360000 | 3.42 | 268000 | 2.25 | R-410A | 26.6667
213896332 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P336ZSKMU-B | Ducted Indoor Units | 320000 | 10.9 | 17.9 | 360000 | 3.42 | 268000 | 2.38 | R-410A | 26.6667
213896291 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P336ZSKMU-B | Non-Ducted Indoor Units | 320000 | 10.1 | 17.4 | 360000 | 3.42 | 268000 | 2.13 | R-410A | 26.6667
213896334 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P360ZSKMU-B | Ducted Indoor Units | 344000 | 10.8 | 17.4 | 386000 | 3.32 | 284000 | 2.32 | R-410A | 28.6667
213916489 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B | PUHY-P120ZKMU-B |  | PUHY-P360ZSKMU-B | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.45 | 17.1 | 386000 | 3.36 | 284000 | 2.18 | R-410A | 28.6667
208812542 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULBV5 |  |  |  | AOUA72ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 25.1 | 77000 | 4.09 | 56000 | 2.55 | R-410A | 5.75
208812543 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULBV5 |  |  |  | AOUA96ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.45 | 23.95 | 103000 | 3.86 | 73000 | 2.49 | R-410A | 7.6667
208812544 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 |  |  |  | AOUA120ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.4 | 24.1 | 129000 | 3.67 | 87000 | 2.43 | R-410A | 9.5833
208812547 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72ULCV5 |  |  |  | AOUA72ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 25.1 | 77000 | 4.09 | 56000 | 2.55 | R-410A | 5.75
208812548 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96ULCV5 |  |  |  | AOUA96ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.45 | 23.95 | 103000 | 3.86 | 73000 | 2.49 | R-410A | 7.6667
208812549 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 |  |  |  | AOUA120ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.4 | 24.1 | 129000 | 3.67 | 87000 | 2.43 | R-410A | 9.5833
213895002 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT6P-UL |  |  |  | MMY-MUP0721HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.23 | 56000 | 2.88 | R-410A | 5.75
213894090 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT6P-UL |  |  |  | MMY-MUP0721HT6P-UL | Non-Ducted Indoor Units | 69000 | 13.4 | 24.1 | 77000 | 4.46 | 56000 | 2.94 | R-410A | 5.75
213894109 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT6P-UL |  |  |  | MMY-MUP0721HT6P-UL | Ducted Indoor Units | 69000 | 12.6 | 22.1 | 77000 | 4.01 | 56000 | 2.82 | R-410A | 5.75
213894116 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL |  |  |  | MMY-MUP0961HT6P-UL | Ducted Indoor Units | 92000 | 12 | 21.9 | 103000 | 3.83 | 76000 | 2.61 | R-410A | 7.6667
213894091 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL |  |  |  | MMY-MUP0961HT6P-UL | Non-Ducted Indoor Units | 92000 | 11.8 | 23.7 | 103000 | 4.21 | 76000 | 2.72 | R-410A | 7.6667
213895006 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL |  |  |  | MMY-MUP0961HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.8 | 103000 | 4.02 | 76000 | 2.66 | R-410A | 7.6667
213895010 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT6P-UL |  |  |  | MMY-MUP1201HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 22 | 129000 | 3.96 | 92000 | 2.81 | R-410A | 9.5
213894092 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT6P-UL |  |  |  | MMY-MUP1201HT6P-UL | Non-Ducted Indoor Units | 114000 | 11.1 | 22.8 | 129000 | 4.09 | 92000 | 2.85 | R-410A | 9.5
213894123 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT6P-UL |  |  |  | MMY-MUP1201HT6P-UL | Ducted Indoor Units | 114000 | 11.7 | 21.2 | 129000 | 3.83 | 92000 | 2.78 | R-410A | 9.5
213895004 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL |  |  |  | MMY-MUP072H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.15 | 23.6 | 77000 | 4.37 | 64000 | 2.84 | R-410A | 5.75
213894107 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL |  |  |  | MMY-MUP072H1HT6PUL | Non-Ducted Indoor Units | 69000 | 13.6 | 24.4 | 77000 | 4.52 | 64000 | 2.91 | R-410A | 5.75
213894111 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL |  |  |  | MMY-MUP072H1HT6PUL | Ducted Indoor Units | 69000 | 12.7 | 22.8 | 77000 | 4.23 | 64000 | 2.78 | R-410A | 5.75
213894114 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL |  |  |  | MMY-MUP096H1HT6PUL | Non-Ducted Indoor Units | 92000 | 12.1 | 23.4 | 103000 | 4.49 | 87000 | 2.84 | R-410A | 7.6667
213894118 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL |  |  |  | MMY-MUP096H1HT6PUL | Ducted Indoor Units | 92000 | 11.8 | 20 | 103000 | 4.22 | 87000 | 2.73 | R-410A | 7.6667
213895008 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL |  |  |  | MMY-MUP096H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.95 | 21.7 | 103000 | 4.35 | 87000 | 2.78 | R-410A | 7.6667
213895012 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL |  |  |  | MMY-MUP120H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.6 | 22.05 | 129000 | 4.02 | 116000 | 2.55 | R-410A | 9.5
213894125 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL |  |  |  | MMY-MUP120H1HT6PUL | Ducted Indoor Units | 114000 | 12 | 21.4 | 129000 | 3.92 | 116000 | 2.59 | R-410A | 9.5
213894121 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL |  |  |  | MMY-MUP120H1HT6PUL | Non-Ducted Indoor Units | 114000 | 11.2 | 22.7 | 129000 | 4.13 | 116000 | 2.51 | R-410A | 9.5
213894110 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT9P-UL |  |  |  | MMY-MUP0721HT9P-UL | Ducted Indoor Units | 69000 | 12.6 | 22.1 | 77000 | 4.01 | 56000 | 2.82 | R-410A | 5.75
213894106 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT9P-UL |  |  |  | MMY-MUP0721HT9P-UL | Non-Ducted Indoor Units | 69000 | 13.4 | 24.1 | 77000 | 4.46 | 56000 | 2.94 | R-410A | 5.75
213895003 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0721HT9P-UL |  |  |  | MMY-MUP0721HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.23 | 56000 | 2.88 | R-410A | 5.75
213895007 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL |  |  |  | MMY-MUP0961HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.8 | 103000 | 4.02 | 76000 | 2.66 | R-410A | 7.6667
213894113 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL |  |  |  | MMY-MUP0961HT9P-UL | Non-Ducted Indoor Units | 92000 | 11.8 | 23.7 | 103000 | 4.21 | 76000 | 2.72 | R-410A | 7.6667
213894117 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL |  |  |  | MMY-MUP0961HT9P-UL | Ducted Indoor Units | 92000 | 12 | 21.9 | 103000 | 3.83 | 76000 | 2.61 | R-410A | 7.6667
213894120 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT9P-UL |  |  |  | MMY-MUP1201HT9P-UL | Non-Ducted Indoor Units | 114000 | 11.1 | 22.8 | 129000 | 4.09 | 92000 | 2.85 | R-410A | 9.5
213894124 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT9P-UL |  |  |  | MMY-MUP1201HT9P-UL | Ducted Indoor Units | 114000 | 11.7 | 21.2 | 129000 | 3.83 | 92000 | 2.78 | R-410A | 9.5
213895011 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1201HT9P-UL |  |  |  | MMY-MUP1201HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 22 | 129000 | 3.96 | 92000 | 2.81 | R-410A | 9.5
213895005 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL |  |  |  | MMY-MUP072H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.15 | 23.6 | 77000 | 4.37 | 64000 | 2.84 | R-410A | 5.75
213894112 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL |  |  |  | MMY-MUP072H1HT9PUL | Ducted Indoor Units | 69000 | 12.7 | 22.8 | 77000 | 4.23 | 64000 | 2.78 | R-410A | 5.75
213894108 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL |  |  |  | MMY-MUP072H1HT9PUL | Non-Ducted Indoor Units | 69000 | 13.6 | 24.4 | 77000 | 4.52 | 64000 | 2.91 | R-410A | 5.75
213894119 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL |  |  |  | MMY-MUP096H1HT9PUL | Ducted Indoor Units | 92000 | 11.8 | 20 | 103000 | 4.22 | 87000 | 2.73 | R-410A | 7.6667
213894115 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL |  |  |  | MMY-MUP096H1HT9PUL | Non-Ducted Indoor Units | 92000 | 12.1 | 23.4 | 103000 | 4.49 | 87000 | 2.84 | R-410A | 7.6667
213895009 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL |  |  |  | MMY-MUP096H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.95 | 21.7 | 103000 | 4.35 | 87000 | 2.78 | R-410A | 7.6667
213895013 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL |  |  |  | MMY-MUP120H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.6 | 22.05 | 129000 | 4.02 | 116000 | 2.55 | R-410A | 9.5
213894126 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL |  |  |  | MMY-MUP120H1HT9PUL | Ducted Indoor Units | 114000 | 12 | 21.4 | 129000 | 3.92 | 116000 | 2.59 | R-410A | 9.5
213894122 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL |  |  |  | MMY-MUP120H1HT9PUL | Non-Ducted Indoor Units | 114000 | 11.2 | 22.7 | 129000 | 4.13 | 116000 | 2.51 | R-410A | 9.5
213884892 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT6P-UL |  |  |  | MMY-MUP0721FT6P-UL | Non-Ducted Indoor Units | 69000 | 13.5 | 26.5 | 77000 | 4.55 | 56000 | 2.8 | R-410A | 5.75
213884896 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT6P-UL |  |  |  | MMY-MUP0721FT6P-UL | Ducted Indoor Units | 69000 | 12.6 | 23.4 | 77000 | 4.18 | 56000 | 2.7 | R-410A | 5.75
213885174 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT6P-UL |  |  |  | MMY-MUP0721FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.05 | 24.95 | 77000 | 4.36 | 56000 | 2.75 | R-410A | 5.75
213885178 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL |  |  |  | MMY-MUP0961FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 23.6 | 103000 | 4.16 | 74000 | 2.65 | R-410A | 7.6667
213884900 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL |  |  |  | MMY-MUP0961FT6P-UL | Non-Ducted Indoor Units | 92000 | 12.1 | 26 | 103000 | 4.45 | 74000 | 2.7 | R-410A | 7.6667
213884912 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT6P-UL |  |  |  | MMY-MUP1201FT6P-UL | Ducted Indoor Units | 115000 | 11.6 | 22 | 129000 | 3.84 | 92000 | 2.44 | R-410A | 9.5833
213884908 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT6P-UL |  |  |  | MMY-MUP1201FT6P-UL | Non-Ducted Indoor Units | 115000 | 12.1 | 24.6 | 129000 | 4.2 | 92000 | 2.68 | R-410A | 9.5833
213885182 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT6P-UL |  |  |  | MMY-MUP1201FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.85 | 23.3 | 129000 | 4.02 | 92000 | 2.56 | R-410A | 9.5833
213884898 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL |  |  |  | MMY-MUP072H1FT6PUL | Ducted Indoor Units | 69000 | 12.6 | 23.4 | 77000 | 4.18 | 64000 | 2.7 | R-410A | 5.75
213884894 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL |  |  |  | MMY-MUP072H1FT6PUL | Non-Ducted Indoor Units | 69000 | 13.5 | 26.5 | 77000 | 4.55 | 64000 | 2.8 | R-410A | 5.75
213885175 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL |  |  |  | MMY-MUP072H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.05 | 24.95 | 77000 | 4.36 | 64000 | 2.75 | R-410A | 5.75
213885179 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL |  |  |  | MMY-MUP096H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 23.45 | 103000 | 4.45 | 86000 | 2.82 | R-410A | 7.6667
213884906 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL |  |  |  | MMY-MUP096H1FT6PUL | Ducted Indoor Units | 92000 | 12.2 | 21.6 | 103000 | 4.1 | 86000 | 2.69 | R-410A | 7.6667
213884902 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL |  |  |  | MMY-MUP096H1FT6PUL | Non-Ducted Indoor Units | 92000 | 13.3 | 25.3 | 103000 | 4.8 | 86000 | 2.95 | R-410A | 7.6667
213884914 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL |  |  |  | MMY-MUP120H1FT6PUL | Ducted Indoor Units | 115000 | 12 | 22.5 | 129000 | 3.91 | 110000 | 2.58 | R-410A | 9.5833
213884910 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL |  |  |  | MMY-MUP120H1FT6PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24.8 | 129000 | 4.43 | 110000 | 2.8 | R-410A | 9.5833
213885183 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL |  |  |  | MMY-MUP120H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.2 | 23.65 | 129000 | 4.17 | 110000 | 2.69 | R-410A | 9.5833
213885173 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT9P-UL |  |  |  | MMY-MUP0721FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.05 | 24.95 | 77000 | 4.36 | 56000 | 2.75 | R-410A | 5.75
213884897 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT9P-UL |  |  |  | MMY-MUP0721FT9P-UL | Ducted Indoor Units | 69000 | 12.6 | 23.4 | 77000 | 4.18 | 56000 | 2.7 | R-410A | 5.75
213884893 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0721FT9P-UL |  |  |  | MMY-MUP0721FT9P-UL | Non-Ducted Indoor Units | 69000 | 13.5 | 26.5 | 77000 | 4.55 | 56000 | 2.8 | R-410A | 5.75
213884901 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL |  |  |  | MMY-MUP0961FT9P-UL | Non-Ducted Indoor Units | 92000 | 12.1 | 26 | 103000 | 4.45 | 74000 | 2.7 | R-410A | 7.6667
213885177 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL |  |  |  | MMY-MUP0961FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 23.6 | 103000 | 4.16 | 74000 | 2.65 | R-410A | 7.6667
213885181 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT9P-UL |  |  |  | MMY-MUP1201FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.85 | 23.3 | 129000 | 4.02 | 92000 | 2.56 | R-410A | 9.5833
213884913 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT9P-UL |  |  |  | MMY-MUP1201FT9P-UL | Ducted Indoor Units | 115000 | 11.6 | 22 | 129000 | 3.84 | 92000 | 2.44 | R-410A | 9.5833
213884909 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1201FT9P-UL |  |  |  | MMY-MUP1201FT9P-UL | Non-Ducted Indoor Units | 115000 | 12.1 | 24.6 | 129000 | 4.2 | 92000 | 2.68 | R-410A | 9.5833
213884899 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL |  |  |  | MMY-MUP072H1FT9PUL | Ducted Indoor Units | 69000 | 12.6 | 23.4 | 77000 | 4.18 | 64000 | 2.7 | R-410A | 5.75
213884895 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL |  |  |  | MMY-MUP072H1FT9PUL | Non-Ducted Indoor Units | 69000 | 13.5 | 26.5 | 77000 | 4.55 | 64000 | 2.8 | R-410A | 5.75
213885176 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL |  |  |  | MMY-MUP072H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.05 | 24.95 | 77000 | 4.36 | 64000 | 2.75 | R-410A | 5.75
213885180 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL |  |  |  | MMY-MUP096H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.75 | 23.45 | 103000 | 4.45 | 86000 | 2.82 | R-410A | 7.6667
213884907 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL |  |  |  | MMY-MUP096H1FT9PUL | Ducted Indoor Units | 92000 | 12.2 | 21.6 | 103000 | 4.1 | 86000 | 2.69 | R-410A | 7.6667
213884903 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL |  |  |  | MMY-MUP096H1FT9PUL | Non-Ducted Indoor Units | 92000 | 13.3 | 25.3 | 103000 | 4.8 | 86000 | 2.95 | R-410A | 7.6667
213884915 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL |  |  |  | MMY-MUP120H1FT9PUL | Ducted Indoor Units | 115000 | 12 | 22.5 | 129000 | 3.91 | 110000 | 2.58 | R-410A | 9.5833
213884911 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL |  |  |  | MMY-MUP120H1FT9PUL | Non-Ducted Indoor Units | 115000 | 12.4 | 24.8 | 129000 | 4.43 | 110000 | 2.8 | R-410A | 9.5833
213885184 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL |  |  |  | MMY-MUP120H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.2 | 23.65 | 129000 | 4.17 | 110000 | 2.69 | R-410A | 9.5833
201830229 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DXN1 |  |  |  | MV5-H72DXN1* | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201830230 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DXN1 |  |  |  | MV5-H72DXN1* | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201850119 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201850120 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201850236 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201850237 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201994655 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201994656 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
202073585 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DXN1 |  |  |  | MV5-H72DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.22 | 20.57 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
204723036 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
204723037 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
207591014 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 12.85 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
207591015 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
207591016 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
204723038 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
202073586 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 |  |  |  | MV5-H96DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 19.94 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
201994657 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201850238 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201850121 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201830231 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 |  |  |  | MV5-H96DXN1* | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201830261 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DZN1 |  |  |  | MV5-H72DZN1* | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201830262 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DZN1 |  |  |  | MV5-H72DZN1* | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201850151 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201850152 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201994705 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201994707 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
201850268 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
201850269 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
202073601 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DZN1 |  |  |  | MV5-H72DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 20.57 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
204723068 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
204723069 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
207591046 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 12.83 | 21.38 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
207591047 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 11.6 | 19.76 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
207591048 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
204723070 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
202073602 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 |  |  |  | MV5-H96DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 19.94 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
201850270 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201994709 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201850153 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201830263 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 |  |  |  | MV5-H96DZN1* | Non-Ducted Indoor Units | 92000 | 11.4 | 20.43 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
201830293 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DXN1 |  |  |  | MV5-2R72DXN1* | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201830294 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DXN1 |  |  |  | MV5-2R72DXN1* | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201850183 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201850184 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201850300 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201850301 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201994758 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201994759 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
202073617 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DXN1 |  |  |  | MV5-2R72DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.75 | 77000 | 3.77 | 54000 | 2.43 | R-410A | 5.75
204723100 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
204723101 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
207591078 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
207591079 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
207591080 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
204723102 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
202073618 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DXN1 |  |  |  | MV5-2R96DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.7 | 21.1 | 103000 | 3.5 | 72000 | 2.31 | R-410A | 7.6667
201994761 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201850302 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201850185 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201830295 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DXN1 |  |  |  | MV5-2R96DXN1* | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201830319 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DZN1 |  |  |  | MV5-2R72DZN1* | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201830320 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DZN1 |  |  |  | MV5-2R72DZN1* | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201850209 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201850210 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201994802 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201994804 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
201850326 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
201850327 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
202073630 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DZN1 |  |  |  | MV5-2R72DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.75 | 77000 | 3.77 | 54000 | 2.43 | R-410A | 5.75
204723126 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
204723127 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
207591104 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 13 | 21.9 | 77000 | 3.89 | 54000 | 2.58 | R-410A | 5.75
207591105 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.66 | 54000 | 2.29 | R-410A | 5.75
207591106 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
204723128 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
202073631 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DZN1 |  |  |  | MV5-2R96DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.7 | 21.1 | 103000 | 3.5 | 72000 | 2.31 | R-410A | 7.6667
201850328 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201994806 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201850211 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
201830321 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DZN1 |  |  |  | MV5-2R96DZN1* | Non-Ducted Indoor Units | 92000 | 11.9 | 21.5 | 103000 | 3.56 | 72000 | 2.39 | R-410A | 7.6667
202583518 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU96RLAVL |  |  |  | AOU96RLAVL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.6 | 22.1 | 103000 | 3.76 | 73000 | 2.49 | R-410A | 7.6667
202583517 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU72RLAVL |  |  |  | AOU72RLAVL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 4.1 | 56000 | 2.64 | R-410A | 5.75
202583519 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU120RLAVL |  |  |  | AOU120RLAVL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.6 | 22.55 | 129000 | 3.7 | 87000 | 2.38 | R-410A | 9.5
202918833 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3Y |  |  |  | VPB072H4M-3Y | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202918834 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3Y |  |  |  | VPB072H4M-3Y | Ducted Indoor Units | 69000 | 12.1 | 21.9 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202918835 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3Y |  |  |  | VPB072H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.45 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202882193 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1 |  |  |  | MV6-X72DXN1 | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202882194 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1 |  |  |  | MV6-X72DXN1 | Ducted Indoor Units | 69000 | 12.1 | 21.9 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202891635 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1 |  |  |  | MV6-X72DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.45 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202891636 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1 |  |  |  | MV6-X72DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.45 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202883243 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1 |  |  |  | MV6-X72DZN1 | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202883244 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1 |  |  |  | MV6-X72DZN1 | Ducted Indoor Units | 69000 | 12.1 | 21.9 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202918830 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3G |  |  |  | VPB072H4M-3G | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202918831 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3G |  |  |  | VPB072H4M-3G | Ducted Indoor Units | 69000 | 12.1 | 21.9 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202918832 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072H4M-3G |  |  |  | VPB072H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.45 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202918941 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3Y |  |  |  | VRB072H4M-3Y | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202918942 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3Y |  |  |  | VRB072H4M-3Y | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202918943 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3Y |  |  |  | VRB072H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202883245 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1 |  |  |  | MV6-R72DXN1 | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202883246 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1 |  |  |  | MV6-R72DXN1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202891643 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1 |  |  |  | MV6-R72DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202891644 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1 |  |  |  | MV6-R72DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202883247 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1 |  |  |  | MV6-R72DZN1 | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202883248 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1 |  |  |  | MV6-R72DZN1 | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202918938 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3G |  |  |  | VRB072H4M-3G | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 58000 | 2.72 | R-410A | 5.75
202918939 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3G |  |  |  | VRB072H4M-3G | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 58000 | 2.57 | R-410A | 5.75
202918940 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072H4M-3G |  |  |  | VRB072H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 58000 | 2.64 | R-410A | 5.75
202918839 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3Y |  |  |  | VPB096H4M-3Y | Non-Ducted Indoor Units | 92000 | 11.7 | 23.3 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202918840 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3Y |  |  |  | VPB096H4M-3Y | Ducted Indoor Units | 92000 | 11.5 | 21 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202918841 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3Y |  |  |  | VPB096H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.6 | 22.15 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202891633 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1 |  |  |  | MV6-X96DXN1 | Non-Ducted Indoor Units | 92000 | 11.7 | 23.3 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202891634 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1 |  |  |  | MV6-X96DXN1 | Ducted Indoor Units | 92000 | 11.5 | 21 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202897134 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1 |  |  |  | MV6-X96DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.6 | 22.15 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202897135 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1 |  |  |  | MV6-X96DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.6 | 22.15 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202891637 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1 |  |  |  | MV6-X96DZN1 | Non-Ducted Indoor Units | 92000 | 11.7 | 23.3 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202891638 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1 |  |  |  | MV6-X96DZN1 | Ducted Indoor Units | 92000 | 11.5 | 21 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202918836 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3G |  |  |  | VPB096H4M-3G | Non-Ducted Indoor Units | 92000 | 11.7 | 23.3 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202918837 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3G |  |  |  | VPB096H4M-3G | Ducted Indoor Units | 92000 | 11.5 | 21 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202918838 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096H4M-3G |  |  |  | VPB096H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.6 | 22.15 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202918947 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3Y |  |  |  | VRB096H4M-3Y | Non-Ducted Indoor Units | 92000 | 11.9 | 22.1 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202918948 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3Y |  |  |  | VRB096H4M-3Y | Ducted Indoor Units | 92000 | 11.6 | 20.8 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202918949 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3Y |  |  |  | VRB096H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.75 | 21.45 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202891639 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1 |  |  |  | MV6-R96DXN1 | Non-Ducted Indoor Units | 92000 | 11.9 | 22.1 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202891640 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1 |  |  |  | MV6-R96DXN1 | Ducted Indoor Units | 92000 | 11.6 | 20.8 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202897136 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1 |  |  |  | MV6-R96DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.75 | 21.45 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202897137 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1 |  |  |  | MV6-R96DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.75 | 21.45 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202891641 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1 |  |  |  | MV6-R96DZN1 | Non-Ducted Indoor Units | 92000 | 11.9 | 22.1 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202891642 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1 |  |  |  | MV6-R96DZN1 | Ducted Indoor Units | 92000 | 11.6 | 20.8 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202918944 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3G |  |  |  | VRB096H4M-3G | Non-Ducted Indoor Units | 92000 | 11.9 | 22.1 | 103000 | 3.99 | 72000 | 2.65 | R-410A | 7.6667
202918945 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3G |  |  |  | VRB096H4M-3G | Ducted Indoor Units | 92000 | 11.6 | 20.8 | 103000 | 3.8 | 72000 | 2.6 | R-410A | 7.6667
202918946 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096H4M-3G |  |  |  | VRB096H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.75 | 21.45 | 103000 | 3.89 | 72000 | 2.62 | R-410A | 7.6667
202918845 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y |  |  |  | VPB120H4M-3Y | Non-Ducted Indoor Units | 115000 | 11.3 | 21.9 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202918846 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y |  |  |  | VPB120H4M-3Y | Ducted Indoor Units | 115000 | 11.1 | 20.6 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202918847 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y |  |  |  | VPB120H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 21.25 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202897138 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 |  |  |  | MV6-X120DXN1 | Non-Ducted Indoor Units | 115000 | 11.3 | 21.9 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202897139 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 |  |  |  | MV6-X120DXN1 | Ducted Indoor Units | 115000 | 11.1 | 20.6 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202897176 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 |  |  |  | MV6-X120DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 21.25 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202897177 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 |  |  |  | MV6-X120DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 21.25 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202897144 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 |  |  |  | MV6-X120DZN1 | Non-Ducted Indoor Units | 115000 | 11.3 | 21.9 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202897145 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 |  |  |  | MV6-X120DZN1 | Ducted Indoor Units | 115000 | 11.1 | 20.6 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202918842 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G |  |  |  | VPB120H4M-3G | Non-Ducted Indoor Units | 115000 | 11.3 | 21.9 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202918843 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G |  |  |  | VPB120H4M-3G | Ducted Indoor Units | 115000 | 11.1 | 20.6 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202918844 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G |  |  |  | VPB120H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 21.25 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202918953 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y |  |  |  | VRB120H4M-3Y | Non-Ducted Indoor Units | 115000 | 11.4 | 21.3 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202918954 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y |  |  |  | VRB120H4M-3Y | Ducted Indoor Units | 115000 | 11.3 | 20.4 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202918955 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y |  |  |  | VRB120H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.35 | 20.85 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202897146 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 |  |  |  | MV6-R120DXN1 | Non-Ducted Indoor Units | 115000 | 11.4 | 21.3 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202897147 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 |  |  |  | MV6-R120DXN1 | Ducted Indoor Units | 115000 | 11.3 | 20.4 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202897178 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 |  |  |  | MV6-R120DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.35 | 20.85 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202897179 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 |  |  |  | MV6-R120DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.35 | 20.85 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
202897148 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 |  |  |  | MV6-R120DZN1 | Non-Ducted Indoor Units | 115000 | 11.4 | 21.3 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202897149 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 |  |  |  | MV6-R120DZN1 | Ducted Indoor Units | 115000 | 11.3 | 20.4 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202918950 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G |  |  |  | VRB120H4M-3G | Non-Ducted Indoor Units | 115000 | 11.4 | 21.3 | 129000 | 3.56 | 84000 | 2.47 | R-410A | 9.5833
202918951 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G |  |  |  | VRB120H4M-3G | Ducted Indoor Units | 115000 | 11.3 | 20.4 | 129000 | 3.64 | 84000 | 2.59 | R-410A | 9.5833
202918952 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G |  |  |  | VRB120H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.35 | 20.85 | 129000 | 3.6 | 84000 | 2.53 | R-410A | 9.5833
213893630 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A |  |  |  | PUHY-P72YNU-A | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213916633 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A |  |  |  | PUHY-P72YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213916634 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A |  |  |  | PUHY-P96YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213893636 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A |  |  |  | PUHY-P96YNU-A | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893637 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A |  |  |  | PUHY-P96YNU-A | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213893628 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A |  |  |  | PUHY-P72TNU-A | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213916594 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A |  |  |  | PUHY-P72TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213916595 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A |  |  |  | PUHY-P96TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213893632 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A |  |  |  | PUHY-P96TNU-A | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893633 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A |  |  |  | PUHY-P96TNU-A | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213893526 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A |  |  |  | PUHY-EP72YNU-A | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893527 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A |  |  |  | PUHY-EP72YNU-A | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213916609 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A |  |  |  | PUHY-EP72YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213916610 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A |  |  |  | PUHY-EP96YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213893534 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A |  |  |  | PUHY-EP96YNU-A | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893535 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A |  |  |  | PUHY-EP96YNU-A | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916570 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A |  |  |  | PUHY-EP72TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213893522 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A |  |  |  | PUHY-EP72TNU-A | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893523 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A |  |  |  | PUHY-EP72TNU-A | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213893530 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A |  |  |  | PUHY-EP96TNU-A | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893531 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A |  |  |  | PUHY-EP96TNU-A | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916571 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A |  |  |  | PUHY-EP96TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213916627 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A |  |  |  | PUHY-HP72YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213893842 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A |  |  |  | PUHY-HP72YNU-A | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213893559 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A |  |  |  | PUHY-HP72YNU-A | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893564 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A |  |  |  | PUHY-HP96YNU-A | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893565 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A |  |  |  | PUHY-HP96YNU-A | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213916628 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A |  |  |  | PUHY-HP96YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213916629 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A |  |  |  | PUHY-HP120YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213893542 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A |  |  |  | PUHY-HP120YNU-A | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893543 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A |  |  |  | PUHY-HP120YNU-A | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893827 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A |  |  |  | PUHY-HP72TNU-A | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213893558 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A |  |  |  | PUHY-HP72TNU-A | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213916588 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A |  |  |  | PUHY-HP72TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213916589 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A |  |  |  | PUHY-HP96TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213893560 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A |  |  |  | PUHY-HP96TNU-A | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893561 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A |  |  |  | PUHY-HP96TNU-A | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213893538 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A |  |  |  | PUHY-HP120TNU-A | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893539 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A |  |  |  | PUHY-HP120TNU-A | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213916590 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A |  |  |  | PUHY-HP120TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213893703 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN |  |  |  | TUHYP0724AN40AN | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213916795 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN |  |  |  | TUHYP0724AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213916799 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN |  |  |  | TUHYP0964AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213893706 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN |  |  |  | TUHYP0964AN40AN | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893707 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN |  |  |  | TUHYP0964AN40AN | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213893702 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN |  |  |  | TUHYP0723AN40AN | Non-Ducted Indoor Units | 69000 | 12 | 26.9 | 76000 | 4.34 | 56000 | 3 | R-410A | 5.75
213916793 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN |  |  |  | TUHYP0723AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.45 | 24.25 | 76000 | 4.15 | 56000 | 2.73 | R-410A | 5.75
213916797 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN |  |  |  | TUHYP0963AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.4 | 23.55 | 103000 | 4.16 | 76000 | 2.69 | R-410A | 7.6667
213893704 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN |  |  |  | TUHYP0963AN40AN | Ducted Indoor Units | 92000 | 11.2 | 22.3 | 103000 | 3.98 | 76000 | 2.57 | R-410A | 7.6667
213893705 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN |  |  |  | TUHYP0963AN40AN | Non-Ducted Indoor Units | 92000 | 11.6 | 24.8 | 103000 | 4.34 | 76000 | 2.82 | R-410A | 7.6667
213893642 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN |  |  |  | TUHYE0724AN40AN | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893643 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN |  |  |  | TUHYE0724AN40AN | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213916700 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN |  |  |  | TUHYE0724AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213916704 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN |  |  |  | TUHYE0964AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213893646 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN |  |  |  | TUHYE0964AN40AN | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893647 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN |  |  |  | TUHYE0964AN40AN | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916698 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN |  |  |  | TUHYE0723AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.95 | 24.65 | 76000 | 4.31 | 64000 | 2.34 | R-410A | 5.75
213893640 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN |  |  |  | TUHYE0723AN40AN | Ducted Indoor Units | 69000 | 12.2 | 22.2 | 76000 | 4.05 | 64000 | 2.29 | R-410A | 5.75
213893641 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN |  |  |  | TUHYE0723AN40AN | Non-Ducted Indoor Units | 69000 | 13.7 | 27.1 | 76000 | 4.57 | 64000 | 2.4 | R-410A | 5.75
213893644 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN |  |  |  | TUHYE0963AN40AN | Ducted Indoor Units | 92000 | 11.9 | 23.5 | 103000 | 4.04 | 80000 | 2.28 | R-410A | 7.6667
213893645 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN |  |  |  | TUHYE0963AN40AN | Non-Ducted Indoor Units | 92000 | 12.3 | 26.5 | 103000 | 4.39 | 80000 | 2.43 | R-410A | 7.6667
213916702 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN |  |  |  | TUHYE0963AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 25 | 103000 | 4.21 | 80000 | 2.35 | R-410A | 7.6667
213893682 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN |  |  |  | TUHYH0724AN40AN | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893683 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN |  |  |  | TUHYH0724AN40AN | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213916774 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN |  |  |  | TUHYH0724AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213916778 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN |  |  |  | TUHYH0964AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213893686 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN |  |  |  | TUHYH0964AN40AN | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893687 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN |  |  |  | TUHYH0964AN40AN | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213893690 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN40AN |  |  |  | TUHYH1204AN40AN | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893691 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN40AN |  |  |  | TUHYH1204AN40AN | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213916782 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN40AN |  |  |  | TUHYH1204AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213916780 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH1203AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.3 | 21.35 | 129000 | 4.01 | 93000 | 2.45 | R-410A | 9.5833
213916776 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0963AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 22.15 | 103000 | 4.17 | 87000 | 2.47 | R-410A | 7.6667
213916772 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0723AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.2 | 23.25 | 76000 | 4.21 | 64000 | 2.41 | R-410A | 5.75
213893688 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH1203AN40AN | Ducted Indoor Units | 115000 | 11.4 | 20.3 | 129000 | 3.76 | 93000 | 2.35 | R-410A | 9.5833
213893689 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH1203AN40AN | Non-Ducted Indoor Units | 115000 | 11.2 | 22.4 | 129000 | 4.26 | 93000 | 2.56 | R-410A | 9.5833
213893684 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0963AN40AN | Ducted Indoor Units | 92000 | 12.3 | 21 | 103000 | 4 | 87000 | 2.39 | R-410A | 7.6667
213893685 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0963AN40AN | Non-Ducted Indoor Units | 92000 | 12.5 | 23.3 | 103000 | 4.35 | 87000 | 2.56 | R-410A | 7.6667
213893680 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0723AN40AN | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 76000 | 4.03 | 64000 | 2.31 | R-410A | 5.75
213893681 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN |  |  |  | TUHYH0723AN40AN | Non-Ducted Indoor Units | 69000 | 12.5 | 24.7 | 76000 | 4.39 | 64000 | 2.51 | R-410A | 5.75
213896013 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YNU-A |  |  |  | PURY-P72YNU-A | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896149 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YNU-A |  |  |  | PURY-P72YNU-A | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896153 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A |  |  |  | PURY-P96YNU-A | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896147 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TNU-A |  |  |  | PURY-P72TNU-A | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896011 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TNU-A |  |  |  | PURY-P72TNU-A | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896151 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A |  |  |  | PURY-P96TNU-A | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896061 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0724AN40AN |  |  |  | TURYP0724AN40AN | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896205 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0724AN40AN |  |  |  | TURYP0724AN40AN | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896209 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN40AN |  |  |  | TURYP0964AN40AN | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896203 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0723AN40AN |  |  |  | TURYP0723AN40AN | Non-Ducted Indoor Units | 69000 | 11.9 | 23 | 76000 | 4.09 | 56000 | 2.26 | R-410A | 5.75
213896059 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0723AN40AN |  |  |  | TURYP0723AN40AN | Ducted Indoor Units | 69000 | 11.4 | 21.6 | 76000 | 3.76 | 56000 | 2.26 | R-410A | 5.75
213896207 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN40AN |  |  |  | TURYP0963AN40AN | Non-Ducted Indoor Units | 92000 | 11.5 | 23.8 | 103000 | 4.14 | 71000 | 2.26 | R-410A | 7.6667
213896101 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72YNU-A |  |  |  | PURY-EP72YNU-A | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213895981 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72YNU-A |  |  |  | PURY-EP72YNU-A | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896105 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A |  |  |  | PURY-EP96YNU-A | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896099 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72TNU-A |  |  |  | PURY-EP72TNU-A | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213895979 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP72TNU-A |  |  |  | PURY-EP72TNU-A | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896103 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A |  |  |  | PURY-EP96TNU-A | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896021 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AN40AN |  |  |  | TURYE0724AN40AN | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896157 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0724AN40AN |  |  |  | TURYE0724AN40AN | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213896161 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN40AN |  |  |  | TURYE0964AN40AN | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896155 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AN40AN |  |  |  | TURYE0723AN40AN | Non-Ducted Indoor Units | 69000 | 12.2 | 23.5 | 76000 | 4.37 | 61000 | 2.3 | R-410A | 5.75
213896019 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0723AN40AN |  |  |  | TURYE0723AN40AN | Ducted Indoor Units | 69000 | 11.8 | 22.2 | 76000 | 3.81 | 61000 | 2.25 | R-410A | 5.75
213896159 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN40AN |  |  |  | TURYE0963AN40AN | Non-Ducted Indoor Units | 92000 | 12 | 24.2 | 103000 | 4.26 | 79000 | 2.3 | R-410A | 7.6667
213896128 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A |  |  |  | PURY-HP72YNU-A | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213895997 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A |  |  |  | PURY-HP72YNU-A | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896001 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A |  |  |  | PURY-HP96YNU-A | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896133 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A |  |  |  | PURY-HP96YNU-A | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
213896125 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A |  |  |  | PURY-HP72TNU-A | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213895995 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A |  |  |  | PURY-HP72TNU-A | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213895999 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A |  |  |  | PURY-HP96TNU-A | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896131 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A |  |  |  | PURY-HP96TNU-A | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
213896189 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN40AN |  |  |  | TURYH0724AN40AN | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213896045 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN40AN |  |  |  | TURYH0724AN40AN | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896049 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN40AN |  |  |  | TURYH0964AN40AN | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896193 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN40AN |  |  |  | TURYH0964AN40AN | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
213896187 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN40AN |  |  |  | TURYH0723AN40AN | Non-Ducted Indoor Units | 69000 | 12.1 | 22.8 | 76000 | 4.09 | 64000 | 2.3 | R-410A | 5.75
213896043 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN40AN |  |  |  | TURYH0723AN40AN | Ducted Indoor Units | 69000 | 11.6 | 21.7 | 76000 | 3.76 | 64000 | 2.27 | R-410A | 5.75
213896047 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN40AN |  |  |  | TURYH0963AN40AN | Ducted Indoor Units | 92000 | 11.6 | 20.3 | 103000 | 3.88 | 87000 | 2.25 | R-410A | 7.6667
213896191 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN40AN |  |  |  | TURYH0963AN40AN | Non-Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 4.14 | 87000 | 2.3 | R-410A | 7.6667
205818928 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y |  |  |  | VPB072L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.05 | 77000 | 4.06 | 66000 | 2.52 | R-410A | 5.75
205811858 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) |  |  |  | MV6-X72DXN1C-(A) | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 66000 | 2.62 | R-410A | 5.75
205811859 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) |  |  |  | MV6-X72DXN1C-(A) | Ducted Indoor Units | 69000 | 12.1 | 21.1 | 77000 | 3.84 | 66000 | 2.43 | R-410A | 5.75
205811954 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) |  |  |  | MV6-X72DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.05 | 77000 | 4.06 | 66000 | 2.52 | R-410A | 5.75
205818832 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y |  |  |  | VPB072L4M-3Y | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 66000 | 2.62 | R-410A | 5.75
205818833 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y |  |  |  | VPB072L4M-3Y | Ducted Indoor Units | 69000 | 12.1 | 21.1 | 77000 | 3.84 | 66000 | 2.43 | R-410A | 5.75
205818834 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G |  |  |  | VPB072L4M-3G | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 66000 | 2.62 | R-410A | 5.75
205818835 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G |  |  |  | VPB072L4M-3G | Ducted Indoor Units | 69000 | 12.1 | 21.1 | 77000 | 3.84 | 66000 | 2.43 | R-410A | 5.75
205811955 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) |  |  |  | MV6-X72DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.05 | 77000 | 4.06 | 66000 | 2.52 | R-410A | 5.75
205811860 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) |  |  |  | MV6-X72DZN1C-(A) | Non-Ducted Indoor Units | 69000 | 12.9 | 23 | 77000 | 4.29 | 66000 | 2.62 | R-410A | 5.75
205811861 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) |  |  |  | MV6-X72DZN1C-(A) | Ducted Indoor Units | 69000 | 12.1 | 21.1 | 77000 | 3.84 | 66000 | 2.43 | R-410A | 5.75
205818929 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G |  |  |  | VPB072L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.5 | 22.05 | 77000 | 4.06 | 66000 | 2.52 | R-410A | 5.75
205818930 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y |  |  |  | VRB072L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 66000 | 2.51 | R-410A | 5.75
205811862 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) |  |  |  | MV6-R72DXN1C-(A) | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 66000 | 2.58 | R-410A | 5.75
205811863 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) |  |  |  | MV6-R72DXN1C-(A) | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 66000 | 2.45 | R-410A | 5.75
205811956 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) |  |  |  | MV6-R72DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 66000 | 2.51 | R-410A | 5.75
205818836 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y |  |  |  | VRB072L4M-3Y | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 66000 | 2.58 | R-410A | 5.75
205818837 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y |  |  |  | VRB072L4M-3Y | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 66000 | 2.45 | R-410A | 5.75
205818838 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G |  |  |  | VRB072L4M-3G | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 66000 | 2.58 | R-410A | 5.75
205818839 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G |  |  |  | VRB072L4M-3G | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 66000 | 2.45 | R-410A | 5.75
205811957 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) |  |  |  | MV6-R72DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 66000 | 2.51 | R-410A | 5.75
205811864 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) |  |  |  | MV6-R72DZN1C-(A) | Non-Ducted Indoor Units | 69000 | 13 | 22 | 77000 | 4.29 | 66000 | 2.58 | R-410A | 5.75
205811865 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) |  |  |  | MV6-R72DZN1C-(A) | Ducted Indoor Units | 69000 | 12.2 | 21.6 | 77000 | 3.84 | 66000 | 2.45 | R-410A | 5.75
205818931 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G |  |  |  | VRB072L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.6 | 21.8 | 77000 | 4.06 | 66000 | 2.51 | R-410A | 5.75
205818932 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y |  |  |  | VPB096L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 22.9 | 103000 | 4.03 | 86000 | 2.63 | R-410A | 7.6667
205811866 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) |  |  |  | MV6-X96DXN1C-(A) | Non-Ducted Indoor Units | 92000 | 12.2 | 23.78 | 103000 | 4.06 | 86000 | 2.6 | R-410A | 7.6667
205811867 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) |  |  |  | MV6-X96DXN1C-(A) | Ducted Indoor Units | 92000 | 11.9 | 22.02 | 103000 | 4.01 | 86000 | 2.66 | R-410A | 7.6667
205811958 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) |  |  |  | MV6-X96DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 22.9 | 103000 | 4.03 | 86000 | 2.63 | R-410A | 7.6667
205818840 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y |  |  |  | VPB096L4M-3Y | Non-Ducted Indoor Units | 92000 | 12.2 | 23.78 | 103000 | 4.06 | 86000 | 2.6 | R-410A | 7.6667
205818841 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y |  |  |  | VPB096L4M-3Y | Ducted Indoor Units | 92000 | 11.9 | 22.02 | 103000 | 4.01 | 86000 | 2.66 | R-410A | 7.6667
205818842 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G |  |  |  | VPB096L4M-3G | Non-Ducted Indoor Units | 92000 | 12.2 | 23.78 | 103000 | 4.06 | 86000 | 2.6 | R-410A | 7.6667
205818843 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G |  |  |  | VPB096L4M-3G | Ducted Indoor Units | 92000 | 11.9 | 22.02 | 103000 | 4.01 | 86000 | 2.66 | R-410A | 7.6667
205811959 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) |  |  |  | MV6-X96DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 22.9 | 103000 | 4.03 | 86000 | 2.63 | R-410A | 7.6667
205811868 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) |  |  |  | MV6-X96DZN1C-(A) | Non-Ducted Indoor Units | 92000 | 12.2 | 23.78 | 103000 | 4.06 | 86000 | 2.6 | R-410A | 7.6667
205811869 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) |  |  |  | MV6-X96DZN1C-(A) | Ducted Indoor Units | 92000 | 11.9 | 22.02 | 103000 | 4.01 | 86000 | 2.66 | R-410A | 7.6667
205818933 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G |  |  |  | VPB096L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 22.9 | 103000 | 4.03 | 86000 | 2.63 | R-410A | 7.6667
205818934 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y |  |  |  | VRB096L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 22.07 | 103000 | 4 | 86000 | 2.66 | R-410A | 7.6667
205811870 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) |  |  |  | MV6-R96DXN1C-(A) | Non-Ducted Indoor Units | 92000 | 12.55 | 22.56 | 103000 | 4.12 | 86000 | 2.7 | R-410A | 7.6667
205811871 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) |  |  |  | MV6-R96DXN1C-(A) | Ducted Indoor Units | 92000 | 12.05 | 21.58 | 103000 | 3.89 | 86000 | 2.62 | R-410A | 7.6667
205811960 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) |  |  |  | MV6-R96DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 22.07 | 103000 | 4 | 86000 | 2.66 | R-410A | 7.6667
205818844 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y |  |  |  | VRB096L4M-3Y | Non-Ducted Indoor Units | 92000 | 12.55 | 22.56 | 103000 | 4.12 | 86000 | 2.7 | R-410A | 7.6667
205818845 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y |  |  |  | VRB096L4M-3Y | Ducted Indoor Units | 92000 | 12.05 | 21.58 | 103000 | 3.89 | 86000 | 2.62 | R-410A | 7.6667
205818846 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G |  |  |  | VRB096L4M-3G | Non-Ducted Indoor Units | 92000 | 12.55 | 22.56 | 103000 | 4.12 | 86000 | 2.7 | R-410A | 7.6667
205818847 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G |  |  |  | VRB096L4M-3G | Ducted Indoor Units | 92000 | 12.05 | 21.58 | 103000 | 3.89 | 86000 | 2.62 | R-410A | 7.6667
205811961 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) |  |  |  | MV6-R96DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 22.07 | 103000 | 4 | 86000 | 2.66 | R-410A | 7.6667
205811872 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) |  |  |  | MV6-R96DZN1C-(A) | Non-Ducted Indoor Units | 92000 | 12.55 | 22.56 | 103000 | 4.12 | 86000 | 2.7 | R-410A | 7.6667
205811873 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) |  |  |  | MV6-R96DZN1C-(A) | Ducted Indoor Units | 92000 | 12.05 | 21.58 | 103000 | 3.89 | 86000 | 2.62 | R-410A | 7.6667
205818935 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G |  |  |  | VRB096L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 22.07 | 103000 | 4 | 86000 | 2.66 | R-410A | 7.6667
205818936 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y |  |  |  | VPB120L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.6 | 22.03 | 129000 | 3.85 | 110000 | 2.44 | R-410A | 9.5833
205811874 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) |  |  |  | MV6-X120DXN1C-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 22.17 | 129000 | 3.78 | 110000 | 2.42 | R-410A | 9.5833
205811875 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) |  |  |  | MV6-X120DXN1C-(A) | Ducted Indoor Units | 115000 | 11.65 | 21.9 | 129000 | 3.92 | 110000 | 2.46 | R-410A | 9.5833
205811962 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) |  |  |  | MV6-X120DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.6 | 22.03 | 129000 | 3.85 | 110000 | 2.44 | R-410A | 9.5833
205818848 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y |  |  |  | VPB120L4M-3Y | Non-Ducted Indoor Units | 115000 | 11.6 | 22.17 | 129000 | 3.78 | 110000 | 2.42 | R-410A | 9.5833
205818849 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y |  |  |  | VPB120L4M-3Y | Ducted Indoor Units | 115000 | 11.65 | 21.9 | 129000 | 3.92 | 110000 | 2.46 | R-410A | 9.5833
205818850 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G |  |  |  | VPB120L4M-3G | Non-Ducted Indoor Units | 115000 | 11.6 | 22.17 | 129000 | 3.78 | 110000 | 2.42 | R-410A | 9.5833
205818851 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G |  |  |  | VPB120L4M-3G | Ducted Indoor Units | 115000 | 11.65 | 21.9 | 129000 | 3.92 | 110000 | 2.46 | R-410A | 9.5833
205811963 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) |  |  |  | MV6-X120DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.6 | 22.03 | 129000 | 3.85 | 110000 | 2.44 | R-410A | 9.5833
205811876 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) |  |  |  | MV6-X120DZN1C-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 22.17 | 129000 | 3.78 | 110000 | 2.42 | R-410A | 9.5833
205811877 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) |  |  |  | MV6-X120DZN1C-(A) | Ducted Indoor Units | 115000 | 11.65 | 21.9 | 129000 | 3.92 | 110000 | 2.46 | R-410A | 9.5833
205818937 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G |  |  |  | VPB120L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.6 | 22.03 | 129000 | 3.85 | 110000 | 2.44 | R-410A | 9.5833
205818938 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y |  |  |  | VRB120L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.75 | 20.95 | 129000 | 3.75 | 110000 | 2.39 | R-410A | 9.5833
205811878 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) |  |  |  | MV6-R120DXN1C-(A) | Non-Ducted Indoor Units | 115000 | 11.75 | 21.1 | 129000 | 3.72 | 110000 | 2.35 | R-410A | 9.5833
205811879 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) |  |  |  | MV6-R120DXN1C-(A) | Ducted Indoor Units | 115000 | 11.8 | 20.81 | 129000 | 3.79 | 110000 | 2.44 | R-410A | 9.5833
205811964 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) |  |  |  | MV6-R120DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.75 | 20.95 | 129000 | 3.75 | 110000 | 2.39 | R-410A | 9.5833
205818852 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y |  |  |  | VRB120L4M-3Y | Non-Ducted Indoor Units | 115000 | 11.75 | 21.1 | 129000 | 3.72 | 110000 | 2.35 | R-410A | 9.5833
205818853 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y |  |  |  | VRB120L4M-3Y | Ducted Indoor Units | 115000 | 11.8 | 20.81 | 129000 | 3.79 | 110000 | 2.44 | R-410A | 9.5833
205818854 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G |  |  |  | VRB120L4M-3G | Non-Ducted Indoor Units | 115000 | 11.75 | 21.1 | 129000 | 3.72 | 110000 | 2.35 | R-410A | 9.5833
205818855 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G |  |  |  | VRB120L4M-3G | Ducted Indoor Units | 115000 | 11.8 | 20.81 | 129000 | 3.79 | 110000 | 2.44 | R-410A | 9.5833
205811965 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) |  |  |  | MV6-R120DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.75 | 20.95 | 129000 | 3.75 | 110000 | 2.39 | R-410A | 9.5833
205811880 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) |  |  |  | MV6-R120DZN1C-(A) | Non-Ducted Indoor Units | 115000 | 11.75 | 21.1 | 129000 | 3.72 | 110000 | 2.35 | R-410A | 9.5833
205811881 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) |  |  |  | MV6-R120DZN1C-(A) | Ducted Indoor Units | 115000 | 11.8 | 20.81 | 129000 | 3.79 | 110000 | 2.44 | R-410A | 9.5833
205818939 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G |  |  |  | VRB120L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.75 | 20.95 | 129000 | 3.75 | 110000 | 2.39 | R-410A | 9.5833
213896311 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72ZKMU-A |  |  |  | PURY-P72ZKMU-A | Non-Ducted Indoor Units | 69000 | 11.4 | 19.8 | 76000 | 3.46 | 56000 | 2.26 | R-410A | 5.75
213896280 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A |  |  |  | PUHY-P72ZKMU-A | Non-Ducted Indoor Units | 69000 | 12.4 | 22.2 | 76000 | 3.85 | 56000 | 2.25 | R-410A | 5.75
213896335 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A |  |  |  | PUHY-P72ZKMU-A | Ducted Indoor Units | 69000 | 12.3 | 20.2 | 76000 | 3.74 | 56000 | 2.59 | R-410A | 5.75
213916464 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A |  |  |  | PUHY-P72ZKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.35 | 21.2 | 76000 | 3.79 | 56000 | 2.42 | R-410A | 5.75
213916465 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A |  |  |  | PUHY-P96ZKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12 | 21.15 | 103000 | 3.73 | 76000 | 2.56 | R-410A | 7.6667
213896336 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A |  |  |  | PUHY-P96ZKMU-A | Ducted Indoor Units | 92000 | 11.9 | 20.1 | 103000 | 3.73 | 76000 | 2.71 | R-410A | 7.6667
213896281 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A |  |  |  | PUHY-P96ZKMU-A | Non-Ducted Indoor Units | 92000 | 12.1 | 22.2 | 103000 | 3.74 | 76000 | 2.42 | R-410A | 7.6667
213896315 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-A |  |  |  | PUHY-P120ZKMU-A | Ducted Indoor Units | 115000 | 11.4 | 19.5 | 129000 | 3.62 | 92000 | 2.51 | R-410A | 9.5833
8175947 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YLMU-A |  |  |  | PUHY-P72YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.25 | 24.85 | 76000 | 3.92 | 56000 | 2.35 | R-410A | 5.75
8175948 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YLMU-A |  |  |  | PUHY-P96YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.55 | 24.9 | 103000 | 3.82 | 76000 | 2.49 | R-410A | 7.6667
8175949 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A |  |  |  | PUHY-P120YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.8 | 23.4 | 129000 | 3.87 | 92000 | 2.34 | R-410A | 9.5
8175962 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TLMU-A |  |  |  | PUHY-P72TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.25 | 24.85 | 76000 | 3.92 | 56000 | 2.35 | R-410A | 5.75
8175963 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TLMU-A |  |  |  | PUHY-P96TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.55 | 24.9 | 103000 | 3.82 | 76000 | 2.49 | R-410A | 7.6667
8175964 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A |  |  |  | PUHY-P120TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.8 | 23.4 | 129000 | 3.87 | 92000 | 2.34 | R-410A | 9.5
8175977 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YLMU-A |  |  |  | PURY-P72YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.4 | 24.1 | 76000 | 3.72 | 56000 | 2.26 | R-410A | 5.75
8175978 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A |  |  |  | PURY-P96YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.35 | 24.3 | 103000 | 3.54 | 71000 | 2.27 | R-410A | 7.6667
8175979 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A |  |  |  | PURY-P120YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.45 | 21.75 | 129000 | 3.66 | 87000 | 2.26 | R-410A | 9.5
8175991 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TLMU-A |  |  |  | PURY-P72TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.4 | 24.1 | 76000 | 3.72 | 56000 | 2.26 | R-410A | 5.75
8175992 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A |  |  |  | PURY-P96TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.35 | 24.3 | 103000 | 3.54 | 71000 | 2.27 | R-410A | 7.6667
8175993 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A |  |  |  | PURY-P120TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.45 | 21.75 | 129000 | 3.66 | 87000 | 2.26 | R-410A | 9.5
8552536 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ120PCTJ |  |  |  | REYQ120PCTJ | Non-Ducted Indoor Units | 110000 | 12.1 | 21.3 | 129000 | 3.6 | 87000 | 2.6 | R-410A | 9.1667
8552584 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ120PCYD |  |  |  | REYQ120PCYD | Non-Ducted Indoor Units | 110000 | 12.1 | 21.3 | 129000 | 3.6 | 87000 | 2.6 | R-410A | 9.1667
8552651 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ144PCTJ |  |  |  | REYQ144PCTJ | Non-Ducted Indoor Units | 124000 | 11.2 | 18.9 | 148000 | 3.6 | 103000 | 2.4 | R-410A | 10.3333
8553652 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PCTJ |  |  |  | REYQ72PCTJ | Ducted Indoor Units | 69000 | 13.7 | 21.3 | 77000 | 3.4 | 52000 | 2.5 | R-410A | 5.75
8554086 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PCYD |  |  |  | REYQ72PCYD | Ducted Indoor Units | 69000 | 13.7 | 21.3 | 77000 | 3.4 | 52000 | 2.5 | R-410A | 5.75
8556740 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PCTJ |  |  |  | REYQ72PCTJ | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.55 | 23.2 | 77000 | 3.8 | 52000 | 2.72 | R-410A | 5.75
8556904 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PCYD |  |  |  | REYQ72PCYD | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.55 | 23.2 | 77000 | 3.8 | 52000 | 2.72 | R-410A | 5.75
8551200 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PCTJ |  |  |  | REYQ72PCTJ | Non-Ducted Indoor Units | 69000 | 15.4 | 25.1 | 77000 | 4.2 | 52000 | 2.95 | R-410A | 5.75
8551238 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PCYD |  |  |  | REYQ72PCYD | Non-Ducted Indoor Units | 69000 | 15.4 | 25.1 | 77000 | 4.2 | 52000 | 2.95 | R-410A | 5.75
9133165 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DXN1 |  |  |  | MV5-2R72DXN1 | Non-Ducted Indoor Units | 69000 | 14.1 | 24.6 | 77000 | 4.37 | 54000 | 2.72 | R-410A | 5.75
9133166 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DXN1 |  |  |  | MV5-2R72DXN1 | Ducted Indoor Units | 69000 | 13.2 | 24.2 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9133167 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DXN1 |  |  |  | MV5-2R96DXN1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9133168 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DXN1 |  |  |  | MV5-2R96DXN1 | Ducted Indoor Units | 92000 | 12.4 | 24.3 | 103000 | 3.63 | 72000 | 2.35 | R-410A | 7.6667
9133169 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R120DXN1 |  |  |  | MV5-2R120DXN1 | Non-Ducted Indoor Units | 114000 | 11.4 | 22.8 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9133170 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R120DXN1 |  |  |  | MV5-2R120DXN1 | Ducted Indoor Units | 114000 | 11.4 | 23.2 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9133181 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DZN1 |  |  |  | MV5-2R72DZN1 | Non-Ducted Indoor Units | 69000 | 14.1 | 24.6 | 77000 | 4.37 | 54000 | 2.72 | R-410A | 5.75
9133182 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DZN1 |  |  |  | MV5-2R72DZN1 | Ducted Indoor Units | 69000 | 13.2 | 24.2 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9133183 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DZN1 |  |  |  | MV5-2R96DZN1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9133184 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DZN1 |  |  |  | MV5-2R96DZN1 | Ducted Indoor Units | 92000 | 12.4 | 24.3 | 103000 | 3.63 | 72000 | 2.35 | R-410A | 7.6667
9133185 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R120DZN1 |  |  |  | MV5-2R120DZN1 | Non-Ducted Indoor Units | 114000 | 11.4 | 22.8 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9133186 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R120DZN1 |  |  |  | MV5-2R120DZN1 | Ducted Indoor Units | 114000 | 11.4 | 23.2 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9133197 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DXN1 |  |  |  | MV5-2R72DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.65 | 24.4 | 77000 | 4.11 | 54000 | 2.56 | R-410A | 5.75
9133198 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DXN1 |  |  |  | MV5-2R96DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.8 | 24 | 103000 | 3.72 | 72000 | 2.43 | R-410A | 7.6667
9133199 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R120DXN1 |  |  |  | MV5-2R120DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 23 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9133205 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R72DZN1 |  |  |  | MV5-2R72DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.65 | 24.4 | 77000 | 4.11 | 54000 | 2.56 | R-410A | 5.75
9133206 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R96DZN1 |  |  |  | MV5-2R96DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.8 | 24 | 103000 | 3.72 | 72000 | 2.43 | R-410A | 7.6667
9133207 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R120DZN1 |  |  |  | MV5-2R120DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 23 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487690 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA120RDS5-1 |  |  |  | 38VMA120RDS5-1 | Ducted Indoor Units | 114000 | 11.4 | 23.2 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487691 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA120RDS5-1 |  |  |  | 38VMA120RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 23 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487692 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA120RDS5-1 |  |  |  | 38VMA120RDS5-1 | Non-Ducted Indoor Units | 114000 | 11.4 | 22.8 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487694 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA120RDS6-1 |  |  |  | 38VMA120RDS6-1 | Ducted Indoor Units | 114000 | 11.4 | 23.2 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487695 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA120RDS6-1 |  |  |  | 38VMA120RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 23 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487696 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA120RDS6-1 |  |  |  | 38VMA120RDS6-1 | Non-Ducted Indoor Units | 114000 | 11.4 | 22.8 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487731 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 13.2 | 24.2 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9487732 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.65 | 24.4 | 77000 | 4.11 | 54000 | 2.56 | R-410A | 5.75
9487733 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 24.6 | 77000 | 4.37 | 54000 | 2.72 | R-410A | 5.75
9487735 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 13.2 | 24.2 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9487736 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.65 | 24.4 | 77000 | 4.11 | 54000 | 2.56 | R-410A | 5.75
9487737 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 24.6 | 77000 | 4.37 | 54000 | 2.72 | R-410A | 5.75
9487738 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Ducted Indoor Units | 92000 | 12.4 | 24.3 | 103000 | 3.63 | 72000 | 2.35 | R-410A | 7.6667
9487739 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.8 | 24 | 103000 | 3.72 | 72000 | 2.43 | R-410A | 7.6667
9487740 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9487741 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Ducted Indoor Units | 92000 | 12.4 | 24.3 | 103000 | 3.63 | 72000 | 2.35 | R-410A | 7.6667
9487743 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.8 | 24 | 103000 | 3.72 | 72000 | 2.43 | R-410A | 7.6667
9487744 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9487745 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA120RDS5-1 |  |  |  | 38VMA120RDS5-1 | Ducted Indoor Units | 114000 | 11.4 | 23.2 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487746 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA120RDS5-1 |  |  |  | 38VMA120RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 23 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487747 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA120RDS5-1 |  |  |  | 38VMA120RDS5-1 | Non-Ducted Indoor Units | 114000 | 11.4 | 22.8 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487748 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA120RDS6-1 |  |  |  | 38VMA120RDS6-1 | Ducted Indoor Units | 114000 | 11.4 | 23.2 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487749 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA120RDS6-1 |  |  |  | 38VMA120RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.4 | 23 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487750 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA120RDS6-1 |  |  |  | 38VMA120RDS6-1 | Non-Ducted Indoor Units | 114000 | 11.4 | 22.8 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
9487785 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Ducted Indoor Units | 69000 | 13.2 | 24.2 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9487787 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.65 | 24.4 | 77000 | 4.11 | 54000 | 2.56 | R-410A | 5.75
9487788 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS5-1 |  |  |  | 38VMA072RDS5-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 24.6 | 77000 | 4.37 | 54000 | 2.72 | R-410A | 5.75
9487789 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Ducted Indoor Units | 69000 | 13.2 | 24.2 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9487790 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.65 | 24.4 | 77000 | 4.11 | 54000 | 2.56 | R-410A | 5.75
9487791 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA072RDS6-1 |  |  |  | 38VMA072RDS6-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 24.6 | 77000 | 4.37 | 54000 | 2.72 | R-410A | 5.75
9487792 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Ducted Indoor Units | 92000 | 12.4 | 24.3 | 103000 | 3.63 | 72000 | 2.35 | R-410A | 7.6667
9487793 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.8 | 24 | 103000 | 3.72 | 72000 | 2.43 | R-410A | 7.6667
9487795 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS5-1 |  |  |  | 38VMA096RDS5-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9487796 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Ducted Indoor Units | 92000 | 12.4 | 24.3 | 103000 | 3.63 | 72000 | 2.35 | R-410A | 7.6667
9487797 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.8 | 24 | 103000 | 3.72 | 72000 | 2.43 | R-410A | 7.6667
9487798 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA096RDS6-1 |  |  |  | 38VMA096RDS6-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
208102077 | 1/1/2027 | LENNOX | HMSR-A-CB | VER096C432Y |  |  |  | VER096C432Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
205281461 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
205281462 | 1/1/2027 | LG | HMSR-A-CB | ARUM121BTE5 |  |  |  | ARUM121BTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
205281464 | 1/1/2027 | LG | HMSR-A-CB | ARUM121DTE5 |  |  |  | ARUM121DTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
206453538 | 1/1/2027 | LG | HMSR-A-CB | ARUM072BTE5 |  |  |  | ARUM072BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.2 | 26 | 77000 | 3.65 | 51000 | 2.57 | R-410A | 5.75
206453539 | 1/1/2027 | LG | HMSR-A-CB | ARUM072DTE5 |  |  |  | ARUM072DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.2 | 26 | 77000 | 3.65 | 51000 | 2.57 | R-410A | 5.75
206453540 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.95 | 29.05 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
206453542 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.95 | 29.05 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
206453543 | 1/1/2027 | LG | HMSR-A-CB | ARUM121BTE5 |  |  |  | ARUM121BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.8 | 27.1 | 129000 | 3.71 | 84000 | 2.63 | R-410A | 9.5
206453545 | 1/1/2027 | LG | HMSR-A-CB | ARUM121DTE5 |  |  |  | ARUM121DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.8 | 27.1 | 129000 | 3.71 | 84000 | 2.63 | R-410A | 9.5
208102000 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 21.5 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
208102003 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
208102009 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
208102015 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432Y |  |  |  | VEP120C432Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
208102081 | 1/1/2027 | LENNOX | HMSR-A-CB | VER120C432Y |  |  |  | VER120C432Y | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 11.25 | 23.4 | 126000 | 3.4 | 83000 | 2.25 | R-410A | 9.25
207382951 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR |  |  |  | AM072FXVAFR | Non-Ducted Indoor Units | 69000 | 13 | 29.7 | 77000 | 3.71 | 51000 | 2.73 | R-410A | 5.75
207382953 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Non-Ducted Indoor Units | 92000 | 12.7 | 28.6 | 103000 | 3.86 | 67000 | 2.65 | R-410A | 7.6667
207382954 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAFR |  |  |  | AM120FXVAFR | Non-Ducted Indoor Units | 114000 | 11.4 | 29.3 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
207385918 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR |  |  |  | AM072FXVAFR | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12 | 25.2 | 77000 | 3.58 | 51000 | 2.59 | R-410A | 5.75
207385920 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 26.55 | 103000 | 3.74 | 67000 | 2.63 | R-410A | 7.6667
207385922 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAFR |  |  |  | AM120FXVAFR | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.3 | 25.85 | 129000 | 3.43 | 84000 | 2.54 | R-410A | 9.5
207574204 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574205 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574206 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574207 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574208 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574209 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574210 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-9AB |  |  |  | CSCVA-APV120-9AB | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574212 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-9AB |  |  |  | CSCVA-APV120-9AB | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574216 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574217 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574218 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574219 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574220 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574221 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574222 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-4AB |  |  |  | CSCVA-APV120-4AB | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574224 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-4AB |  |  |  | CSCVA-APV120-4AB | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574228 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574229 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574230 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574231 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574232 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574233 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574234 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-9AH |  |  |  | CSCVA-APV120-9AH | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574236 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-9AH |  |  |  | CSCVA-APV120-9AH | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574240 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574241 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574242 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574243 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574244 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574245 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574246 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-4AH |  |  |  | CSCVA-APV120-4AH | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574248 | 1/1/2027 | ComfortStar | HMSV-A-CB | CSCVA-APV120-4AH |  |  |  | CSCVA-APV120-4AH | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574252 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574253 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574254 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AB |  |  |  | CSCVA-APV072-9AB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574255 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574256 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574257 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AB |  |  |  | CSCVA-APV096-9AB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574258 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-9AB |  |  |  | CSCVA-APV120-9AB | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574260 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-9AB |  |  |  | CSCVA-APV120-9AB | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574264 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574265 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574266 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AB |  |  |  | CSCVA-APV072-4AB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574267 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574268 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574269 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AB |  |  |  | CSCVA-APV096-4AB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574270 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-4AB |  |  |  | CSCVA-APV120-4AB | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574272 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-4AB |  |  |  | CSCVA-APV120-4AB | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574276 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574277 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574278 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-9AH |  |  |  | CSCVA-APV072-9AH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574279 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574280 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574281 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-9AH |  |  |  | CSCVA-APV096-9AH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574282 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-9AH |  |  |  | CSCVA-APV120-9AH | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574284 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-9AH |  |  |  | CSCVA-APV120-9AH | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207574288 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
207574289 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
207574290 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV072-4AH |  |  |  | CSCVA-APV072-4AH | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
207574291 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
207574292 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
207574293 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV096-4AH |  |  |  | CSCVA-APV096-4AH | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
207574294 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-4AH |  |  |  | CSCVA-APV120-4AH | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
207574296 | 1/1/2027 | VRF PLUS | HMSV-A-CB | CSCVA-APV120-4AH |  |  |  | CSCVA-APV120-4AH | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
207699040 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.32 | 103000 | 2.45 | R-410A | 7.6667
207699044 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.3 | 28.85 | 103000 | 3.95 | 103000 | 2.41 | R-410A | 7.6667
210691220 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHA |  |  |  | AVWT-72FHFSHA | Ducted Indoor Units | 69000 | 11.4 | 21.9 | 75000 | 3.4 | 52500 | 2.25 | R-410A | 5.75
210691221 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA |  |  |  | AVWT-96FHFSHA | Ducted Indoor Units | 92000 | 11.1 | 21.8 | 100000 | 3.51 | 70000 | 2.32 | R-410A | 7.6667
210691222 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA |  |  |  | AVWT-96FHFSHA | Non-Ducted Indoor Units | 92000 | 13.2 | 29.7 | 100000 | 3.98 | 70000 | 2.57 | R-410A | 7.6667
210691223 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA |  |  |  | AVWT-96FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.15 | 25.75 | 100000 | 3.74 | 70000 | 2.44 | R-410A | 7.6667
210691224 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA |  |  |  | AVWT-120FHFSHA | Ducted Indoor Units | 114000 | 11.1 | 21.6 | 126000 | 3.42 | 81000 | 2.32 | R-410A | 9.5
210691225 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA |  |  |  | AVWT-120FHFSHA | Non-Ducted Indoor Units | 114000 | 13 | 29.4 | 126000 | 4.17 | 81000 | 2.73 | R-410A | 9.5
210691226 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA |  |  |  | AVWT-120FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.05 | 25.5 | 126000 | 3.79 | 81000 | 2.52 | R-410A | 9.5
210713380 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHA |  |  |  | AVWT-72FHFSHA | Non-Ducted Indoor Units | 69000 | 13.9 | 29.1 | 75000 | 4.03 | 52500 | 2.61 | R-410A | 5.75
210713381 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHA |  |  |  | AVWT-72FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.65 | 25.5 | 75000 | 3.71 | 52500 | 2.43 | R-410A | 5.75
210720743 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Non-Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
210845528 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
210845822 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
212511003 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Non-Ducted Indoor Units | 69000 | 14.8 | 29 | 77000 | 4.23 | 56000 | 2.68 | R-410A | 5.75
212511004 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Ducted Indoor Units | 92000 | 13.3 | 22.3 | 103000 | 4 | 76000 | 2.83 | R-410A | 7.6667
212511005 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Ducted Indoor Units | 114000 | 12.1 | 21.6 | 129000 | 3.89 | 92000 | 2.75 | R-410A | 9.5
212511024 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Ducted Indoor Units | 69000 | 13.5 | 22.7 | 77000 | 3.79 | 56000 | 2.74 | R-410A | 5.75
212511025 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Non-Ducted Indoor Units | 92000 | 12.6 | 28 | 103000 | 4.5 | 76000 | 2.84 | R-410A | 7.6667
212511026 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Non-Ducted Indoor Units | 114000 | 12.8 | 25.1 | 129000 | 3.99 | 92000 | 2.79 | R-410A | 9.5
212511039 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Non-Ducted Indoor Units | 69000 | 14.8 | 29 | 77000 | 4.23 | 56000 | 2.68 | R-410A | 5.75
212511040 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Ducted Indoor Units | 92000 | 13.3 | 22.3 | 103000 | 4 | 76000 | 2.83 | R-410A | 7.6667
212511041 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Ducted Indoor Units | 114000 | 12.1 | 21.6 | 129000 | 3.89 | 92000 | 2.75 | R-410A | 9.5
212511061 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Ducted Indoor Units | 69000 | 13.5 | 22.7 | 77000 | 3.79 | 56000 | 2.74 | R-410A | 5.75
212511062 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Non-Ducted Indoor Units | 92000 | 12.6 | 28 | 103000 | 4.5 | 76000 | 2.84 | R-410A | 7.6667
212511063 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Non-Ducted Indoor Units | 114000 | 12.8 | 25.1 | 129000 | 3.99 | 92000 | 2.79 | R-410A | 9.5
212511071 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Non-Ducted Indoor Units | 69000 | 14.6 | 26.6 | 77000 | 3.67 | 56000 | 2.73 | R-410A | 5.75
212511072 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Ducted Indoor Units | 69000 | 12.6 | 19.5 | 77000 | 3.42 | 56000 | 2.44 | R-410A | 5.75
212511073 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Non-Ducted Indoor Units | 69000 | 14.6 | 26.6 | 77000 | 3.67 | 56000 | 2.73 | R-410A | 5.75
212511074 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Ducted Indoor Units | 69000 | 12.6 | 19.5 | 77000 | 3.42 | 56000 | 2.44 | R-410A | 5.75
212511075 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Non-Ducted Indoor Units | 92000 | 12.5 | 28.3 | 103000 | 3.85 | 76000 | 2.61 | R-410A | 7.6667
212511076 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Ducted Indoor Units | 92000 | 11.7 | 21.4 | 103000 | 3.71 | 76000 | 2.54 | R-410A | 7.6667
212511077 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Non-Ducted Indoor Units | 92000 | 12.5 | 28.3 | 103000 | 3.85 | 76000 | 2.61 | R-410A | 7.6667
212511078 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Ducted Indoor Units | 92000 | 11.7 | 21.4 | 103000 | 3.71 | 76000 | 2.54 | R-410A | 7.6667
212511079 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Non-Ducted Indoor Units | 114000 | 11.8 | 27.5 | 129000 | 3.61 | 92000 | 2.44 | R-410A | 9.5
212511080 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Ducted Indoor Units | 114000 | 11.9 | 20 | 129000 | 3.48 | 92000 | 2.46 | R-410A | 9.5
212511081 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Non-Ducted Indoor Units | 114000 | 11.8 | 27.5 | 129000 | 3.61 | 92000 | 2.44 | R-410A | 9.5
212511082 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Ducted Indoor Units | 114000 | 11.9 | 20 | 129000 | 3.48 | 92000 | 2.46 | R-410A | 9.5
212512454 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.15 | 25.85 | 77000 | 4.01 | 56000 | 2.71 | R-410A | 5.75
212512455 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
212512456 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
212512457 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.95 | 25.15 | 103000 | 4.25 | 76000 | 2.83 | R-410A | 7.6667
212512458 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 24.85 | 103000 | 3.78 | 76000 | 2.57 | R-410A | 7.6667
212512459 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 24.85 | 103000 | 3.78 | 76000 | 2.57 | R-410A | 7.6667
212512460 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.45 | 23.35 | 129000 | 3.94 | 92000 | 2.77 | R-410A | 9.5
212512461 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.85 | 23.75 | 129000 | 3.54 | 92000 | 2.45 | R-410A | 9.5
212512462 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.85 | 23.75 | 129000 | 3.54 | 92000 | 2.45 | R-410A | 9.5
212512523 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.15 | 25.85 | 77000 | 4.01 | 56000 | 2.71 | R-410A | 5.75
212512524 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.95 | 25.15 | 103000 | 4.25 | 76000 | 2.83 | R-410A | 7.6667
212512525 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.45 | 23.35 | 129000 | 3.94 | 92000 | 2.77 | R-410A | 9.5
212512538 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
212924814 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB |  |  |  | AVWT-72FFFSHB | Ducted Indoor Units | 72000 | 12 | 19.5 | 81000 | 3.65 | 52500 | 2.45 | R-410A | 6
212924815 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB |  |  |  | AVWT-72FFFSHB | Non-Ducted Indoor Units | 72000 | 12.5 | 23 | 81000 | 4.25 | 52500 | 2.67 | R-410A | 6
212924816 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB |  |  |  | AVWT-96FFFSHB | Ducted Indoor Units | 96000 | 11.7 | 19.7 | 103000 | 3.75 | 70000 | 2.45 | R-410A | 8
212924817 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB |  |  |  | AVWT-96FFFSHB | Non-Ducted Indoor Units | 96000 | 12.5 | 22.6 | 103000 | 4.05 | 70000 | 2.55 | R-410A | 8
212924818 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB |  |  |  | AVWT-120FFFSHB | Ducted Indoor Units | 120000 | 12 | 20.65 | 129000 | 3.71 | 81000 | 2.4 | R-410A | 10
212924819 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB |  |  |  | AVWT-120FFFSHB | Non-Ducted Indoor Units | 120000 | 12 | 22.1 | 129000 | 3.9 | 81000 | 2.53 | R-410A | 10
212924821 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB |  |  |  | AVWT-72FHFSHB | Ducted Indoor Units | 72000 | 12 | 19.5 | 81000 | 3.65 | 52500 | 2.45 | R-410A | 6
212924822 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB |  |  |  | AVWT-72FHFSHB | Non-Ducted Indoor Units | 72000 | 12.5 | 23 | 81000 | 4.25 | 52500 | 2.67 | R-410A | 6
212924823 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB |  |  |  | AVWT-96FHFSHB | Ducted Indoor Units | 96000 | 11.7 | 19.7 | 103000 | 3.75 | 70000 | 2.45 | R-410A | 8
212924824 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB |  |  |  | AVWT-96FHFSHB | Non-Ducted Indoor Units | 96000 | 12.5 | 22.6 | 103000 | 4.05 | 70000 | 2.55 | R-410A | 8
212924825 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB |  |  |  | AVWT-120FHFSHB | Ducted Indoor Units | 120000 | 12 | 20.65 | 129000 | 3.71 | 81000 | 2.4 | R-410A | 10
212924826 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB |  |  |  | AVWT-120FHFSHB | Non-Ducted Indoor Units | 120000 | 12 | 22.1 | 129000 | 3.9 | 81000 | 2.53 | R-410A | 10
212924829 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB |  |  |  | AVWT-72FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 72000 | 12.25 | 21.25 | 81000 | 3.95 | 52500 | 2.56 | R-410A | 6
212924830 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB |  |  |  | AVWT-96FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 96000 | 12.1 | 21.15 | 103000 | 3.9 | 70000 | 2.5 | R-410A | 8
212924831 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB |  |  |  | AVWT-120FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 120000 | 12 | 21.37 | 129000 | 3.8 | 81000 | 2.46 | R-410A | 10
212924832 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB |  |  |  | AVWT-72FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 72000 | 12.25 | 21.25 | 81000 | 3.95 | 52500 | 2.56 | R-410A | 6
212924833 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB |  |  |  | AVWT-96FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 96000 | 12.1 | 21.15 | 103000 | 3.9 | 70000 | 2.5 | R-410A | 8
212924834 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB |  |  |  | AVWT-120FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 120000 | 12 | 21.37 | 129000 | 3.8 | 81000 | 2.46 | R-410A | 10
213500518 | 1/1/2027 | HISENSE | HMSV-A-CB | AVW-96H8FH3H2 |  |  |  | AVW-96H8FH3H2 | Non-Ducted Indoor Units | 92000 | 11.5 | 25.4 | 103000 | 3.6 | 70000 | 2.4 | R-410A | 7.6667
213500519 | 1/1/2027 | HISENSE | HMSV-A-CB | AVW-76H8FH3H2 |  |  |  | AVW-76H8FH3H2 | Non-Ducted Indoor Units | 72000 | 11.6 | 26.5 | 81000 | 3.7 | 52500 | 2.6 | R-410A | 6
213500525 | 1/1/2027 | HISENSE | HMSV-A-CB | AVW-96H8FH3H2 |  |  |  | AVW-96H8FH3H2 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.25 | 21.75 | 103000 | 3.45 | 70000 | 2.35 | R-410A | 7.6667
213500526 | 1/1/2027 | HISENSE | HMSV-A-CB | AVW-76H8FH3H2 |  |  |  | AVW-76H8FH3H2 | Mixed Ducted and Non-Ducted Indoor Units | 72000 | 11.35 | 22.55 | 81000 | 3.55 | 52500 | 2.5 | R-410A | 6
200084023 | 1/1/2027 | MAMMOTH | HMSR-A-CB | V5BV-R120WMBK |  |  |  | V5BV-R120WMBK | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 11.25 | 23.4 | 126000 | 3.4 | 83000 | 2.25 | R-410A | 9.25
200084024 | 1/1/2027 | REZNOR | HMSR-A-CB | V5BV-R120WMBK |  |  |  | V5BV-R120WMBK | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 11.25 | 23.4 | 126000 | 3.4 | 83000 | 2.25 | R-410A | 9.25
200084025 | 1/1/2027 | NORTEK | HMSR-A-CB | V5BV-R120WMBK |  |  |  | V5BV-R120WMBK | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 11.25 | 23.4 | 126000 | 3.4 | 83000 | 2.25 | R-410A | 9.25
200084014 | 1/1/2027 | MAMMOTH | HMSR-A-CB | V5BV-R96WMBK |  |  |  | V5BV-R96WMBK | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
200084015 | 1/1/2027 | REZNOR | HMSR-A-CB | V5BV-R96WMBK |  |  |  | V5BV-R96WMBK | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
200084016 | 1/1/2027 | NORTEK | HMSR-A-CB | V5BV-R96WMBK |  |  |  | V5BV-R96WMBK | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
10306463 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H6CDC712(A) |  |  |  | IOV072H6CDC712(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 21.5 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
10479770 | 1/1/2027 | GREE | HMSV-A-CB | GMV-V96W/A-F(U) |  |  |  | GMV-V96W/A-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 20 | 103000 | 3.5 | 70000 | 2.25 | R-410A | 7.6667
10515227 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* |  |  |  | RELQ72TATJ* | Non-Ducted Indoor Units | 69000 | 15.8 | 24 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
10515228 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* |  |  |  | RELQ72TAYD* | Non-Ducted Indoor Units | 69000 | 15.8 | 24 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
10515229 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* |  |  |  | RELQ96TATJ* | Non-Ducted Indoor Units | 92000 | 15.3 | 24.8 | 103000 | 4.23 | 86000 | 2.5 | R-410A | 7.6667
10515230 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* |  |  |  | RELQ96TAYD* | Non-Ducted Indoor Units | 92000 | 15.3 | 24.8 | 103000 | 4.23 | 86000 | 2.5 | R-410A | 7.6667
10515231 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* |  |  |  | RELQ120TATJ* | Non-Ducted Indoor Units | 114000 | 13.7 | 23.4 | 129000 | 3.98 | 110000 | 2.25 | R-410A | 9.5
10515232 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* |  |  |  | RELQ120TAYD* | Non-Ducted Indoor Units | 114000 | 13.7 | 23.4 | 129000 | 3.98 | 110000 | 2.25 | R-410A | 9.5
10515237 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* |  |  |  | RELQ72TATJ* | Ducted Indoor Units | 69000 | 13.7 | 20.8 | 77000 | 3.68 | 58000 | 2.3 | R-410A | 5.75
10515238 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* |  |  |  | RELQ72TAYD* | Ducted Indoor Units | 69000 | 13.7 | 20.8 | 77000 | 3.68 | 58000 | 2.3 | R-410A | 5.75
10515239 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* |  |  |  | RELQ96TATJ* | Ducted Indoor Units | 92000 | 12.5 | 19.1 | 103000 | 3.42 | 86000 | 2.25 | R-410A | 7.6667
10515240 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* |  |  |  | RELQ96TAYD* | Ducted Indoor Units | 92000 | 12.5 | 19.1 | 103000 | 3.42 | 86000 | 2.25 | R-410A | 7.6667
10515241 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* |  |  |  | RELQ120TATJ* | Ducted Indoor Units | 114000 | 12.4 | 19.6 | 129000 | 3.51 | 110000 | 2.25 | R-410A | 9.5
10515242 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* |  |  |  | RELQ120TAYD* | Ducted Indoor Units | 114000 | 12.4 | 19.6 | 129000 | 3.51 | 110000 | 2.25 | R-410A | 9.5
10515247 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* |  |  |  | RELQ72TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 22.4 | 77000 | 3.99 | 58000 | 2.4 | R-410A | 5.75
10515248 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* |  |  |  | RELQ72TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 22.4 | 77000 | 3.99 | 58000 | 2.4 | R-410A | 5.75
10515249 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* |  |  |  | RELQ96TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.9 | 21.95 | 103000 | 3.82 | 86000 | 2.37 | R-410A | 7.6667
10515250 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* |  |  |  | RELQ96TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.9 | 21.95 | 103000 | 3.82 | 86000 | 2.37 | R-410A | 7.6667
10515251 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* |  |  |  | RELQ120TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.05 | 21.5 | 129000 | 3.74 | 110000 | 2.25 | R-410A | 9.5
10515252 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* |  |  |  | RELQ120TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.05 | 21.5 | 129000 | 3.74 | 110000 | 2.25 | R-410A | 9.5
10594255 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DXN1-(A) |  |  |  | MV5-R72DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
10594256 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DZN1-(A) |  |  |  | MV5-R72DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
10594257 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DXN1-(A) |  |  |  | MV5-X72DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
10594258 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DZN1-(A) |  |  |  | MV5-X72DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.9 | 23.15 | 77000 | 3.97 | 54000 | 2.53 | R-410A | 5.75
10267502 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) |  |  |  | GMV-72WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 21.5 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
10306433 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) |  |  |  | IOV072H3CDC712(A) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
10306436 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) |  |  |  | IOV096H3CDC716(A) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
10306439 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC720(A) |  |  |  | IOV120H3CDC720(A) | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
10340639 | 1/1/2027 | GREE | HMSV-A-CB | GMV-Y96WM/A-F(U) |  |  |  | GMV-Y96WM/A-F(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 22 | 103000 | 3.5 | 67000 | 2.3 | R-410A | 7.6667
10340640 | 1/1/2027 | GREE | HMSV-A-CB | GMV-Y96WM/A-F(U) |  |  |  | GMV-Y96WM/A-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.2 | 21 | 103000 | 3.4 | 67000 | 2.27 | R-410A | 7.6667
201874139 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A |  |  |  | PUHY-P120TLMU-A | Non-Ducted Indoor Units | 114000 | 14.4 | 24.9 | 129000 | 4.03 | 92000 | 2.3 | R-410A | 9.5
201874140 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A |  |  |  | PUHY-P120YLMU-A | Non-Ducted Indoor Units | 114000 | 14.4 | 24.9 | 129000 | 4.03 | 92000 | 2.3 | R-410A | 9.5
201874147 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TLMU-A |  |  |  | PUHY-P72TLMU-A | Non-Ducted Indoor Units | 69000 | 14.8 | 26.6 | 76000 | 4.01 | 56000 | 2.25 | R-410A | 5.75
201874148 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YLMU-A |  |  |  | PUHY-P72YLMU-A | Non-Ducted Indoor Units | 69000 | 14.8 | 26.6 | 76000 | 4.01 | 56000 | 2.25 | R-410A | 5.75
201874150 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TLMU-A |  |  |  | PUHY-P96TLMU-A | Non-Ducted Indoor Units | 92000 | 14 | 26.7 | 103000 | 3.85 | 76000 | 2.42 | R-410A | 7.6667
201874151 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YLMU-A |  |  |  | PUHY-P96YLMU-A | Non-Ducted Indoor Units | 92000 | 14 | 26.7 | 103000 | 3.85 | 76000 | 2.42 | R-410A | 7.6667
201874025 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A |  |  |  | PUHY-P120TKMU-A | Ducted Indoor Units | 114000 | 12.5 | 19.1 | 129000 | 3.66 | 92000 | 2.51 | R-410A | 9.5
201874026 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A |  |  |  | PUHY-P120TLMU-A | Ducted Indoor Units | 114000 | 13.2 | 21.9 | 129000 | 3.71 | 92000 | 2.38 | R-410A | 9.5
201874027 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A |  |  |  | PUHY-P120YKMU-A | Ducted Indoor Units | 114000 | 12.5 | 19.1 | 129000 | 3.66 | 92000 | 2.51 | R-410A | 9.5
201874028 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A |  |  |  | PUHY-P120YLMU-A | Ducted Indoor Units | 114000 | 13.2 | 21.9 | 129000 | 3.71 | 92000 | 2.38 | R-410A | 9.5
201874035 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TKMU-A |  |  |  | PUHY-P72TKMU-A | Ducted Indoor Units | 69000 | 13 | 19.8 | 76000 | 3.83 | 56000 | 2.59 | R-410A | 5.75
201874036 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TLMU-A |  |  |  | PUHY-P72TLMU-A | Ducted Indoor Units | 69000 | 13.7 | 23.1 | 76000 | 3.84 | 56000 | 2.46 | R-410A | 5.75
201874037 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YKMU-A |  |  |  | PUHY-P72YKMU-A | Ducted Indoor Units | 69000 | 13 | 19.8 | 76000 | 3.83 | 56000 | 2.59 | R-410A | 5.75
201874038 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YLMU-A |  |  |  | PUHY-P72YLMU-A | Ducted Indoor Units | 69000 | 13.7 | 23.1 | 76000 | 3.84 | 56000 | 2.46 | R-410A | 5.75
201874039 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TKMU-A |  |  |  | PUHY-P96TKMU-A | Ducted Indoor Units | 92000 | 12.6 | 19.7 | 103000 | 3.95 | 76000 | 2.71 | R-410A | 7.6667
201874040 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TLMU-A |  |  |  | PUHY-P96TLMU-A | Ducted Indoor Units | 92000 | 13.1 | 23.1 | 103000 | 3.79 | 76000 | 2.57 | R-410A | 7.6667
201874041 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YKMU-A |  |  |  | PUHY-P96YKMU-A | Ducted Indoor Units | 92000 | 12.6 | 19.7 | 103000 | 3.95 | 76000 | 2.71 | R-410A | 7.6667
201874042 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YLMU-A |  |  |  | PUHY-P96YLMU-A | Ducted Indoor Units | 92000 | 13.1 | 23.1 | 103000 | 3.79 | 76000 | 2.57 | R-410A | 7.6667
201902897 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 21.5 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
202515347 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 |  |  |  | ARUN072DTE4 | Non-Ducted Indoor Units | 69000 | 13.4 | 27.5 | 77000 | 3.8 | 51000 | 2.6 | R-410A | 5.75
202515348 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 |  |  |  | ARUN072DTE4 | Ducted Indoor Units | 69000 | 13 | 23.5 | 77000 | 3.82 | 51000 | 2.7 | R-410A | 5.75
202515434 | 1/1/2027 | LG | HMSR-A-CB | ARUM072BTE5 |  |  |  | ARUM072BTE5 | Non-Ducted Indoor Units | 69000 | 13.4 | 28.4 | 77000 | 3.83 | 51000 | 2.66 | R-410A | 5.75
202515520 | 1/1/2027 | LG | HMSR-A-CB | ARUM072BTE5 |  |  |  | ARUM072BTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
202515521 | 1/1/2027 | LG | HMSR-A-CB | ARUM072DTE5 |  |  |  | ARUM072DTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
202515522 | 1/1/2027 | LG | HMSR-A-CB | ARUM072DTE5 |  |  |  | ARUM072DTE5 | Non-Ducted Indoor Units | 69000 | 13.4 | 28.4 | 77000 | 3.83 | 51000 | 2.66 | R-410A | 5.75
202515523 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 |  |  |  | ARUN072BTE4 | Ducted Indoor Units | 69000 | 13 | 23.5 | 77000 | 3.82 | 51000 | 2.7 | R-410A | 5.75
202516169 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
202516171 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
202516172 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 |  |  |  | ARUN096DTE4 | Ducted Indoor Units | 92000 | 12.7 | 25 | 103000 | 3.73 | 67000 | 2.71 | R-410A | 7.6667
202516173 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 |  |  |  | ARUN096DTE4 | Non-Ducted Indoor Units | 92000 | 13.5 | 32 | 103000 | 3.98 | 67000 | 2.66 | R-410A | 7.6667
202516175 | 1/1/2027 | LG | HMSR-A-CB | ARUM121BTE5 |  |  |  | ARUM121BTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
202516176 | 1/1/2027 | LG | HMSR-A-CB | ARUM121BTE5 |  |  |  | ARUM121BTE5 | Non-Ducted Indoor Units | 114000 | 13.1 | 29.6 | 129000 | 3.97 | 84000 | 2.74 | R-410A | 9.5
202516178 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DTE4 |  |  |  | ARUN121DTE4 | Ducted Indoor Units | 114000 | 12.6 | 23 | 129000 | 3.53 | 84000 | 2.57 | R-410A | 9.5
202516179 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DTE4 |  |  |  | ARUN121DTE4 | Non-Ducted Indoor Units | 114000 | 13.2 | 24.3 | 129000 | 3.68 | 84000 | 2.57 | R-410A | 9.5
202517456 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BTE4 |  |  |  | ARUB121BTE4 | Ducted Indoor Units | 114000 | 12.6 | 23.5 | 129000 | 3.53 | 84000 | 2.57 | R-410A | 9.5
202517457 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BTE4 |  |  |  | ARUB121BTE4 | Non-Ducted Indoor Units | 114000 | 13.2 | 24.3 | 129000 | 3.68 | 84000 | 2.57 | R-410A | 9.5
202517458 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DTE4 |  |  |  | ARUB121DTE4 | Ducted Indoor Units | 114000 | 12.6 | 23.5 | 129000 | 3.53 | 84000 | 2.57 | R-410A | 9.5
202517459 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DTE4 |  |  |  | ARUB121DTE4 | Non-Ducted Indoor Units | 114000 | 13.2 | 24.3 | 129000 | 3.68 | 84000 | 2.57 | R-410A | 9.5
202517460 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BTE4 |  |  |  | ARUN121BTE4 | Ducted Indoor Units | 114000 | 12.6 | 23 | 129000 | 3.53 | 84000 | 2.57 | R-410A | 9.5
202517461 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BTE4 |  |  |  | ARUN121BTE4 | Non-Ducted Indoor Units | 114000 | 13.2 | 24.3 | 129000 | 3.68 | 84000 | 2.57 | R-410A | 9.5
202524541 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
202524542 | 1/1/2027 | LG | HMSR-A-CB | ARUM096DTE5 |  |  |  | ARUM096DTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
202524543 | 1/1/2027 | LG | HMSR-A-CB | ARUM121DTE5 |  |  |  | ARUM121DTE5 | Non-Ducted Indoor Units | 114000 | 13.1 | 29.6 | 129000 | 3.97 | 84000 | 2.74 | R-410A | 9.5
202524544 | 1/1/2027 | LG | HMSR-A-CB | ARUM121DTE5 |  |  |  | ARUM121DTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
202534251 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 |  |  |  | ARUB096DTE4 | Non-Ducted Indoor Units | 92000 | 13.5 | 32 | 103000 | 3.98 | 67000 | 2.66 | R-410A | 7.6667
202534253 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 |  |  |  | ARUN096BTE4 | Non-Ducted Indoor Units | 92000 | 13.5 | 32 | 103000 | 3.98 | 67000 | 2.66 | R-410A | 7.6667
202534254 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 |  |  |  | ARUN096BTE4 | Ducted Indoor Units | 92000 | 12.7 | 25 | 103000 | 3.73 | 67000 | 2.71 | R-410A | 7.6667
202534255 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 |  |  |  | ARUB096DTE4 | Ducted Indoor Units | 92000 | 12.7 | 25 | 103000 | 3.73 | 67000 | 2.71 | R-410A | 7.6667
202534256 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 |  |  |  | ARUB096BTE4 | Ducted Indoor Units | 92000 | 12.7 | 25 | 103000 | 3.73 | 67000 | 2.71 | R-410A | 7.6667
202534257 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 |  |  |  | ARUB096BTE4 | Non-Ducted Indoor Units | 92000 | 13.5 | 32 | 103000 | 3.98 | 67000 | 2.66 | R-410A | 7.6667
203297452 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A |  |  |  | PURY-P120TLMU-A | Ducted Indoor Units | 114000 | 12.8 | 19.5 | 129000 | 3.49 | 87000 | 2.26 | R-410A | 9.5
203297456 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A |  |  |  | PURY-P120YLMU-A | Ducted Indoor Units | 114000 | 12.8 | 19.5 | 129000 | 3.49 | 87000 | 2.26 | R-410A | 9.5
203297553 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TKMU-A |  |  |  | PURY-P72TKMU-A | Ducted Indoor Units | 69000 | 13.9 | 20 | 76000 | 3.75 | 56000 | 2.58 | R-410A | 5.75
203297554 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TKMU-A |  |  |  | PURY-P72TKMU-A | Non-Ducted Indoor Units | 69000 | 15.5 | 20.9 | 76000 | 3.66 | 56000 | 2.45 | R-410A | 5.75
203297555 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TLMU-A |  |  |  | PURY-P72TLMU-A | Non-Ducted Indoor Units | 69000 | 13.3 | 25.1 | 76000 | 3.8 | 56000 | 2.26 | R-410A | 5.75
203297558 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YKMU-A |  |  |  | PURY-P72YKMU-A | Ducted Indoor Units | 69000 | 13.9 | 20 | 76000 | 3.75 | 56000 | 2.58 | R-410A | 5.75
203297559 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YKMU-A |  |  |  | PURY-P72YKMU-A | Non-Ducted Indoor Units | 69000 | 15.5 | 20.9 | 76000 | 3.66 | 56000 | 2.45 | R-410A | 5.75
203297560 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YLMU-A |  |  |  | PURY-P72YLMU-A | Ducted Indoor Units | 69000 | 13.5 | 21.9 | 76000 | 3.59 | 56000 | 2.26 | R-410A | 5.75
203297561 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YLMU-A |  |  |  | PURY-P72YLMU-A | Non-Ducted Indoor Units | 69000 | 13.3 | 25.1 | 76000 | 3.8 | 56000 | 2.26 | R-410A | 5.75
203297566 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A |  |  |  | PURY-P96TKMU-A | Non-Ducted Indoor Units | 92000 | 13.6 | 20.1 | 103000 | 3.66 | 76000 | 2.46 | R-410A | 7.6667
203297567 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A |  |  |  | PURY-P96TLMU-A | Non-Ducted Indoor Units | 92000 | 12.7 | 24.5 | 103000 | 3.55 | 71000 | 2.26 | R-410A | 7.6667
203297570 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A |  |  |  | PURY-P96YKMU-A | Non-Ducted Indoor Units | 92000 | 13.6 | 20.1 | 103000 | 3.66 | 76000 | 2.46 | R-410A | 7.6667
203297571 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A |  |  |  | PURY-P96YLMU-A | Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 3.49 | 71000 | 2.25 | R-410A | 7.6667
203297572 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A |  |  |  | PURY-P96YLMU-A | Non-Ducted Indoor Units | 92000 | 12.7 | 24.5 | 103000 | 3.55 | 71000 | 2.26 | R-410A | 7.6667
203300875 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A |  |  |  | PURY-P96TKMU-A | Ducted Indoor Units | 92000 | 12.2 | 18.9 | 103000 | 3.6 | 76000 | 2.44 | R-410A | 7.6667
203300876 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A |  |  |  | PURY-P96YKMU-A | Ducted Indoor Units | 92000 | 12.2 | 18.9 | 103000 | 3.6 | 76000 | 2.44 | R-410A | 7.6667
203300877 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A |  |  |  | PURY-P96TLMU-A | Ducted Indoor Units | 92000 | 12 | 23.2 | 103000 | 3.49 | 71000 | 2.25 | R-410A | 7.6667
203300907 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TLMU-A |  |  |  | PURY-P72TLMU-A | Ducted Indoor Units | 69000 | 13.5 | 21.9 | 76000 | 3.59 | 56000 | 2.26 | R-410A | 5.75
203301894 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TKMU-A |  |  |  | PURY-P120TKMU-A | Non-Ducted Indoor Units | 114000 | 12.2 | 20.3 | 129000 | 3.57 | 92000 | 2.4 | R-410A | 9.5
203301895 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YKMU-A |  |  |  | PURY-P120YKMU-A | Non-Ducted Indoor Units | 114000 | 12.2 | 20.3 | 129000 | 3.57 | 92000 | 2.4 | R-410A | 9.5
203301896 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A |  |  |  | PURY-P120TLMU-A | Non-Ducted Indoor Units | 114000 | 14.1 | 23.6 | 129000 | 3.8 | 87000 | 2.26 | R-410A | 9.5
203301897 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A |  |  |  | PURY-P120YLMU-A | Non-Ducted Indoor Units | 114000 | 14.1 | 23.6 | 129000 | 3.8 | 87000 | 2.26 | R-410A | 9.5
203334936 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XATJ* |  |  |  | REYQ72XATJ* | Non-Ducted Indoor Units | 69000 | 15.8 | 25.2 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
203334937 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* |  |  |  | REYQ96XATJ* | Non-Ducted Indoor Units | 92000 | 14.6 | 27.8 | 103000 | 4.23 | 72000 | 2.63 | R-410A | 7.6667
203334938 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* |  |  |  | REYQ120XATJ* | Non-Ducted Indoor Units | 114000 | 13.2 | 25.5 | 129000 | 3.81 | 88000 | 2.54 | R-410A | 9.5
203334953 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYD* |  |  |  | REYQ72XAYD* | Non-Ducted Indoor Units | 69000 | 15.8 | 25.2 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
203334954 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* |  |  |  | REYQ96XAYD* | Non-Ducted Indoor Units | 92000 | 14.6 | 27.8 | 103000 | 4.23 | 72000 | 2.63 | R-410A | 7.6667
203334955 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* |  |  |  | REYQ120XAYD* | Non-Ducted Indoor Units | 114000 | 13.2 | 25.5 | 129000 | 3.81 | 88000 | 2.54 | R-410A | 9.5
203334970 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYC* |  |  |  | REYQ72XAYC* | Non-Ducted Indoor Units | 69000 | 15.8 | 25.2 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
203334971 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* |  |  |  | REYQ96XAYC* | Non-Ducted Indoor Units | 92000 | 14.6 | 27.8 | 103000 | 4.23 | 72000 | 2.63 | R-410A | 7.6667
203334972 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* |  |  |  | REYQ120XAYC* | Non-Ducted Indoor Units | 114000 | 13.2 | 25.5 | 129000 | 3.81 | 88000 | 2.54 | R-410A | 9.5
203334986 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XATJ* |  |  |  | REYQ72XATJ* | Ducted Indoor Units | 69000 | 13.9 | 21.3 | 77000 | 3.68 | 58000 | 2.25 | R-410A | 5.75
203334987 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* |  |  |  | REYQ96XATJ* | Ducted Indoor Units | 92000 | 12.5 | 21.9 | 103000 | 3.56 | 72000 | 2.31 | R-410A | 7.6667
203334988 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* |  |  |  | REYQ120XATJ* | Ducted Indoor Units | 114000 | 12.3 | 22.6 | 129000 | 3.48 | 88000 | 2.28 | R-410A | 9.5
203335003 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYD* |  |  |  | REYQ72XAYD* | Ducted Indoor Units | 69000 | 13.9 | 21.3 | 77000 | 3.68 | 58000 | 2.25 | R-410A | 5.75
203335004 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* |  |  |  | REYQ96XAYD* | Ducted Indoor Units | 92000 | 12.5 | 21.9 | 103000 | 3.56 | 72000 | 2.31 | R-410A | 7.6667
203335005 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* |  |  |  | REYQ120XAYD* | Ducted Indoor Units | 114000 | 12.3 | 22.6 | 129000 | 3.48 | 88000 | 2.28 | R-410A | 9.5
203335020 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYC* |  |  |  | REYQ72XAYC* | Ducted Indoor Units | 69000 | 13.9 | 21.3 | 77000 | 3.68 | 58000 | 2.25 | R-410A | 5.75
203335021 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* |  |  |  | REYQ96XAYC* | Ducted Indoor Units | 92000 | 12.5 | 21.9 | 103000 | 3.56 | 72000 | 2.31 | R-410A | 7.6667
203335022 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* |  |  |  | REYQ120XAYC* | Ducted Indoor Units | 114000 | 12.3 | 22.6 | 129000 | 3.48 | 88000 | 2.28 | R-410A | 9.5
203360783 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-SHC120K/220V |  |  |  | TVRF-SHC120K/220V | Non-Ducted Indoor Units | 114000 | 11.5 | 22 | 126000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
203364244 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XATJ* |  |  |  | REYQ72XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.85 | 23.25 | 77000 | 3.99 | 58000 | 2.37 | R-410A | 5.75
203364245 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* |  |  |  | REYQ96XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.55 | 24.85 | 103000 | 3.89 | 72000 | 2.47 | R-410A | 7.6667
203364246 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* |  |  |  | REYQ120XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.75 | 24.05 | 129000 | 3.64 | 88000 | 2.41 | R-410A | 9.5
203364261 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYD* |  |  |  | REYQ72XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.85 | 23.25 | 77000 | 3.99 | 58000 | 2.37 | R-410A | 5.75
203364262 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* |  |  |  | REYQ96XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.55 | 24.85 | 103000 | 3.89 | 72000 | 2.47 | R-410A | 7.6667
203364263 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* |  |  |  | REYQ120XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.75 | 24.05 | 129000 | 3.64 | 88000 | 2.41 | R-410A | 9.5
203364278 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72XAYC* |  |  |  | REYQ72XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.85 | 23.25 | 77000 | 3.99 | 58000 | 2.37 | R-410A | 5.75
203364279 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* |  |  |  | REYQ96XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.55 | 24.85 | 103000 | 3.89 | 72000 | 2.47 | R-410A | 7.6667
203364280 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* |  |  |  | REYQ120XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.75 | 24.05 | 129000 | 3.64 | 88000 | 2.41 | R-410A | 9.5
204572223 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAFH |  |  |  | AM096FXVAFH | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
204572238 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAJH |  |  |  | AM096FXVAJH | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
204572253 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
204572268 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAJR |  |  |  | AM096FXVAJR | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
204572282 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH |  |  |  | AM072KXVTFH | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
204572283 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH |  |  |  | AM096KXVTFH | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
204572290 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH |  |  |  | AM072KXVTJH | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
204572291 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH |  |  |  | AM096KXVTJH | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
204572298 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR |  |  |  | AM072KXVTFR | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
204572299 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
204572306 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR |  |  |  | AM072KXVTJR | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
204572307 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR |  |  |  | AM096KXVTJR | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
204793015 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME2CA* |  |  |  | MVHP072ME2CA* | Ducted Indoor Units | 69000 | 12.1 | 21 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
204793016 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME2CA* |  |  |  | MVHP072ME2CA* | Non-Ducted Indoor Units | 69000 | 13.5 | 25 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
204793017 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME2CA* |  |  |  | MVHR072ME2CA* | Ducted Indoor Units | 69000 | 11.9 | 20 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
204793018 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME2CA* |  |  |  | MVHR072ME2CA* | Non-Ducted Indoor Units | 69000 | 13 | 24.5 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
204793019 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME2CA* |  |  |  | MVHP096ME2CA* | Ducted Indoor Units | 92000 | 12.1 | 22.8 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
204793020 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME2CA* |  |  |  | MVHP096ME2CA* | Non-Ducted Indoor Units | 92000 | 12 | 23 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
204793021 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME2CA* |  |  |  | MVHR096ME2CA* | Ducted Indoor Units | 92000 | 11.9 | 21.8 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
204793022 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME2CA* |  |  |  | MVHR096ME2CA* | Non-Ducted Indoor Units | 92000 | 12.3 | 23 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
204793023 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME2CA* |  |  |  | MVHP120ME2CA* | Ducted Indoor Units | 115000 | 12.1 | 23 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
204793024 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME2CA* |  |  |  | MVHP120ME2CA* | Non-Ducted Indoor Units | 115000 | 12.1 | 22 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
204793025 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME2CA* |  |  |  | MVHR120ME2CA* | Ducted Indoor Units | 115000 | 11.9 | 21.9 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
204793026 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME2CA* |  |  |  | MVHR120ME2CA* | Non-Ducted Indoor Units | 115000 | 11.9 | 22 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
205000511 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAFR |  |  |  | AM120FXVAFR | Non-Ducted Indoor Units | 114000 | 11.4 | 29.3 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
205000539 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAFH |  |  |  | AM120FXVAFH | Non-Ducted Indoor Units | 114000 | 11.4 | 29.3 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
205000540 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAJH |  |  |  | AM120FXVAJH | Non-Ducted Indoor Units | 114000 | 11.4 | 29.3 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
205000541 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAJR |  |  |  | AM120FXVAJR | Non-Ducted Indoor Units | 114000 | 11.4 | 29.3 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
205048202 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/460V |  |  |  | TVRF-OC72KHP/460V | Ducted Indoor Units | 69000 | 11.1 | 20 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
205048203 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/460V |  |  |  | TVRF-OC72KHP/460V | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
205048204 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/460V |  |  |  | TVRF-OC96KHP/460V | Ducted Indoor Units | 92000 | 11.2 | 19 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
205048205 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/460V |  |  |  | TVRF-OC96KHP/460V | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
205048206 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC120KHP/460V |  |  |  | TVRF-OC120KHP/460V | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
205048213 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC72K/460V |  |  |  | TVRF-SHC72K/460V | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
205048215 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC96K/460V |  |  |  | TVRF-SHC96K/460V | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
205048217 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC120K/460V |  |  |  | TVRF-SHC120K/460V | Non-Ducted Indoor Units | 114000 | 11.5 | 22 | 126000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
205233054 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XATJ* |  |  |  | RXYQ72XATJ* | Non-Ducted Indoor Units | 69000 | 14.7 | 25.8 | 73000 | 3.67 | 39000 | 2.44 | R-410A | 5.75
205233055 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* |  |  |  | RXYQ96XATJ* | Non-Ducted Indoor Units | 92000 | 14 | 27.3 | 103000 | 4 | 67000 | 2.63 | R-410A | 7.6667
205233056 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* |  |  |  | RXYQ120XATJ* | Non-Ducted Indoor Units | 114000 | 12 | 25.4 | 129000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
205233059 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYD* |  |  |  | RXYQ72XAYD* | Non-Ducted Indoor Units | 69000 | 14.7 | 25.8 | 73000 | 3.67 | 39000 | 2.44 | R-410A | 5.75
205233060 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* |  |  |  | RXYQ96XAYD* | Non-Ducted Indoor Units | 92000 | 14 | 27.3 | 103000 | 4 | 67000 | 2.63 | R-410A | 7.6667
205233061 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* |  |  |  | RXYQ120XAYD* | Non-Ducted Indoor Units | 114000 | 12 | 25.4 | 129000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
205233065 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* |  |  |  | RXYQ96XATJ* | Ducted Indoor Units | 92000 | 12.6 | 22.5 | 103000 | 3.49 | 67000 | 2.48 | R-410A | 7.6667
205233070 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* |  |  |  | RXYQ96XAYD* | Ducted Indoor Units | 92000 | 12.6 | 22.5 | 103000 | 3.49 | 67000 | 2.48 | R-410A | 7.6667
205234780 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYC* |  |  |  | RXYQ72XAYC* | Non-Ducted Indoor Units | 69000 | 15.1 | 24 | 77000 | 4.37 | 58000 | 2.52 | R-410A | 5.75
205234781 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* |  |  |  | RXYQ96XAYC* | Non-Ducted Indoor Units | 92000 | 13.6 | 24.3 | 103000 | 4.33 | 72000 | 2.66 | R-410A | 7.6667
205234782 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* |  |  |  | RXYQ120XAYC* | Non-Ducted Indoor Units | 114000 | 12.5 | 23.3 | 129000 | 3.89 | 88000 | 2.58 | R-410A | 9.5
205234814 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XATJ* |  |  |  | RXYQ72XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.7 | 23.25 | 73000 | 3.48 | 39000 | 2.34 | R-410A | 5.75
205234815 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* |  |  |  | RXYQ96XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.3 | 24.9 | 103000 | 3.74 | 67000 | 2.55 | R-410A | 7.6667
205234816 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* |  |  |  | RXYQ120XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 23.7 | 129000 | 3.4 | 81000 | 2.31 | R-410A | 9.5
205234819 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYD* |  |  |  | RXYQ72XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.7 | 23.25 | 73000 | 3.48 | 39000 | 2.34 | R-410A | 5.75
205234820 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* |  |  |  | RXYQ96XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.3 | 24.9 | 103000 | 3.74 | 67000 | 2.55 | R-410A | 7.6667
205234821 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* |  |  |  | RXYQ120XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 23.7 | 129000 | 3.4 | 81000 | 2.31 | R-410A | 9.5
205234828 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYC* |  |  |  | RXYQ72XAYC* | Ducted Indoor Units | 69000 | 13 | 20.4 | 77000 | 3.73 | 58000 | 2.31 | R-410A | 5.75
205234829 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* |  |  |  | RXYQ96XAYC* | Ducted Indoor Units | 92000 | 11.4 | 18.9 | 103000 | 3.61 | 72000 | 2.32 | R-410A | 7.6667
205234830 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* |  |  |  | RXYQ120XAYC* | Ducted Indoor Units | 114000 | 11.1 | 19 | 129000 | 3.54 | 88000 | 2.3 | R-410A | 9.5
205234860 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYC* |  |  |  | RXYQ72XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.05 | 22.2 | 77000 | 4.05 | 58000 | 2.41 | R-410A | 5.75
205234861 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* |  |  |  | RXYQ96XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 21.6 | 103000 | 3.97 | 72000 | 2.49 | R-410A | 7.6667
205234862 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* |  |  |  | RXYQ120XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 21.15 | 129000 | 3.71 | 88000 | 2.44 | R-410A | 9.5
203381168 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TKMU-A |  |  |  | PURY-P120TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.95 | 19.25 | 129000 | 3.49 | 92000 | 2.34 | R-410A | 9.5
203381170 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A |  |  |  | PURY-P120TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.45 | 21.55 | 129000 | 3.64 | 87000 | 2.26 | R-410A | 9.5
203381172 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YKMU-A |  |  |  | PURY-P120YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.95 | 19.25 | 129000 | 3.49 | 92000 | 2.34 | R-410A | 9.5
203381174 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A |  |  |  | PURY-P120YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.45 | 21.55 | 129000 | 3.64 | 87000 | 2.26 | R-410A | 9.5
203381254 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TKMU-A |  |  |  | PURY-P72TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.7 | 20.45 | 76000 | 3.7 | 56000 | 2.51 | R-410A | 5.75
203381256 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TLMU-A |  |  |  | PURY-P72TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.4 | 23.5 | 76000 | 3.69 | 56000 | 2.26 | R-410A | 5.75
203381258 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YKMU-A |  |  |  | PURY-P72YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.7 | 20.45 | 76000 | 3.7 | 56000 | 2.51 | R-410A | 5.75
203381260 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YLMU-A |  |  |  | PURY-P72YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.4 | 23.5 | 76000 | 3.69 | 56000 | 2.26 | R-410A | 5.75
203381263 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A |  |  |  | PURY-P96TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.9 | 19.5 | 103000 | 3.63 | 76000 | 2.45 | R-410A | 7.6667
203381265 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A |  |  |  | PURY-P96TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.35 | 23.85 | 103000 | 3.52 | 71000 | 2.25 | R-410A | 7.6667
203381267 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A |  |  |  | PURY-P96YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.9 | 19.5 | 103000 | 3.63 | 76000 | 2.45 | R-410A | 7.6667
203381269 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A |  |  |  | PURY-P96YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.35 | 23.85 | 103000 | 3.52 | 71000 | 2.25 | R-410A | 7.6667
202515497 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 |  |  |  | ARUN072BTE4 | Non-Ducted Indoor Units | 69000 | 13.4 | 27.5 | 77000 | 3.8 | 51000 | 2.6 | R-410A | 5.75
202583514 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU72RLAVL |  |  |  | AOU72RLAVL | Ducted Indoor Units | 69000 | 11.9 | 21.5 | 77000 | 4.01 | 56000 | 2.64 | R-410A | 5.75
202583515 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU96RLAVL |  |  |  | AOU96RLAVL | Ducted Indoor Units | 92000 | 11.6 | 21.1 | 103000 | 3.66 | 73000 | 2.47 | R-410A | 7.6667
202583516 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOU120RLAVL |  |  |  | AOU120RLAVL | Ducted Indoor Units | 114000 | 11.6 | 20.9 | 129000 | 3.64 | 87000 | 2.35 | R-410A | 9.5
204442775 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH |  |  |  | AM072KXVTFH | Non-Ducted Indoor Units | 69000 | 14.1 | 32.6 | 77000 | 4.35 | 77000 | 2.58 | R-410A | 5.75
204442776 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH |  |  |  | AM096KXVTFH | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.32 | 103000 | 2.45 | R-410A | 7.6667
204442783 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH |  |  |  | AM072KXVTJH | Non-Ducted Indoor Units | 69000 | 14.1 | 32.6 | 77000 | 4.35 | 77000 | 2.58 | R-410A | 5.75
204442784 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH |  |  |  | AM096KXVTJH | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.32 | 103000 | 2.45 | R-410A | 7.6667
205708872 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/460V |  |  |  | TVRF-OC72KHP/460V | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 21.5 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
205708873 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/460V |  |  |  | TVRF-OC96KHP/460V | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 22.5 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
205708874 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC120KHP/460V |  |  |  | TVRF-OC120KHP/460V | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
205782688 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC96K/220V |  |  |  | TVRF-SHC96K/220V | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
205782689 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC120K/220V |  |  |  | TVRF-SHC120K/220V | Mixed Ducted and Non-Ducted Indoor Units | 112000 | 11.25 | 22.4 | 126000 | 3.4 | 82000 | 2.25 | R-410A | 9.3333
204442792 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.32 | 103000 | 2.45 | R-410A | 7.6667
205281456 | 1/1/2027 | LG | HMSR-A-CB | ARUM072BTE5 |  |  |  | ARUM072BTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
205281458 | 1/1/2027 | LG | HMSR-A-CB | ARUM072DTE5 |  |  |  | ARUM072DTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
205281459 | 1/1/2027 | LG | HMSR-A-CB | ARUM096BTE5 |  |  |  | ARUM096BTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
206568879 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME4CA* |  |  |  | MVHP072ME4CA* | Ducted Indoor Units | 69000 | 12.1 | 21 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
206568881 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME4CA* |  |  |  | MVHP072ME4CA* | Non-Ducted Indoor Units | 69000 | 13.5 | 25 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
206568882 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME4CA* |  |  |  | MVHR072ME4CA* | Ducted Indoor Units | 69000 | 11.9 | 20 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
206568883 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME4CA* |  |  |  | MVHR072ME4CA* | Non-Ducted Indoor Units | 69000 | 13 | 24.5 | 77000 | 3.6 | 54000 | 2.5 | R-410A | 5.75
206568885 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME4CA* |  |  |  | MVHP096ME4CA* | Ducted Indoor Units | 92000 | 12.1 | 22.8 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
206568886 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME4CA* |  |  |  | MVHP096ME4CA* | Non-Ducted Indoor Units | 92000 | 12 | 23 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
206568887 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME4CA* |  |  |  | MVHR096ME4CA* | Ducted Indoor Units | 92000 | 11.9 | 21.8 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
206568888 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME4CA* |  |  |  | MVHR096ME4CA* | Non-Ducted Indoor Units | 92000 | 12.3 | 23 | 103000 | 3.6 | 72000 | 2.5 | R-410A | 7.6667
206568890 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME4CA* |  |  |  | MVHP120ME4CA* | Ducted Indoor Units | 115000 | 12.1 | 23 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
206568891 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME4CA* |  |  |  | MVHP120ME4CA* | Non-Ducted Indoor Units | 115000 | 12.1 | 22 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
206568892 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME4CA* |  |  |  | MVHR120ME4CA* | Ducted Indoor Units | 115000 | 11.9 | 21.9 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
206568893 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME4CA* |  |  |  | MVHR120ME4CA* | Non-Ducted Indoor Units | 115000 | 11.9 | 22 | 129000 | 3.6 | 84000 | 2.5 | R-410A | 9.5833
206799419 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH |  |  |  | AM072KXVTFH | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
206799420 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR |  |  |  | AM072KXVTFR | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
206799421 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH |  |  |  | AM072KXVTJH | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
206799422 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR |  |  |  | AM072KXVTJR | Ducted Indoor Units | 69000 | 11.7 | 25.3 | 77000 | 3.64 | 77000 | 2.4 | R-410A | 5.75
206799423 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAFH |  |  |  | AM096FXVAFH | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
206799424 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
206799425 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAJH |  |  |  | AM096FXVAJH | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
206799426 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAJR |  |  |  | AM096FXVAJR | Ducted Indoor Units | 92000 | 11.9 | 24.5 | 103000 | 3.63 | 67000 | 2.62 | R-410A | 7.6667
206799427 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH |  |  |  | AM096KXVTFH | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
206799428 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
206799429 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH |  |  |  | AM096KXVTJH | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
206799430 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR |  |  |  | AM096KXVTJR | Ducted Indoor Units | 92000 | 12.2 | 24.7 | 103000 | 3.59 | 103000 | 2.38 | R-410A | 7.6667
207172462 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
207172463 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Non-Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
207172466 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BSS5 |  |  |  | ARUN072BSS5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.9 | 21.8 | 77000 | 3.8 | 54000 | 2.6 | R-410A | 5.75
201760441 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-*G |  |  |  | VRA072H4M-*G | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201760442 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-*G |  |  |  | VRA072H4M-*G | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201760443 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-*G |  |  |  | VPA072H4M-*G | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201760445 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-*G |  |  |  | VPA072H4M-*G | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201760446 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-*Y |  |  |  | VRA072H4M-*Y | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201760447 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-*Y |  |  |  | VRA072H4M-*Y | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201760449 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-*Y |  |  |  | VPA072H4M-*Y | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201760450 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-*Y |  |  |  | VPA072H4M-*Y | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201830205 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) |  |  |  | MV5-R96DXN1-(A)* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201830208 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) |  |  |  | MV5-R96DXN1-(A)* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201830209 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) |  |  |  | MV5-R120DXN1-(A)* | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201830213 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) |  |  |  | MV5-R96DZN1-(A)* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201830214 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) |  |  |  | MV5-R96DZN1-(A)* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201830215 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) |  |  |  | MV5-R120DZN1-(A)* | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201830219 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) |  |  |  | MV5-X96DXN1-(A)* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201830220 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) |  |  |  | MV5-X96DXN1-(A)* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201830224 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) |  |  |  | MV5-X96DZN1-(A)* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201830225 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) |  |  |  | MV5-X96DZN1-(A)* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201830349 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) |  |  |  | MV5-X120DXN1-(A)* | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201830350 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) |  |  |  | MV5-X120DZN1-(A)* | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201847109 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-2G |  |  |  | VPA072H4M-2G | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201847110 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-2G |  |  |  | VPA072H4M-2G | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201847111 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-2Y |  |  |  | VPA072H4M-2Y | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201847112 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072H4M-2Y |  |  |  | VPA072H4M-2Y | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201847113 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G |  |  |  | VPA096H4M-2G | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201847114 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G |  |  |  | VPA096H4M-2G | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201847115 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y |  |  |  | VPA096H4M-2Y | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201847116 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y |  |  |  | VPA096H4M-2Y | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201847118 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G |  |  |  | VPA120H4M-2G | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201847120 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y |  |  |  | VPA120H4M-2Y | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201847169 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-2Y |  |  |  | VRA072H4M-2Y | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201847170 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-2Y |  |  |  | VRA072H4M-2Y | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201847171 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-2G |  |  |  | VRA072H4M-2G | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201847172 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072H4M-2G |  |  |  | VRA072H4M-2G | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201847173 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y |  |  |  | VRA096H4M-2Y | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201847174 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y |  |  |  | VRA096H4M-2Y | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201847175 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G |  |  |  | VRA096H4M-2G | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201847176 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G |  |  |  | VRA096H4M-2G | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201847177 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y |  |  |  | VRA120H4M-2Y | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201847179 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G |  |  |  | VRA120H4M-2G | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201856718 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DXN1-(A) |  |  |  | MV5-RC72DXN1-(A) | Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201856719 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DXN1-(A) |  |  |  | MV5-RC72DXN1-(A) | Ducted Indoor Units | 69000 | 11.8 | 21.6 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201856720 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) |  |  |  | MV5-RC96DXN1-(A) | Non-Ducted Indoor Units | 92000 | 12.7 | 24.1 | 103000 | 3.82 | 72000 | 2.44 | R-410A | 7.6667
201856722 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) |  |  |  | MV5-RC120DXN1-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 21.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201856742 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DZN1-(A) |  |  |  | MV5-RC72DZN1-(A) | Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201856743 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DZN1-(A) |  |  |  | MV5-RC72DZN1-(A) | Ducted Indoor Units | 69000 | 11.8 | 21.6 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201856744 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) |  |  |  | MV5-RC96DZN1-(A) | Non-Ducted Indoor Units | 92000 | 12.7 | 24.1 | 103000 | 3.82 | 72000 | 2.44 | R-410A | 7.6667
201856746 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) |  |  |  | MV5-RC120DZN1-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 21.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201856766 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DXN1-(A) |  |  |  | MV5-XC72DXN1-(A) | Non-Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201856767 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DXN1-(A) |  |  |  | MV5-XC72DXN1-(A) | Ducted Indoor Units | 69000 | 11.8 | 21.5 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201856768 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) |  |  |  | MV5-XC96DXN1-(A) | Non-Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.93 | 72000 | 2.44 | R-410A | 7.6667
201856770 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) |  |  |  | MV5-XC120DXN1-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 21.7 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201856788 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DZN1-(A) |  |  |  | MV5-XC72DZN1-(A) | Non-Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201856789 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DZN1-(A) |  |  |  | MV5-XC72DZN1-(A) | Ducted Indoor Units | 69000 | 11.8 | 21.5 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201856790 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) |  |  |  | MV5-XC96DZN1-(A) | Non-Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.93 | 72000 | 2.44 | R-410A | 7.6667
201856792 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) |  |  |  | MV5-XC120DZN1-(A) | Non-Ducted Indoor Units | 115000 | 11.6 | 21.7 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201862854 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2Y |  |  |  | VRA072L4M-2Y | Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201862855 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2Y |  |  |  | VRA072L4M-2Y | Ducted Indoor Units | 69000 | 11.8 | 21.6 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201862856 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y |  |  |  | VRA096L4M-2Y | Non-Ducted Indoor Units | 92000 | 12.7 | 24.1 | 103000 | 3.82 | 72000 | 2.44 | R-410A | 7.6667
201862858 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y |  |  |  | VRA120L4M-2Y | Non-Ducted Indoor Units | 115000 | 11.6 | 21.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201862878 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2G |  |  |  | VRA072L4M-2G | Non-Ducted Indoor Units | 69000 | 13 | 23.1 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201862879 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2G |  |  |  | VRA072L4M-2G | Ducted Indoor Units | 69000 | 11.8 | 21.6 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201862880 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G |  |  |  | VRA096L4M-2G | Non-Ducted Indoor Units | 92000 | 12.7 | 24.1 | 103000 | 3.82 | 72000 | 2.44 | R-410A | 7.6667
201862882 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G |  |  |  | VRA120L4M-2G | Non-Ducted Indoor Units | 115000 | 11.6 | 21.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201862902 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2Y |  |  |  | VPA072L4M-2Y | Non-Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201862903 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2Y |  |  |  | VPA072L4M-2Y | Ducted Indoor Units | 69000 | 11.8 | 21.5 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201862904 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y |  |  |  | VPA096L4M-2Y | Non-Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.93 | 72000 | 2.44 | R-410A | 7.6667
201862906 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y |  |  |  | VPA120L4M-2Y | Non-Ducted Indoor Units | 115000 | 11.6 | 21.7 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201862924 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2G |  |  |  | VPA072L4M-2G | Non-Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 4.05 | 54000 | 2.53 | R-410A | 5.75
201862925 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2G |  |  |  | VPA072L4M-2G | Ducted Indoor Units | 69000 | 11.8 | 21.5 | 77000 | 3.68 | 54000 | 2.25 | R-410A | 5.75
201862926 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G |  |  |  | VPA096L4M-2G | Non-Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.93 | 72000 | 2.44 | R-410A | 7.6667
201862928 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G |  |  |  | VPA120L4M-2G | Non-Ducted Indoor Units | 115000 | 11.6 | 21.7 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201864458 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C6000AA |  |  |  | 4TVR0072C6000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201864459 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C6000AA |  |  |  | 4TVR0072C6000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201864460 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0096C6000AA |  |  |  | 4TVR0096C6000AA* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201864461 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0096C6000AA |  |  |  | 4TVR0096C6000AA* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201864462 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0115C6000AA |  |  |  | 4TVR0115C6000AA* | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201864466 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C4000AA |  |  |  | 4TVR0072C4000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201864467 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C4000AA |  |  |  | 4TVR0072C4000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201864468 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0096C4000AA |  |  |  | 4TVR0096C4000AA* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201864469 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0096C4000AA |  |  |  | 4TVR0096C4000AA* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201864470 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0115C4000AA |  |  |  | 4TVR0115C4000AA* | Non-Ducted Indoor Units | 115000 | 11.4 | 23.2 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201864474 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0072C6000AA |  |  |  | 4TVH0072C6000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201864475 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0072C6000AA |  |  |  | 4TVH0072C6000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201864476 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0096C6000AA |  |  |  | 4TVH0096C6000AA* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201864477 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0096C6000AA |  |  |  | 4TVH0096C6000AA* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201864478 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0115C6000AA |  |  |  | 4TVH0115C6000AA* | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
201864482 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0072C4000AA |  |  |  | 4TVH0072C4000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
201864483 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0072C4000AA |  |  |  | 4TVH0072C4000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
201864484 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0096C4000AA |  |  |  | 4TVH0096C4000AA* | Non-Ducted Indoor Units | 92000 | 12.4 | 23.5 | 103000 | 3.8 | 72000 | 2.46 | R-410A | 7.6667
201864485 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0096C4000AA |  |  |  | 4TVH0096C4000AA* | Ducted Indoor Units | 92000 | 11.7 | 22.5 | 103000 | 3.57 | 72000 | 2.3 | R-410A | 7.6667
201864486 | 1/1/2027 | TRANE | HMSV-A-CB | 4TVH0115C4000AA |  |  |  | 4TVH0115C4000AA* | Non-Ducted Indoor Units | 115000 | 11.4 | 22.9 | 120000 | 3.52 | 80000 | 2.25 | R-410A | 9.5833
10612394 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Non-Ducted Indoor Units | 69000 | 14.8 | 29 | 77000 | 4.23 | 56000 | 2.68 | R-410A | 5.75
10612395 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Non-Ducted Indoor Units | 69000 | 14.8 | 29 | 77000 | 4.23 | 56000 | 2.68 | R-410A | 5.75
10612396 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Ducted Indoor Units | 92000 | 13.3 | 22.3 | 103000 | 4 | 76000 | 2.83 | R-410A | 7.6667
10612397 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Ducted Indoor Units | 92000 | 13.3 | 22.3 | 103000 | 4 | 76000 | 2.83 | R-410A | 7.6667
10612398 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Ducted Indoor Units | 114000 | 12.1 | 21.6 | 129000 | 3.89 | 92000 | 2.75 | R-410A | 9.5
10612399 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Ducted Indoor Units | 114000 | 12.1 | 21.6 | 129000 | 3.89 | 92000 | 2.75 | R-410A | 9.5
10612437 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Ducted Indoor Units | 69000 | 13.5 | 22.7 | 77000 | 3.79 | 56000 | 2.74 | R-410A | 5.75
10612438 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Ducted Indoor Units | 69000 | 13.5 | 22.7 | 77000 | 3.79 | 56000 | 2.74 | R-410A | 5.75
10612439 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.15 | 25.85 | 77000 | 4.01 | 56000 | 2.71 | R-410A | 5.75
10612440 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
10612441 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
10612442 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 23.05 | 77000 | 3.54 | 56000 | 2.58 | R-410A | 5.75
10612443 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Non-Ducted Indoor Units | 92000 | 12.6 | 28 | 103000 | 4.5 | 76000 | 2.84 | R-410A | 7.6667
10612444 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Non-Ducted Indoor Units | 92000 | 12.6 | 28 | 103000 | 4.5 | 76000 | 2.84 | R-410A | 7.6667
10612445 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.95 | 25.15 | 103000 | 4.25 | 76000 | 2.83 | R-410A | 7.6667
10612446 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 24.85 | 103000 | 3.78 | 76000 | 2.57 | R-410A | 7.6667
10612447 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 24.85 | 103000 | 3.78 | 76000 | 2.57 | R-410A | 7.6667
10612448 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Non-Ducted Indoor Units | 114000 | 12.8 | 25.1 | 129000 | 3.99 | 92000 | 2.79 | R-410A | 9.5
10612449 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Non-Ducted Indoor Units | 114000 | 12.8 | 25.1 | 129000 | 3.99 | 92000 | 2.79 | R-410A | 9.5
10612450 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.45 | 23.35 | 129000 | 3.94 | 92000 | 2.77 | R-410A | 9.5
10612451 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.85 | 23.75 | 129000 | 3.54 | 92000 | 2.45 | R-410A | 9.5
10612452 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.85 | 23.75 | 129000 | 3.54 | 92000 | 2.45 | R-410A | 9.5
10612546 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.15 | 25.85 | 77000 | 4.01 | 56000 | 2.71 | R-410A | 5.75
10612547 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Non-Ducted Indoor Units | 69000 | 14.6 | 26.6 | 77000 | 3.67 | 56000 | 2.73 | R-410A | 5.75
10612548 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Ducted Indoor Units | 69000 | 12.6 | 19.5 | 77000 | 3.42 | 56000 | 2.44 | R-410A | 5.75
10612549 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Non-Ducted Indoor Units | 69000 | 14.6 | 26.6 | 77000 | 3.67 | 56000 | 2.73 | R-410A | 5.75
10612550 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Ducted Indoor Units | 69000 | 12.6 | 19.5 | 77000 | 3.42 | 56000 | 2.44 | R-410A | 5.75
10612551 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Non-Ducted Indoor Units | 69000 | 14.6 | 26.6 | 77000 | 3.67 | 56000 | 2.73 | R-410A | 5.75
10612552 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Ducted Indoor Units | 69000 | 12.6 | 19.5 | 77000 | 3.42 | 56000 | 2.44 | R-410A | 5.75
10612553 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.95 | 25.15 | 103000 | 4.25 | 76000 | 2.83 | R-410A | 7.6667
10612554 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Non-Ducted Indoor Units | 92000 | 12.5 | 28.3 | 103000 | 3.85 | 76000 | 2.61 | R-410A | 7.6667
10612555 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Ducted Indoor Units | 92000 | 11.7 | 21.4 | 103000 | 3.71 | 76000 | 2.54 | R-410A | 7.6667
10612556 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Non-Ducted Indoor Units | 92000 | 12.5 | 28.3 | 103000 | 3.85 | 76000 | 2.61 | R-410A | 7.6667
10612557 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Ducted Indoor Units | 92000 | 11.7 | 21.4 | 103000 | 3.71 | 76000 | 2.54 | R-410A | 7.6667
10612558 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.45 | 23.35 | 129000 | 3.94 | 92000 | 2.77 | R-410A | 9.5
10612559 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Non-Ducted Indoor Units | 114000 | 11.8 | 27.5 | 129000 | 3.61 | 92000 | 2.44 | R-410A | 9.5
10612560 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Ducted Indoor Units | 114000 | 11.9 | 20 | 129000 | 3.48 | 92000 | 2.46 | R-410A | 9.5
10612561 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Non-Ducted Indoor Units | 114000 | 11.8 | 27.5 | 129000 | 3.61 | 92000 | 2.44 | R-410A | 9.5
10612562 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Ducted Indoor Units | 114000 | 11.9 | 20 | 129000 | 3.48 | 92000 | 2.46 | R-410A | 9.5
201978071 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A |  |  |  | PUHY-P120TKMU-A | Non-Ducted Indoor Units | 114000 | 12.7 | 19.1 | 129000 | 3.83 | 92000 | 2.38 | R-410A | 9.5
201978072 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A |  |  |  | PUHY-P120YKMU-A | Non-Ducted Indoor Units | 114000 | 12.7 | 19.1 | 129000 | 3.83 | 92000 | 2.38 | R-410A | 9.5
201978090 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TKMU-A |  |  |  | PUHY-P72TKMU-A | Non-Ducted Indoor Units | 69000 | 14.2 | 21.3 | 76000 | 4.19 | 56000 | 2.39 | R-410A | 5.75
201978091 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TKMU-A |  |  |  | PUHY-P96TKMU-A | Non-Ducted Indoor Units | 92000 | 13.7 | 20.7 | 103000 | 4.22 | 76000 | 2.68 | R-410A | 7.6667
201978092 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YKMU-A |  |  |  | PUHY-P96YKMU-A | Non-Ducted Indoor Units | 92000 | 13.7 | 20.7 | 103000 | 4.22 | 76000 | 2.68 | R-410A | 7.6667
201981539 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YKMU-A |  |  |  | PUHY-P72YKMU-A | Non-Ducted Indoor Units | 69000 | 14.2 | 21.3 | 76000 | 4.19 | 56000 | 2.39 | R-410A | 5.75
201992871 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* |  |  |  | RXLQ72TAYC* | Non-Ducted Indoor Units | 69000 | 15.1 | 24 | 77000 | 4.37 | 58000 | 2.52 | R-410A | 5.75
201992872 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYC* |  |  |  | RXYQ72TAYC* | Non-Ducted Indoor Units | 69000 | 15.1 | 24 | 77000 | 4.37 | 58000 | 2.52 | R-410A | 5.75
201992873 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* |  |  |  | RXYQ96TAYC* | Non-Ducted Indoor Units | 92000 | 13.6 | 24.3 | 103000 | 4.33 | 72000 | 2.66 | R-410A | 7.6667
201992874 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* |  |  |  | RXYQ120TAYC* | Non-Ducted Indoor Units | 114000 | 12.5 | 23.3 | 129000 | 3.89 | 88000 | 2.58 | R-410A | 9.5
201992879 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* |  |  |  | RXLQ72TATJ* | Non-Ducted Indoor Units | 69000 | 15.1 | 24 | 77000 | 4.37 | 58000 | 2.52 | R-410A | 5.75
201992880 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* |  |  |  | RXLQ72TAYD* | Non-Ducted Indoor Units | 69000 | 15.1 | 24 | 77000 | 4.37 | 58000 | 2.52 | R-410A | 5.75
201993173 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* |  |  |  | RXLQ96TAYC* | Non-Ducted Indoor Units | 92000 | 14.9 | 24.7 | 103000 | 4.29 | 86000 | 2.51 | R-410A | 7.6667
201993174 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* |  |  |  | RXLQ120TAYC* | Non-Ducted Indoor Units | 114000 | 13.5 | 23.3 | 129000 | 4.05 | 110000 | 2.27 | R-410A | 9.5
201993477 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* |  |  |  | RXLQ96TATJ* | Non-Ducted Indoor Units | 92000 | 14.9 | 24.7 | 103000 | 4.29 | 86000 | 2.51 | R-410A | 7.6667
201993478 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* |  |  |  | RXLQ96TAYD* | Non-Ducted Indoor Units | 92000 | 14.9 | 24.7 | 103000 | 4.29 | 86000 | 2.51 | R-410A | 7.6667
201993479 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* |  |  |  | RXLQ120TATJ* | Non-Ducted Indoor Units | 114000 | 13.5 | 23.3 | 129000 | 4.05 | 110000 | 2.27 | R-410A | 9.5
201993480 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* |  |  |  | RXLQ120TAYD* | Non-Ducted Indoor Units | 114000 | 13.5 | 23.3 | 129000 | 4.05 | 110000 | 2.27 | R-410A | 9.5
202021864 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* |  |  |  | RXLQ72TATJ* | Ducted Indoor Units | 69000 | 13 | 20.4 | 77000 | 3.73 | 58000 | 2.31 | R-410A | 5.75
202021865 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* |  |  |  | RXLQ72TAYD* | Ducted Indoor Units | 69000 | 13 | 20.4 | 77000 | 3.73 | 58000 | 2.31 | R-410A | 5.75
202021866 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* |  |  |  | RXLQ72TAYC* | Ducted Indoor Units | 69000 | 13 | 20.4 | 77000 | 3.73 | 58000 | 2.31 | R-410A | 5.75
202021867 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* |  |  |  | RXLQ96TATJ* | Ducted Indoor Units | 92000 | 12.3 | 18.9 | 103000 | 3.49 | 86000 | 2.26 | R-410A | 7.6667
202021868 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* |  |  |  | RXLQ96TAYD* | Ducted Indoor Units | 92000 | 12.3 | 18.9 | 103000 | 3.49 | 86000 | 2.26 | R-410A | 7.6667
202021869 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* |  |  |  | RXLQ96TAYC* | Ducted Indoor Units | 92000 | 12.3 | 18.9 | 103000 | 3.49 | 86000 | 2.26 | R-410A | 7.6667
202021870 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* |  |  |  | RXLQ120TATJ* | Ducted Indoor Units | 114000 | 12.2 | 19.4 | 129000 | 3.56 | 110000 | 2.26 | R-410A | 9.5
202021871 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* |  |  |  | RXLQ120TAYD* | Ducted Indoor Units | 114000 | 12.2 | 19.4 | 129000 | 3.56 | 110000 | 2.26 | R-410A | 9.5
202021872 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* |  |  |  | RXLQ120TAYC* | Ducted Indoor Units | 114000 | 12.2 | 19.4 | 129000 | 3.56 | 110000 | 2.26 | R-410A | 9.5
202021882 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* |  |  |  | RXYQ96TAYC* | Ducted Indoor Units | 92000 | 11.4 | 18.9 | 103000 | 3.61 | 72000 | 2.32 | R-410A | 7.6667
202021883 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* |  |  |  | RXYQ120TAYC* | Ducted Indoor Units | 114000 | 11.1 | 19 | 129000 | 3.54 | 88000 | 2.3 | R-410A | 9.5
202022800 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* |  |  |  | RXYQ96TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 21.6 | 103000 | 3.97 | 72000 | 2.49 | R-410A | 7.6667
202022801 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* |  |  |  | RXYQ120TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 21.15 | 129000 | 3.71 | 88000 | 2.44 | R-410A | 9.5
202022813 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* |  |  |  | RXLQ72TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.05 | 22.2 | 77000 | 4.05 | 58000 | 2.41 | R-410A | 5.75
202022814 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* |  |  |  | RXLQ72TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.05 | 22.2 | 77000 | 4.05 | 58000 | 2.41 | R-410A | 5.75
202022815 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* |  |  |  | RXLQ72TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.05 | 22.2 | 77000 | 4.05 | 58000 | 2.41 | R-410A | 5.75
202022816 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* |  |  |  | RXLQ96TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.6 | 21.8 | 103000 | 3.89 | 86000 | 2.38 | R-410A | 7.6667
202022817 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* |  |  |  | RXLQ96TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.6 | 21.8 | 103000 | 3.89 | 86000 | 2.38 | R-410A | 7.6667
202022818 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* |  |  |  | RXLQ96TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.6 | 21.8 | 103000 | 3.89 | 86000 | 2.38 | R-410A | 7.6667
202022819 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* |  |  |  | RXLQ120TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.85 | 21.35 | 129000 | 3.8 | 110000 | 2.26 | R-410A | 9.5
202022820 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* |  |  |  | RXLQ120TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.85 | 21.35 | 129000 | 3.8 | 110000 | 2.26 | R-410A | 9.5
202022821 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* |  |  |  | RXLQ120TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.85 | 21.35 | 129000 | 3.8 | 110000 | 2.26 | R-410A | 9.5
202022845 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYC* |  |  |  | RXYQ72TAYC* | Ducted Indoor Units | 69000 | 13 | 20.4 | 77000 | 3.73 | 58000 | 2.31 | R-410A | 5.75
202022846 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYC* |  |  |  | RXYQ72TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.05 | 22.2 | 77000 | 4.05 | 58000 | 2.41 | R-410A | 5.75
202073573 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) |  |  |  | MV5-R96DXN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
202073574 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) |  |  |  | MV5-R120DXN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.35 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
202073576 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) |  |  |  | MV5-R96DZN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
202073577 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) |  |  |  | MV5-R120DZN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.35 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
202073579 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) |  |  |  | MV5-X96DXN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
202073580 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) |  |  |  | MV5-X120DXN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
202073582 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) |  |  |  | MV5-X96DZN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.05 | 23 | 103000 | 3.68 | 72000 | 2.38 | R-410A | 7.6667
202073583 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) |  |  |  | MV5-X120DZN1-(A)* | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 22.05 | 120000 | 3.46 | 80000 | 2.26 | R-410A | 9.5833
202606694 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S |  |  |  | TVAHP072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
202606695 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S |  |  |  | HVAHP072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
202606696 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S |  |  |  | YVAHP072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
202606697 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S |  |  |  | TVAHP072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
202606698 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S |  |  |  | HVAHP072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
202606699 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S |  |  |  | YVAHP072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
202606700 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S |  |  |  | TVAHR072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
202606701 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S |  |  |  | HVAHR072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
202606702 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S |  |  |  | YVAHR072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
202606703 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S |  |  |  | TVAHR072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
202606704 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S |  |  |  | HVAHR072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
202606705 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S |  |  |  | YVAHR072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
202606706 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S |  |  |  | TVAHP072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
202606707 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S |  |  |  | HVAHP072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
202606708 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S |  |  |  | YVAHP072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
202606709 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S |  |  |  | TVAHP072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
202606710 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S |  |  |  | HVAHP072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
202606711 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S |  |  |  | YVAHP072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
202606712 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S |  |  |  | TVAHR072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
202606713 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S |  |  |  | HVAHR072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
202606714 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S |  |  |  | YVAHR072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
202606715 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S |  |  |  | TVAHR072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
202606716 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S |  |  |  | HVAHR072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
202606717 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S |  |  |  | YVAHR072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
202606730 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S |  |  |  | TVAHP096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
202606731 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S |  |  |  | HVAHP096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
202606732 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S |  |  |  | YVAHP096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
202606736 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S |  |  |  | TVAHR096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
202606737 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S |  |  |  | HVAHR096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
202606738 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S |  |  |  | YVAHR096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
202606742 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S |  |  |  | TVAHP096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
202606743 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S |  |  |  | HVAHP096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
202606744 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S |  |  |  | YVAHP096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
202606745 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S |  |  |  | TVAHP096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
202606746 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S |  |  |  | HVAHP096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
202606747 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S |  |  |  | YVAHP096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
202606748 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S |  |  |  | TVAHR096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
202606749 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S |  |  |  | HVAHR096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
202606750 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S |  |  |  | YVAHR096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
202606751 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S |  |  |  | TVAHR096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
202606752 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S |  |  |  | HVAHR096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
202606753 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S |  |  |  | YVAHR096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
202606760 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW |  |  |  | TVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606761 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW |  |  |  | HVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606762 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW |  |  |  | YVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606763 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW |  |  |  | TVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606764 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW |  |  |  | HVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606765 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW |  |  |  | YVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
202606766 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S |  |  |  | TVAHP120B31S | Ducted Indoor Units | 115000 | 11.3 | 20.1 | 129000 | 3.56 | 89000 | 2.25 | R-410A | 9.5833
202606767 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S |  |  |  | HVAHP120B31S | Ducted Indoor Units | 115000 | 11.3 | 20.1 | 129000 | 3.56 | 89000 | 2.25 | R-410A | 9.5833
202606768 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S |  |  |  | YVAHP120B31S | Ducted Indoor Units | 115000 | 11.3 | 20.1 | 129000 | 3.56 | 89000 | 2.25 | R-410A | 9.5833
202606772 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S |  |  |  | TVAHR120B31S | Ducted Indoor Units | 115000 | 11.1 | 19 | 129000 | 3.58 | 89000 | 2.25 | R-410A | 9.5833
202606773 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S |  |  |  | HVAHR120B31S | Ducted Indoor Units | 115000 | 11.1 | 19 | 129000 | 3.58 | 89000 | 2.25 | R-410A | 9.5833
202606774 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S |  |  |  | YVAHR120B31S | Ducted Indoor Units | 115000 | 11.1 | 19 | 129000 | 3.58 | 89000 | 2.25 | R-410A | 9.5833
202607341 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607342 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607343 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607344 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607345 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607346 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607347 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607348 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607349 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607350 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607351 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607352 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
202607353 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607354 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607355 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607356 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607357 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607358 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607359 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607360 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607361 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607362 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607363 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607364 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
202607365 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607366 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607367 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607368 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607369 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607370 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607371 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607372 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607373 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607374 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607375 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607376 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
202607377 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607378 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607379 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607380 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607381 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607382 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607383 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607384 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607385 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607386 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607387 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607388 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
202607389 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607390 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607391 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607392 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607393 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607394 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607395 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607396 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607397 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607398 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607399 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607400 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
202607451 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S |  |  |  | TVAHP120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
202607452 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S |  |  |  | HVAHP120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
202607453 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S |  |  |  | YVAHP120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
202607454 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S |  |  |  | TVAHP120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
202607455 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S |  |  |  | HVAHP120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
202607456 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S |  |  |  | YVAHP120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
202607457 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S |  |  |  | TVAHR120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
202607458 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S |  |  |  | HVAHR120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
202607459 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S |  |  |  | YVAHR120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
202607460 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S |  |  |  | TVAHR120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
202607461 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S |  |  |  | HVAHR120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
202607462 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S |  |  |  | YVAHR120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
202607463 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607464 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607465 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607466 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607467 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607468 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607469 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607470 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607471 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607472 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607473 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607474 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
202607926 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607927 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607928 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607929 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607930 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607931 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607932 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607933 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607934 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607935 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607936 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607937 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
202607956 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607957 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607958 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607959 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607960 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607961 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607962 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607963 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607964 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607965 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607966 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607967 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
202607980 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607981 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607982 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607983 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607984 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607985 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607986 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607987 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607988 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607989 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607990 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
202607991 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
203906567 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW |  |  |  | TVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203906568 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW |  |  |  | HVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203906569 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW |  |  |  | YVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203906570 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW |  |  |  | TVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203906571 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW |  |  |  | HVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203906573 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW |  |  |  | YVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203906599 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906600 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906601 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906602 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906603 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906604 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906605 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906606 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906607 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906608 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906609 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906610 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
203906612 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906613 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906614 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906615 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906616 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906617 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906618 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906619 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906620 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906621 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906622 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906624 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
203906625 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906626 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906627 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906628 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906629 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906630 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906631 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906632 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906633 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906634 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906635 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906636 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
203906637 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906638 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906639 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906640 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906641 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906642 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906643 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906644 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906646 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906647 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906648 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906649 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
203906650 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906651 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906652 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906653 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906654 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906655 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906656 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906657 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906658 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906660 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906661 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906662 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
203906713 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906714 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906715 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906716 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906717 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906718 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906719 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906720 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906721 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906722 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906723 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203906725 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
203993607 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B31CW |  |  |  | TVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203993609 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW |  |  |  | HVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203993611 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW |  |  |  | YVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203993614 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B41CW |  |  |  | TVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203993616 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW |  |  |  | HVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
203993618 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW |  |  |  | YVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
204268347 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204268350 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B52S |  |  |  | TVAHR096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268352 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B52S |  |  |  | TVAHR120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204268375 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204268376 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B52S |  |  |  | HVAHR096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268378 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B52S |  |  |  | HVAHR120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204268392 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204268393 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B52S |  |  |  | YVAHR096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268394 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B52S |  |  |  | YVAHR120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204268408 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204268409 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B52S |  |  |  | TVAHR096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268410 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B52S |  |  |  | TVAHR120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204268424 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204268425 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B52S |  |  |  | HVAHR096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268426 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B52S |  |  |  | HVAHR120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204268441 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204268442 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B52S |  |  |  | YVAHR096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268443 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B52S |  |  |  | YVAHR120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204268471 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204268472 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B52S |  |  |  | TVAHP096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268473 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B52S |  |  |  | TVAHP120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204268495 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204268497 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B52S |  |  |  | HVAHP096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268499 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B52S |  |  |  | HVAHP120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204268530 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
204268531 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B52S |  |  |  | YVAHP096B52S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
204268533 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B52S |  |  |  | YVAHP120B52S | Non-Ducted Indoor Units | 114000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5
204268557 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204268558 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B52S |  |  |  | TVAHP096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268559 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B52S |  |  |  | TVAHP120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204268580 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204268581 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B52S |  |  |  | HVAHP096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268582 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B52S |  |  |  | HVAHP120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204268596 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
204268597 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B52S |  |  |  | YVAHP096B52S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
204268598 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B52S |  |  |  | YVAHP120B52S | Ducted Indoor Units | 114000 | 12.4 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5
204269024 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B52S |  |  |  | TVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269025 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B52S |  |  |  | TVAHR096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204269026 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B52S |  |  |  | TVAHR120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204269040 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B52S |  |  |  | HVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269041 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B52S |  |  |  | HVAHR096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204269042 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B52S |  |  |  | HVAHR120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204269056 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B52S |  |  |  | YVAHR072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269057 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B52S |  |  |  | YVAHR096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204269058 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B52S |  |  |  | YVAHR120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204269072 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B52S |  |  |  | TVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269073 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B52S |  |  |  | TVAHP096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204269074 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B52S |  |  |  | TVAHP120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204269088 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B52S |  |  |  | HVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269089 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B52S |  |  |  | HVAHP096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204269090 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B52S |  |  |  | HVAHP120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204269104 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B52S |  |  |  | YVAHP072B52S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
204269105 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B52S |  |  |  | YVAHP096B52S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
204269106 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B52S |  |  |  | YVAHP120B52S | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5
204442713 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH |  |  |  | AM072FXVAFH | Non-Ducted Indoor Units | 69000 | 13 | 29.7 | 77000 | 3.71 | 51000 | 2.73 | R-410A | 5.75
204442714 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAFH |  |  |  | AM096FXVAFH | Non-Ducted Indoor Units | 92000 | 12.7 | 28.6 | 103000 | 3.86 | 67000 | 2.65 | R-410A | 7.6667
204442728 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH |  |  |  | AM072FXVAJH | Non-Ducted Indoor Units | 69000 | 13 | 29.7 | 77000 | 3.71 | 51000 | 2.73 | R-410A | 5.75
204442729 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAJH |  |  |  | AM096FXVAJH | Non-Ducted Indoor Units | 92000 | 12.7 | 28.6 | 103000 | 3.86 | 67000 | 2.65 | R-410A | 7.6667
204442744 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR |  |  |  | AM072FXVAFR | Non-Ducted Indoor Units | 69000 | 13 | 29.7 | 77000 | 3.71 | 51000 | 2.73 | R-410A | 5.75
204442745 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Non-Ducted Indoor Units | 92000 | 12.7 | 28.6 | 103000 | 3.86 | 67000 | 2.65 | R-410A | 7.6667
9956607 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER096C432Y |  |  |  | VER096C432Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
9956574 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432Y |  |  |  | VEP120C432Y | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
9956601 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER120C432Y |  |  |  | VER120C432Y | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 11.25 | 23.4 | 126000 | 3.4 | 83000 | 2.25 | R-410A | 9.25
9956564 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
9956571 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
9550137 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Non-Ducted Indoor Units | 69000 | 15.4 | 28.4 | 77000 | 4.11 | 56000 | 2.82 | R-410A | 5.75
9550159 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Ducted Indoor Units | 69000 | 13.2 | 20.6 | 77000 | 3.5 | 56000 | 2.49 | R-410A | 5.75
9680959 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL |  |  |  | MMY-MAP0726FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.3 | 24.5 | 77000 | 3.8 | 56000 | 2.65 | R-410A | 5.75
9133488 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC72K/220V |  |  |  | TVRF-SHC72K/220V | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
9133489 | 1/1/2027 | TOSOT | HMSR-A-CB | TVRF-SHC96K/220V |  |  |  | TVRF-SHC96K/220V | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
9302718 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 |  |  |  | 38VMA120HDS5-1 | Ducted Indoor Units | 112000 | 11.2 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.3333
9302719 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 |  |  |  | 38VMA120HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 112000 | 11.45 | 22.2 | 120000 | 3.52 | 80000 | 2.34 | R-410A | 9.3333
9302720 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 |  |  |  | 38VMA120HDS5-1 | Non-Ducted Indoor Units | 112000 | 11.7 | 22.5 | 120000 | 3.6 | 80000 | 2.38 | R-410A | 9.3333
9302721 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 |  |  |  | 38VMA120HDS6-1 | Ducted Indoor Units | 112000 | 11.2 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.3333
9302722 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 |  |  |  | 38VMA120HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 112000 | 11.45 | 22.2 | 120000 | 3.52 | 80000 | 2.34 | R-410A | 9.3333
9302723 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 |  |  |  | 38VMA120HDS6-1 | Non-Ducted Indoor Units | 112000 | 11.7 | 22.5 | 120000 | 3.6 | 80000 | 2.38 | R-410A | 9.3333
9363538 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 12.8 | 23.6 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9363539 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.05 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
9363540 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 22.5 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
9363541 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 12.8 | 23.6 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9363542 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.05 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
9363544 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 22.5 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
9363545 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Ducted Indoor Units | 92000 | 11.8 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
9363546 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 23.25 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
9363547 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.5 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9363549 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Ducted Indoor Units | 92000 | 11.8 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
9363550 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 23.25 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
9363551 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.5 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
10035438 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR |  |  |  | AM072KXVTFR | Non-Ducted Indoor Units | 69000 | 11.3 | 29.3 | 77000 | 3.41 | 77000 | 2.25 | R-410A | 5.75
10035439 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR |  |  |  | AM096KXVTFR | Non-Ducted Indoor Units | 92000 | 11.9 | 28.3 | 103000 | 3.61 | 103000 | 2.25 | R-410A | 7.6667
10035456 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR |  |  |  | AM072KXVTJR | Non-Ducted Indoor Units | 69000 | 11.3 | 29.3 | 77000 | 3.41 | 77000 | 2.25 | R-410A | 5.75
10035457 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR |  |  |  | AM096KXVTJR | Non-Ducted Indoor Units | 92000 | 11.9 | 28.3 | 103000 | 3.61 | 103000 | 2.25 | R-410A | 7.6667
10323534 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10323535 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10323536 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10323550 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10323551 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10323552 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10323566 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10323567 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10323568 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10323582 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10323583 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10323584 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10323598 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10323599 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10323600 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10323614 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10323615 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10323616 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10323630 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10323631 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10323632 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10323646 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10323647 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10323648 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10323662 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10323663 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10323664 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10323678 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10323679 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10323680 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10323694 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10323695 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10323696 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10323710 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10323711 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10323712 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10323728 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B42S |  |  |  | TVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10323729 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B42S |  |  |  | TVAHR096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10323730 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S |  |  |  | TVAHR120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10323744 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B42S |  |  |  | HVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10323745 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B42S |  |  |  | HVAHR096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10323746 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S |  |  |  | HVAHR120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10323760 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B42S |  |  |  | YVAHR072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10323761 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B42S |  |  |  | YVAHR096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10323762 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S |  |  |  | YVAHR120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10323777 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B32S |  |  |  | TVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10323778 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B32S |  |  |  | TVAHR096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10323779 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S |  |  |  | TVAHR120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10323793 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B32S |  |  |  | HVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10323794 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B32S |  |  |  | HVAHR096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10323795 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S |  |  |  | HVAHR120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10323809 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B32S |  |  |  | YVAHR072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10323810 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B32S |  |  |  | YVAHR096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10323811 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S |  |  |  | YVAHR120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10103102 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* |  |  |  | RELQ72TAYC* | Non-Ducted Indoor Units | 69000 | 15.8 | 24 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
10103103 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* |  |  |  | RELQ96TAYC* | Non-Ducted Indoor Units | 92000 | 15.3 | 24.8 | 103000 | 4.23 | 86000 | 2.5 | R-410A | 7.6667
10103104 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* |  |  |  | RELQ120TAYC* | Non-Ducted Indoor Units | 114000 | 13.7 | 23.4 | 129000 | 3.98 | 110000 | 2.25 | R-410A | 9.5
10103108 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYC* |  |  |  | REYQ72TAYC* | Non-Ducted Indoor Units | 69000 | 15.8 | 24 | 77000 | 4.3 | 58000 | 2.5 | R-410A | 5.75
10103109 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* |  |  |  | REYQ96TAYC* | Non-Ducted Indoor Units | 92000 | 14.6 | 25.1 | 103000 | 4.23 | 72000 | 2.63 | R-410A | 7.6667
10103110 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* |  |  |  | REYQ120TAYC* | Non-Ducted Indoor Units | 114000 | 13.1 | 23.4 | 129000 | 3.81 | 88000 | 2.54 | R-410A | 9.5
10103123 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* |  |  |  | RELQ72TAYC* | Ducted Indoor Units | 69000 | 13.7 | 20.8 | 77000 | 3.68 | 58000 | 2.3 | R-410A | 5.75
10103124 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* |  |  |  | RELQ96TAYC* | Ducted Indoor Units | 92000 | 12.5 | 19.1 | 103000 | 3.42 | 86000 | 2.25 | R-410A | 7.6667
10103125 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* |  |  |  | RELQ120TAYC* | Ducted Indoor Units | 114000 | 12.4 | 19.6 | 129000 | 3.51 | 110000 | 2.25 | R-410A | 9.5
10103129 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* |  |  |  | RELQ72TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.75 | 22.4 | 77000 | 3.99 | 58000 | 2.4 | R-410A | 5.75
10103130 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* |  |  |  | RELQ96TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.9 | 21.95 | 103000 | 3.82 | 86000 | 2.37 | R-410A | 7.6667
10103131 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* |  |  |  | RELQ120TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 13.05 | 21.5 | 129000 | 3.74 | 110000 | 2.25 | R-410A | 9.5
10103135 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYC* |  |  |  | REYQ72TAYC* | Ducted Indoor Units | 69000 | 13.8 | 20.8 | 77000 | 3.68 | 58000 | 2.25 | R-410A | 5.75
10103136 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* |  |  |  | REYQ96TAYC* | Ducted Indoor Units | 92000 | 12.3 | 19.3 | 103000 | 3.56 | 72000 | 2.31 | R-410A | 7.6667
10103137 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* |  |  |  | REYQ120TAYC* | Ducted Indoor Units | 114000 | 12 | 19.6 | 129000 | 3.48 | 88000 | 2.28 | R-410A | 9.5
10103149 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYC* |  |  |  | REYQ72TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.8 | 22.4 | 77000 | 3.99 | 58000 | 2.37 | R-410A | 5.75
10103150 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* |  |  |  | REYQ96TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.45 | 22.2 | 103000 | 3.89 | 72000 | 2.47 | R-410A | 7.6667
10103151 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* |  |  |  | REYQ120TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.55 | 21.5 | 129000 | 3.64 | 88000 | 2.41 | R-410A | 9.5
10206676 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10206677 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10206678 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10206690 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10206691 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10206692 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10206704 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10206705 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10206706 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10206718 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10206719 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10206720 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10206732 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10206733 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10206734 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10206746 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Non-Ducted Indoor Units | 69000 | 14.9 | 26.5 | 77000 | 4.25 | 56000 | 2.6 | R-410A | 5.75
10206747 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Non-Ducted Indoor Units | 92000 | 12.4 | 23.9 | 103000 | 3.77 | 76000 | 2.4 | R-410A | 7.6667
10206748 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Non-Ducted Indoor Units | 115000 | 12.7 | 24.4 | 129000 | 3.84 | 92000 | 2.37 | R-410A | 9.5833
10206760 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10206761 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10206762 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10206774 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10206775 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10206776 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10206788 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10206789 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10206790 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10206802 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10206803 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10206804 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10206816 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10206817 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10206818 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10206830 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Ducted Indoor Units | 69000 | 12.2 | 21.1 | 77000 | 3.54 | 56000 | 2.38 | R-410A | 5.75
10206831 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Ducted Indoor Units | 92000 | 12.4 | 22.1 | 103000 | 3.65 | 76000 | 2.36 | R-410A | 7.6667
10206832 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Ducted Indoor Units | 115000 | 12.2 | 21.7 | 129000 | 3.55 | 92000 | 2.3 | R-410A | 9.5833
10207510 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B32S |  |  |  | TVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10207511 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B32S |  |  |  | TVAHP096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10207512 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S |  |  |  | TVAHP120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10207524 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B32S |  |  |  | HVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10207525 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B32S |  |  |  | HVAHP096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10207526 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S |  |  |  | HVAHP120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10207538 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B32S |  |  |  | YVAHP072B32S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10207539 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B32S |  |  |  | YVAHP096B32S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10207540 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S |  |  |  | YVAHP120B32S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10207552 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B42S |  |  |  | TVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10207553 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B42S |  |  |  | TVAHP096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10207554 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S |  |  |  | TVAHP120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10207566 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B42S |  |  |  | HVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10207567 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B42S |  |  |  | HVAHP096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10207568 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S |  |  |  | HVAHP120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
10207580 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B42S |  |  |  | YVAHP072B42S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.55 | 23.8 | 77000 | 3.89 | 56000 | 2.49 | R-410A | 5.75
10207581 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B42S |  |  |  | YVAHP096B42S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.71 | 76000 | 2.38 | R-410A | 7.6667
10207582 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S |  |  |  | YVAHP120B42S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.45 | 23.05 | 129000 | 3.69 | 92000 | 2.33 | R-410A | 9.5833
9302802 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Ducted Indoor Units | 69000 | 12.8 | 23.6 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9302803 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.05 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
9302804 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS5-1 |  |  |  | 38VMA072HDS5-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 22.5 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
9302805 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Ducted Indoor Units | 69000 | 12.8 | 23.6 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9302806 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.05 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
9302807 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA072HDS6-1 |  |  |  | 38VMA072HDS6-1 | Non-Ducted Indoor Units | 69000 | 14.1 | 22.5 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
9302808 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Ducted Indoor Units | 92000 | 11.8 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
9302809 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 23.25 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
9302810 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 |  |  |  | 38VMA096HDS5-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.5 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9302811 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Ducted Indoor Units | 92000 | 11.8 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
9302812 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 23.25 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
9302813 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 |  |  |  | 38VMA096HDS6-1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.5 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9363440 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 |  |  |  | 38VMA120HDS5-1 | Ducted Indoor Units | 112000 | 11.2 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.3333
9363441 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 |  |  |  | 38VMA120HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 112000 | 11.45 | 22.2 | 120000 | 3.52 | 80000 | 2.34 | R-410A | 9.3333
9363442 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 |  |  |  | 38VMA120HDS5-1 | Non-Ducted Indoor Units | 112000 | 11.7 | 22.5 | 120000 | 3.6 | 80000 | 2.38 | R-410A | 9.3333
9363443 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 |  |  |  | 38VMA120HDS6-1 | Ducted Indoor Units | 112000 | 11.2 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.3333
9363444 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 |  |  |  | 38VMA120HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 112000 | 11.45 | 22.2 | 120000 | 3.52 | 80000 | 2.34 | R-410A | 9.3333
9363445 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 |  |  |  | 38VMA120HDS6-1 | Non-Ducted Indoor Units | 112000 | 11.7 | 22.5 | 120000 | 3.6 | 80000 | 2.38 | R-410A | 9.3333
9989439 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TATJ* |  |  |  | RXYQ72TATJ* | Non-Ducted Indoor Units | 69000 | 14.7 | 25.8 | 73000 | 3.67 | 39000 | 2.44 | R-410A | 5.75
9989440 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* |  |  |  | RXYQ96TATJ* | Non-Ducted Indoor Units | 92000 | 14 | 27.3 | 103000 | 4 | 67000 | 2.63 | R-410A | 7.6667
9990029 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYD* |  |  |  | RXYQ72TAYD* | Non-Ducted Indoor Units | 69000 | 14.7 | 25.8 | 73000 | 3.67 | 39000 | 2.44 | R-410A | 5.75
9990030 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* |  |  |  | RXYQ96TAYD* | Non-Ducted Indoor Units | 92000 | 14 | 27.3 | 103000 | 4 | 67000 | 2.63 | R-410A | 7.6667
9990031 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* |  |  |  | RXYQ120TATJ* | Non-Ducted Indoor Units | 114000 | 12 | 25.4 | 129000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
9990046 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* |  |  |  | RXYQ96TATJ* | Ducted Indoor Units | 92000 | 12.6 | 22.5 | 103000 | 3.49 | 67000 | 2.48 | R-410A | 7.6667
9990047 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* |  |  |  | RXYQ96TAYD* | Ducted Indoor Units | 92000 | 12.6 | 22.5 | 103000 | 3.49 | 67000 | 2.48 | R-410A | 7.6667
9990048 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* |  |  |  | RXYQ120TAYD* | Non-Ducted Indoor Units | 114000 | 12 | 25.4 | 129000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
9990087 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TATJ* |  |  |  | RXYQ72TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.7 | 23.25 | 73000 | 3.48 | 39000 | 2.34 | R-410A | 5.75
9990088 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYD* |  |  |  | RXYQ72TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.7 | 23.25 | 73000 | 3.48 | 39000 | 2.34 | R-410A | 5.75
9990089 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* |  |  |  | RXYQ96TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.3 | 24.9 | 103000 | 3.74 | 67000 | 2.55 | R-410A | 7.6667
9990090 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* |  |  |  | RXYQ96TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.3 | 24.9 | 103000 | 3.74 | 67000 | 2.55 | R-410A | 7.6667
9990091 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* |  |  |  | RXYQ120TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 23.7 | 129000 | 3.4 | 81000 | 2.31 | R-410A | 9.5
9990092 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* |  |  |  | RXYQ120TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 23.7 | 129000 | 3.4 | 81000 | 2.31 | R-410A | 9.5
9990287 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 |  |  |  | AOUA72RLBV1 | Ducted Indoor Units | 69000 | 12.3 | 20 | 77000 | 3.64 | 56000 | 2.38 | R-410A | 5.75
9990288 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 |  |  |  | AOUA96RLBV1 | Ducted Indoor Units | 92000 | 11.3 | 20.2 | 103000 | 3.6 | 73000 | 2.42 | R-410A | 7.6667
9990289 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 |  |  |  | AOUA120RLBV1 | Ducted Indoor Units | 114000 | 11.3 | 20.1 | 129000 | 3.49 | 87000 | 2.41 | R-410A | 9.5
9990290 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 |  |  |  | AOUA72RLBV1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.4 | 22.05 | 77000 | 3.85 | 56000 | 2.45 | R-410A | 5.75
9990291 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 |  |  |  | AOUA96RLBV1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 21.9 | 103000 | 3.66 | 73000 | 2.44 | R-410A | 7.6667
9990292 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 |  |  |  | AOUA120RLBV1 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.3 | 21.95 | 129000 | 3.55 | 87000 | 2.42 | R-410A | 9.5
9088683 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC714 |  |  |  | IOV120H3CDC714 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
9121814 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q120WM/B-F(U) |  |  |  | GMV-Q120WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 11.25 | 23.4 | 126000 | 3.4 | 83000 | 2.25 | R-410A | 9.25
9121821 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/B-F(U) |  |  |  | GMV-Q96WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.1 | 22 | 100000 | 3.4 | 67000 | 2.32 | R-410A | 7.6667
9121934 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DXN1 |  |  |  | MV5-H72DXN1 | Non-Ducted Indoor Units | 69000 | 14.1 | 22.5 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
9121935 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DXN1 |  |  |  | MV5-H72DXN1 | Ducted Indoor Units | 69000 | 12.8 | 23.6 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9121936 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DXN1 |  |  |  | MV5-H72DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.05 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
9121937 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 |  |  |  | MV5-H96DXN1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.5 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9121938 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 |  |  |  | MV5-H96DXN1 | Ducted Indoor Units | 92000 | 11.8 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
9088673 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712 |  |  |  | IOV072H3CDC712 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
9088680 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC713 |  |  |  | IOV096H3CDC736 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
9133443 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/220V |  |  |  | TVRF-OC72KHP/220V | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
9133481 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V |  |  |  | TVRF-OC96KHP/220V | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
9122304 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DZN1 |  |  |  | MV5-H72DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.05 | 77000 | 4.07 | 54000 | 2.6 | R-410A | 5.75
9122305 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 |  |  |  | MV5-H96DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 23.25 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
9122306 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 |  |  |  | MV5-H120DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 112000 | 11.45 | 22.2 | 120000 | 3.52 | 80000 | 2.34 | R-410A | 9.3333
9122947 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Non-Ducted Indoor Units | 69000 | 15.4 | 28.4 | 77000 | 4.11 | 56000 | 2.82 | R-410A | 5.75
9122948 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Non-Ducted Indoor Units | 92000 | 14.5 | 30.1 | 103000 | 4.31 | 76000 | 2.8 | R-410A | 7.6667
9122949 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Non-Ducted Indoor Units | 114000 | 13 | 29 | 129000 | 3.95 | 92000 | 2.6 | R-410A | 9.5
9122968 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Ducted Indoor Units | 69000 | 13.2 | 20.6 | 77000 | 3.5 | 56000 | 2.49 | R-410A | 5.75
9122969 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Non-Ducted Indoor Units | 69000 | 15.4 | 28.4 | 77000 | 4.11 | 56000 | 2.82 | R-410A | 5.75
9122970 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Ducted Indoor Units | 69000 | 13.2 | 20.6 | 77000 | 3.5 | 56000 | 2.49 | R-410A | 5.75
9122971 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Ducted Indoor Units | 92000 | 12.2 | 22.8 | 103000 | 3.8 | 76000 | 2.6 | R-410A | 7.6667
9122972 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Non-Ducted Indoor Units | 92000 | 14.5 | 30.1 | 103000 | 4.31 | 76000 | 2.8 | R-410A | 7.6667
9122973 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Ducted Indoor Units | 92000 | 12.2 | 22.8 | 103000 | 3.8 | 76000 | 2.6 | R-410A | 7.6667
9122974 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Ducted Indoor Units | 114000 | 12.3 | 21.1 | 129000 | 3.53 | 92000 | 2.5 | R-410A | 9.5
9122975 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Non-Ducted Indoor Units | 114000 | 13 | 29 | 129000 | 3.95 | 92000 | 2.6 | R-410A | 9.5
9122976 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Ducted Indoor Units | 114000 | 12.3 | 21.1 | 129000 | 3.53 | 92000 | 2.5 | R-410A | 9.5
9123031 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT6P-UL |  |  |  | MMY-MAP0726FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.3 | 24.5 | 77000 | 3.8 | 56000 | 2.65 | R-410A | 5.75
9123032 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT9P-UL |  |  |  | MMY-MAP0726FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.3 | 24.5 | 77000 | 3.8 | 56000 | 2.65 | R-410A | 5.75
9123033 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL |  |  |  | MMY-MAP0966FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.35 | 26.45 | 103000 | 4.05 | 76000 | 2.7 | R-410A | 7.6667
9123034 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL |  |  |  | MMY-MAP0966FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.35 | 26.45 | 103000 | 4.05 | 76000 | 2.7 | R-410A | 7.6667
9123035 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL |  |  |  | MMY-MAP1206FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.65 | 25.05 | 129000 | 3.74 | 92000 | 2.55 | R-410A | 9.5
9123036 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL |  |  |  | MMY-MAP1206FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.65 | 25.05 | 129000 | 3.74 | 92000 | 2.55 | R-410A | 9.5
9121941 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 |  |  |  | MV5-H120DXN1 | Non-Ducted Indoor Units | 112000 | 11.7 | 22.5 | 120000 | 3.6 | 80000 | 2.38 | R-410A | 9.3333
9121942 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 |  |  |  | MV5-H120DXN1 | Ducted Indoor Units | 112000 | 11.2 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.3333
9121943 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 |  |  |  | MV5-H96DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.5 | 23.25 | 103000 | 3.72 | 72000 | 2.41 | R-410A | 7.6667
9121944 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 |  |  |  | MV5-H120DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 112000 | 11.45 | 22.2 | 120000 | 3.52 | 80000 | 2.34 | R-410A | 9.3333
9121951 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DZN1 |  |  |  | MV5-H72DZN1 | Non-Ducted Indoor Units | 69000 | 14.1 | 22.5 | 77000 | 4.29 | 54000 | 2.8 | R-410A | 5.75
9121952 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H72DZN1 |  |  |  | MV5-H72DZN1 | Ducted Indoor Units | 69000 | 12.8 | 23.6 | 77000 | 3.85 | 54000 | 2.41 | R-410A | 5.75
9121953 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 |  |  |  | MV5-H96DZN1 | Non-Ducted Indoor Units | 92000 | 13.2 | 23.5 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
9121954 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 |  |  |  | MV5-H96DZN1 | Ducted Indoor Units | 92000 | 11.8 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
9121981 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 |  |  |  | MV5-H120DZN1 | Non-Ducted Indoor Units | 112000 | 11.7 | 22.5 | 120000 | 3.6 | 80000 | 2.38 | R-410A | 9.3333
9121982 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 |  |  |  | MV5-H120DZN1 | Ducted Indoor Units | 112000 | 11.2 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.3333
9045746 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW |  |  |  | TVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
9045748 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW |  |  |  | TVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
9045770 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW |  |  |  | HVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
9045772 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW |  |  |  | HVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
9045794 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW |  |  |  | YVAHP096B31CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
9045796 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW |  |  |  | YVAHP096B41CW | Non-Ducted Indoor Units | 92000 | 11.9 | 18.9 | 103000 | 3.8 | 87000 | 2.27 | R-410A | 7.6667
9085396 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Non-Ducted Indoor Units | 69000 | 15 | 29 | 77000 | 4.3 | 56000 | 2.7 | R-410A | 5.75
9085397 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Ducted Indoor Units | 69000 | 13.7 | 23.4 | 77000 | 3.88 | 56000 | 2.8 | R-410A | 5.75
9085398 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Non-Ducted Indoor Units | 92000 | 15.3 | 30.2 | 103000 | 4.8 | 76000 | 2.95 | R-410A | 7.6667
9085399 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Ducted Indoor Units | 92000 | 13.5 | 23.1 | 103000 | 4.1 | 76000 | 2.9 | R-410A | 7.6667
9085400 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Non-Ducted Indoor Units | 114000 | 13 | 25.4 | 129000 | 4 | 92000 | 2.8 | R-410A | 9.5
9085401 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Ducted Indoor Units | 114000 | 12.2 | 22.3 | 129000 | 3.95 | 92000 | 2.8 | R-410A | 9.5
9085438 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0726HT9P-UL |  |  |  | MMY-MAP0726HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.35 | 26.2 | 77000 | 4.09 | 56000 | 2.75 | R-410A | 5.75
9085439 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL |  |  |  | MMY-MAP0966HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.4 | 26.65 | 103000 | 4.45 | 76000 | 2.92 | R-410A | 7.6667
9085440 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL |  |  |  | MMY-MAP1206HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.6 | 23.85 | 129000 | 3.97 | 92000 | 2.8 | R-410A | 9.5
8552534 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PCTJ |  |  |  | REYQ96PCTJ | Non-Ducted Indoor Units | 90000 | 13.2 | 22.9 | 103000 | 3.7 | 69000 | 2.7 | R-410A | 7.5
8656992 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72ZKMU-A |  |  |  | PURY-P72ZKMU-A | Non-Ducted Indoor Units | 69000 | 13.1 | 21.3 | 76000 | 3.62 | 56000 | 2.26 | R-410A | 5.75
8656994 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96ZKMU-A |  |  |  | PURY-P96ZKMU-A | Non-Ducted Indoor Units | 92000 | 12.4 | 22.7 | 103000 | 3.46 | 71000 | 2.26 | R-410A | 7.6667
8656996 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120ZKMU-A |  |  |  | PURY-P120ZKMU-A | Non-Ducted Indoor Units | 114000 | 13.2 | 22.3 | 129000 | 3.5 | 87000 | 2.26 | R-410A | 9.5
8657012 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72ZKMU-A |  |  |  | PUHY-P72ZKMU-A | Non-Ducted Indoor Units | 69000 | 13.6 | 25.9 | 76000 | 3.85 | 56000 | 2.25 | R-410A | 5.75
8657014 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96ZKMU-A |  |  |  | PUHY-P96ZKMU-A | Non-Ducted Indoor Units | 92000 | 13.2 | 25.6 | 103000 | 3.74 | 76000 | 2.42 | R-410A | 7.6667
8657016 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A |  |  |  | PUHY-P120ZKMU-A | Non-Ducted Indoor Units | 114000 | 13.7 | 24.2 | 129000 | 3.87 | 92000 | 2.3 | R-410A | 9.5
8989551 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Non-Ducted Indoor Units | 69000 | 15 | 29 | 77000 | 4.3 | 56000 | 2.7 | R-410A | 5.75
8989552 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Non-Ducted Indoor Units | 92000 | 15.3 | 30.2 | 103000 | 4.8 | 76000 | 2.95 | R-410A | 7.6667
8989553 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Non-Ducted Indoor Units | 114000 | 13 | 25.4 | 129000 | 4 | 92000 | 2.8 | R-410A | 9.5
8989566 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Ducted Indoor Units | 69000 | 13.7 | 23.4 | 77000 | 3.88 | 56000 | 2.8 | R-410A | 5.75
8989567 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Ducted Indoor Units | 92000 | 13.5 | 23.1 | 103000 | 4.1 | 76000 | 2.9 | R-410A | 7.6667
8989568 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Ducted Indoor Units | 114000 | 12.2 | 22.3 | 129000 | 3.95 | 92000 | 2.8 | R-410A | 9.5
8989607 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0726HT6P-UL |  |  |  | MMY-MAP0726HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.35 | 26.2 | 77000 | 4.09 | 56000 | 2.75 | R-410A | 5.75
8989608 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0966HT6P-UL |  |  |  | MMY-MAP0966HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.4 | 26.65 | 103000 | 4.45 | 76000 | 2.92 | R-410A | 7.6667
8989609 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL |  |  |  | MMY-MAP1206HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.6 | 23.85 | 129000 | 3.97 | 92000 | 2.8 | R-410A | 9.5
8683032 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVHFH |  |  |  | AM072KXVHFH | Non-Ducted Indoor Units | 69000 | 15.5 | 40 | 77000 | 4.5 | 77000 | 2.45 | R-410A | 5.75
8683033 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVHFH |  |  |  | AM096KXVHFH | Non-Ducted Indoor Units | 92000 | 15.5 | 38.6 | 103000 | 4.65 | 103000 | 2.4 | R-410A | 7.6667
8683034 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVHJH |  |  |  | AM072KXVHJH | Non-Ducted Indoor Units | 69000 | 15.5 | 40 | 77000 | 4.5 | 77000 | 2.45 | R-410A | 5.75
8683035 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVHJH |  |  |  | AM096KXVHJH | Non-Ducted Indoor Units | 92000 | 15.5 | 38.6 | 103000 | 4.65 | 103000 | 2.4 | R-410A | 7.6667
8797068 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH |  |  |  | AM072KXVTFH | Non-Ducted Indoor Units | 69000 | 11.3 | 29.3 | 77000 | 3.41 | 77000 | 2.25 | R-410A | 5.75
8797069 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH |  |  |  | AM096KXVTFH | Non-Ducted Indoor Units | 92000 | 11.9 | 28.3 | 103000 | 3.61 | 103000 | 2.25 | R-410A | 7.6667
8797070 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH |  |  |  | AM072KXVTJH | Non-Ducted Indoor Units | 69000 | 11.3 | 29.3 | 77000 | 3.41 | 77000 | 2.25 | R-410A | 5.75
8797071 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH |  |  |  | AM096KXVTJH | Non-Ducted Indoor Units | 92000 | 11.9 | 28.3 | 103000 | 3.61 | 103000 | 2.25 | R-410A | 7.6667
8556905 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PCTJ |  |  |  | REYQ96PCTJ | Mixed Ducted and Non-Ducted Indoor Units | 90000 | 12.2 | 21.3 | 103000 | 3.65 | 69000 | 2.67 | R-410A | 7.5
8554690 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PCTJ |  |  |  | REYQ96PCTJ | Ducted Indoor Units | 90000 | 11.2 | 19.7 | 103000 | 3.6 | 69000 | 2.65 | R-410A | 7.5
8554691 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PCYD |  |  |  | REYQ96PCYD | Ducted Indoor Units | 90000 | 11.2 | 19.7 | 103000 | 3.6 | 69000 | 2.65 | R-410A | 7.5
8635954 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PCYD |  |  |  | REYQ96PCYD | Non-Ducted Indoor Units | 90000 | 13.2 | 22.9 | 103000 | 3.7 | 69000 | 2.7 | R-410A | 7.5
8635955 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PCYD |  |  |  | REYQ96PCYD | Mixed Ducted and Non-Ducted Indoor Units | 90000 | 12.2 | 21.3 | 103000 | 3.65 | 69000 | 2.67 | R-410A | 7.5
7041873 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TTJU |  |  |  | RXYQ72TTJU | Ducted Indoor Units | 69000 | 13.5 | 22.8 | 77000 | 3.58 | 43000 | 2.25 | R-410A | 5.75
7041874 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TYDN |  |  |  | RXYQ72TYDN | Ducted Indoor Units | 69000 | 13.5 | 22.8 | 77000 | 3.58 | 43000 | 2.25 | R-410A | 5.75
7041875 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TTJU |  |  |  | RXYQ72TTJU | Non-Ducted Indoor Units | 69000 | 15 | 26.5 | 77000 | 4.21 | 43000 | 2.49 | R-410A | 5.75
7041876 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TYDN |  |  |  | RXYQ72TYDN | Non-Ducted Indoor Units | 69000 | 15 | 26.5 | 77000 | 4.21 | 43000 | 2.49 | R-410A | 5.75
7041877 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU |  |  |  | RXYQ96TTJU | Ducted Indoor Units | 92000 | 13 | 22.7 | 103000 | 3.99 | 67000 | 2.61 | R-410A | 7.6667
7041878 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN |  |  |  | RXYQ96TYDN | Ducted Indoor Units | 92000 | 13 | 22.7 | 103000 | 3.99 | 67000 | 2.61 | R-410A | 7.6667
7041879 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU |  |  |  | RXYQ96TTJU | Non-Ducted Indoor Units | 92000 | 15.1 | 28 | 103000 | 4.59 | 67000 | 2.86 | R-410A | 7.6667
7041880 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN |  |  |  | RXYQ96TYDN | Non-Ducted Indoor Units | 92000 | 15.1 | 28 | 103000 | 4.59 | 67000 | 2.86 | R-410A | 7.6667
7041881 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU |  |  |  | RXYQ120TTJU | Ducted Indoor Units | 114000 | 12.1 | 21.4 | 129000 | 3.46 | 85000 | 2.58 | R-410A | 9.5
7041882 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN |  |  |  | RXYQ120TYDN | Ducted Indoor Units | 114000 | 12.1 | 21.4 | 129000 | 3.46 | 85000 | 2.58 | R-410A | 9.5
7041883 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU |  |  |  | RXYQ120TTJU | Non-Ducted Indoor Units | 114000 | 13.2 | 23.5 | 129000 | 3.79 | 85000 | 2.61 | R-410A | 9.5
7041884 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN |  |  |  | RXYQ120TYDN | Non-Ducted Indoor Units | 114000 | 13.2 | 23.5 | 129000 | 3.79 | 85000 | 2.61 | R-410A | 9.5
7042709 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TTJU |  |  |  | RXYQ72TTJU | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.25 | 24.65 | 77000 | 3.89 | 43000 | 2.37 | R-410A | 5.75
7042710 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TYDN |  |  |  | RXYQ72TYDN | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.25 | 24.65 | 77000 | 3.89 | 43000 | 2.37 | R-410A | 5.75
7042711 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU |  |  |  | RXYQ96TTJU | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.05 | 25.35 | 103000 | 4.29 | 67000 | 2.73 | R-410A | 7.6667
7042712 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN |  |  |  | RXYQ96TYDN | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 14.05 | 25.35 | 103000 | 4.29 | 67000 | 2.73 | R-410A | 7.6667
7042713 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU |  |  |  | RXYQ120TTJU | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.65 | 22.45 | 129000 | 3.62 | 85000 | 2.59 | R-410A | 9.5
7042714 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN |  |  |  | RXYQ120TYDN | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.65 | 22.45 | 129000 | 3.62 | 85000 | 2.59 | R-410A | 9.5
7159057 | 1/1/2027 | PANASONIC | HMSV-A-CB | U-96ME2U9 |  |  |  | U-96ME2U9 | Non-Ducted Indoor Units | 92000 | 12.5 | 25.3 | 103000 | 3.92 | 67000 | 2.71 | R-410A | 7.6667
7159060 | 1/1/2027 | PANASONIC | HMSV-A-CB | U-120ME2U9 |  |  |  | U-120ME2U9 | Non-Ducted Indoor Units | 114000 | 12.1 | 26.4 | 129000 | 3.7 | 75000 | 2.48 | R-410A | 9.5
7160224 | 1/1/2027 | PANASONIC | HMSV-A-CB | U-72ME2U9 |  |  |  | U-72ME2U9 | Mixed Ducted and Non-Ducted Indoor Units | 72000 | 13.25 | 21.8 | 77000 | 4.08 | 52000 | 2.85 | R-410A | 6
7465339 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DXN1-(A) |  |  |  | MV5-R72DXN1-(A) | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7465340 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DXN1-(A) |  |  |  | MV5-R72DXN1-(A) | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7465341 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) |  |  |  | MV5-R96DXN1-(A) | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
7465342 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) |  |  |  | MV5-R96DXN1-(A) | Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
7465343 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) |  |  |  | MV5-R120DXN1-(A) | Non-Ducted Indoor Units | 114000 | 12.2 | 22.8 | 120000 | 3.66 | 80000 | 2.38 | R-410A | 9.5
7465344 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) |  |  |  | MV5-R120DXN1-(A) | Ducted Indoor Units | 114000 | 11.4 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
7465345 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DXN1-(A) |  |  |  | MV5-X72DXN1-(A) | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7465346 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DXN1-(A) |  |  |  | MV5-X72DXN1-(A) | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7465347 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) |  |  |  | MV5-X96DXN1-(A) | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
7465348 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) |  |  |  | MV5-X96DXN1-(A) | Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
7465349 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) |  |  |  | MV5-X120DXN1-(A) | Non-Ducted Indoor Units | 114000 | 12.2 | 22.8 | 120000 | 3.66 | 80000 | 2.38 | R-410A | 9.5
7465350 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) |  |  |  | MV5-X120DXN1-(A) | Ducted Indoor Units | 114000 | 11.4 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
7490338 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U |  |  |  | PUHY-P120TKMU-U | Ducted Indoor Units | 114000 | 12.5 | 19.1 | 129000 | 3.66 | 92000 | 2.51 | R-410A | 9.5
7490339 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U |  |  |  | PUHY-P120TKMU-U | Non-Ducted Indoor Units | 114000 | 12.7 | 19.1 | 129000 | 3.83 | 92000 | 2.38 | R-410A | 9.5
7490340 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U |  |  |  | PUHY-P120YKMU-U | Ducted Indoor Units | 114000 | 12.5 | 19.1 | 129000 | 3.66 | 92000 | 2.51 | R-410A | 9.5
7490341 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U |  |  |  | PUHY-P120YKMU-U | Non-Ducted Indoor Units | 114000 | 12.7 | 19.1 | 129000 | 3.83 | 92000 | 2.38 | R-410A | 9.5
7490413 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TKMU-U |  |  |  | PUHY-P72TKMU-U | Ducted Indoor Units | 69000 | 13 | 19.8 | 76000 | 3.83 | 56000 | 2.59 | R-410A | 5.75
7490415 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TKMU-U |  |  |  | PUHY-P72TKMU-U | Non-Ducted Indoor Units | 69000 | 14.2 | 21.3 | 76000 | 4.19 | 56000 | 2.39 | R-410A | 5.75
7490417 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-U |  |  |  | PUHY-P72YKMU-U | Ducted Indoor Units | 69000 | 13 | 19.8 | 76000 | 3.83 | 56000 | 2.59 | R-410A | 5.75
7490419 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-U |  |  |  | PUHY-P72YKMU-U | Non-Ducted Indoor Units | 69000 | 14.2 | 21.3 | 76000 | 4.19 | 56000 | 2.39 | R-410A | 5.75
7490421 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-U |  |  |  | PUHY-P96TKMU-U | Ducted Indoor Units | 92000 | 12.6 | 19.7 | 103000 | 3.95 | 76000 | 2.71 | R-410A | 7.6667
7490423 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-U |  |  |  | PUHY-P96TKMU-U | Non-Ducted Indoor Units | 92000 | 13.7 | 20.7 | 103000 | 4.22 | 76000 | 2.68 | R-410A | 7.6667
7490424 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-U |  |  |  | PUHY-P96YKMU-U | Ducted Indoor Units | 92000 | 12.6 | 19.7 | 103000 | 3.95 | 76000 | 2.71 | R-410A | 7.6667
7490425 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-U |  |  |  | PUHY-P96YKMU-U | Non-Ducted Indoor Units | 92000 | 13.7 | 20.7 | 103000 | 4.22 | 76000 | 2.68 | R-410A | 7.6667
7490427 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-U |  |  |  | PURY-P120TKMU-U | Non-Ducted Indoor Units | 114000 | 12.2 | 20.8 | 129000 | 3.61 | 92000 | 2.42 | R-410A | 9.5
7490429 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-U |  |  |  | PURY-P120YKMU-U | Non-Ducted Indoor Units | 114000 | 12.2 | 20.8 | 129000 | 3.61 | 92000 | 2.42 | R-410A | 9.5
7490464 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TKMU-U |  |  |  | PURY-P72TKMU-U | Ducted Indoor Units | 69000 | 13.9 | 21.1 | 76000 | 3.81 | 56000 | 2.62 | R-410A | 5.75
7490465 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TKMU-U |  |  |  | PURY-P72TKMU-U | Non-Ducted Indoor Units | 69000 | 15.5 | 22.1 | 76000 | 3.72 | 56000 | 2.49 | R-410A | 5.75
7490467 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-U |  |  |  | PURY-P72YKMU-U | Ducted Indoor Units | 69000 | 13.9 | 21.1 | 76000 | 3.81 | 56000 | 2.62 | R-410A | 5.75
7490468 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-U |  |  |  | PURY-P72YKMU-U | Non-Ducted Indoor Units | 69000 | 15.5 | 22.1 | 76000 | 3.72 | 56000 | 2.49 | R-410A | 5.75
7490470 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-U |  |  |  | PURY-P96TKMU-U | Ducted Indoor Units | 92000 | 12.2 | 19.7 | 103000 | 3.64 | 76000 | 2.47 | R-410A | 7.6667
7490471 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-U |  |  |  | PURY-P96TKMU-U | Non-Ducted Indoor Units | 92000 | 13.6 | 20.9 | 103000 | 3.71 | 76000 | 2.49 | R-410A | 7.6667
7490472 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-U |  |  |  | PURY-P96YKMU-U | Ducted Indoor Units | 92000 | 12.2 | 19.7 | 103000 | 3.64 | 76000 | 2.47 | R-410A | 7.6667
7490473 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-U |  |  |  | PURY-P96YKMU-U | Non-Ducted Indoor Units | 92000 | 13.6 | 20.9 | 103000 | 3.71 | 76000 | 2.49 | R-410A | 7.6667
7499011 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DZN1-(A) |  |  |  | MV5-R72DZN1-(A) | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7499012 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R72DZN1-(A) |  |  |  | MV5-R72DZN1-(A) | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7499013 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) |  |  |  | MV5-R96DZN1-(A) | Non-Ducted Indoor Units | 92000 | 13.2 | 23.7 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
7499014 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) |  |  |  | MV5-R96DZN1-(A) | Ducted Indoor Units | 92000 | 12.4 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
7499015 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) |  |  |  | MV5-R120DZN1-(A) | Non-Ducted Indoor Units | 112000 | 12.2 | 22.8 | 120000 | 3.66 | 80000 | 2.38 | R-410A | 9.3333
7499016 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DZN1-(A) |  |  |  | MV5-X72DZN1-(A) | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7499017 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X72DZN1-(A) |  |  |  | MV5-X72DZN1-(A) | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7499018 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) |  |  |  | MV5-X96DZN1-(A) | Non-Ducted Indoor Units | 92000 | 13.2 | 23.5 | 103000 | 3.82 | 72000 | 2.52 | R-410A | 7.6667
7499019 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) |  |  |  | MV5-X96DZN1-(A) | Ducted Indoor Units | 92000 | 12.3 | 23 | 103000 | 3.63 | 72000 | 2.3 | R-410A | 7.6667
7499020 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) |  |  |  | MV5-X120DZN1-(A) | Non-Ducted Indoor Units | 114000 | 12.2 | 22.5 | 120000 | 3.66 | 80000 | 2.38 | R-410A | 9.5
7499021 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) |  |  |  | MV5-X120DZN1-(A) | Ducted Indoor Units | 114000 | 11.2 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.5
7499022 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) |  |  |  | MV5-R120DZN1-(A) | Ducted Indoor Units | 112000 | 11.4 | 21.9 | 120000 | 3.45 | 80000 | 2.3 | R-410A | 9.3333
7502097 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C4000AA |  |  |  | 4TVR0072C4000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7502098 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C4000AA |  |  |  | 4TVR0072C4000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7502109 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C6000AA |  |  |  | 4TVR0072C6000AA | Non-Ducted Indoor Units | 69000 | 13.8 | 23.6 | 77000 | 4.25 | 54000 | 2.65 | R-410A | 5.75
7502110 | 1/1/2027 | TRANE | HMSR-A-CB | 4TVR0072C6000AA |  |  |  | 4TVR0072C6000AA | Ducted Indoor Units | 69000 | 12 | 22.7 | 77000 | 3.69 | 54000 | 2.41 | R-410A | 5.75
7505310 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBTJ |  |  |  | REYQ72PBTJ | Non-Ducted Indoor Units | 69000 | 15.4 | 25.1 | 77000 | 4.2 | 52000 | 2.95 | R-410A | 5.75
7505311 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBYD |  |  |  | REYQ72PBYD | Non-Ducted Indoor Units | 69000 | 15.4 | 25.1 | 77000 | 4.2 | 52000 | 2.95 | R-410A | 5.75
7505343 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ120PBTJ |  |  |  | REYQ120PBTJ | Non-Ducted Indoor Units | 114000 | 12.1 | 21.3 | 129000 | 3.6 | 87000 | 2.6 | R-410A | 9.5
7505344 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ120PBYD |  |  |  | REYQ120PBYD | Non-Ducted Indoor Units | 114000 | 12.1 | 21.3 | 129000 | 3.6 | 87000 | 2.6 | R-410A | 9.5
7505355 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBTJ |  |  |  | REYQ72PBTJ | Ducted Indoor Units | 69000 | 13.8 | 21.3 | 77000 | 3.8 | 52000 | 2.6 | R-410A | 5.75
7505356 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBYD |  |  |  | REYQ72PBYD | Ducted Indoor Units | 69000 | 13.8 | 21.3 | 77000 | 3.8 | 52000 | 2.6 | R-410A | 5.75
7505357 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBTJ |  |  |  | REYQ96PBTJ | Non-Ducted Indoor Units | 92000 | 13.2 | 22.9 | 103000 | 3.7 | 69000 | 2.7 | R-410A | 7.6667
7505358 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBTJ |  |  |  | REYQ96PBTJ | Ducted Indoor Units | 92000 | 12.1 | 19.7 | 103000 | 3.6 | 69000 | 2.65 | R-410A | 7.6667
7505359 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBYD |  |  |  | REYQ96PBYD | Non-Ducted Indoor Units | 92000 | 13.2 | 22.9 | 103000 | 3.7 | 69000 | 2.7 | R-410A | 7.6667
7505360 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBYD |  |  |  | REYQ96PBYD | Ducted Indoor Units | 92000 | 12.1 | 19.7 | 103000 | 3.6 | 69000 | 2.65 | R-410A | 7.6667
7505428 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBTJ |  |  |  | REYQ72PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.6 | 23.2 | 77000 | 4 | 52000 | 2.77 | R-410A | 5.75
7505429 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBYD |  |  |  | REYQ72PBYD | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.6 | 23.2 | 77000 | 4 | 52000 | 2.77 | R-410A | 5.75
7505430 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBTJ |  |  |  | REYQ96PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.65 | 21.3 | 103000 | 3.65 | 69000 | 2.67 | R-410A | 7.6667
7505431 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBYD |  |  |  | REYQ96PBYD | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.65 | 21.3 | 103000 | 3.65 | 69000 | 2.67 | R-410A | 7.6667
7628329 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TTJU |  |  |  | REYQ72TTJU | Non-Ducted Indoor Units | 67000 | 15.8 | 26.2 | 75000 | 4.29 | 54000 | 2.77 | R-410A | 5.5833
7628332 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TYDN |  |  |  | REYQ72TYDN | Non-Ducted Indoor Units | 67000 | 15.8 | 26.2 | 75000 | 4.29 | 54000 | 2.77 | R-410A | 5.5833
7628545 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TTJU |  |  |  | REYQ96TTJU | Non-Ducted Indoor Units | 90000 | 15.1 | 29.3 | 100000 | 4.25 | 70000 | 2.63 | R-410A | 7.5
7628548 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TYDN |  |  |  | REYQ96TYDN | Non-Ducted Indoor Units | 90000 | 15.1 | 29.3 | 100000 | 4.25 | 70000 | 2.63 | R-410A | 7.5
7628550 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU |  |  |  | REYQ120TTJU | Non-Ducted Indoor Units | 111000 | 13.9 | 25.4 | 126000 | 3.98 | 86000 | 2.54 | R-410A | 9.25
7628553 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN |  |  |  | REYQ120TYDN | Non-Ducted Indoor Units | 111000 | 13.9 | 25.4 | 126000 | 3.98 | 86000 | 2.54 | R-410A | 9.25
7628613 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TTJU |  |  |  | REYQ72TTJU | Ducted Indoor Units | 67000 | 13.4 | 21.1 | 75000 | 3.82 | 54000 | 2.63 | R-410A | 5.5833
7628614 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TYDN |  |  |  | REYQ72TYDN | Ducted Indoor Units | 67000 | 13.4 | 21.1 | 75000 | 3.82 | 54000 | 2.63 | R-410A | 5.5833
7628617 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TTJU |  |  |  | REYQ96TTJU | Ducted Indoor Units | 90000 | 13.1 | 24.3 | 100000 | 3.72 | 70000 | 2.31 | R-410A | 7.5
7628619 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TYDN |  |  |  | REYQ96TYDN | Ducted Indoor Units | 90000 | 13.1 | 24.3 | 100000 | 3.72 | 70000 | 2.31 | R-410A | 7.5
7628621 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU |  |  |  | REYQ120TTJU | Ducted Indoor Units | 111000 | 12.6 | 22.6 | 126000 | 3.51 | 86000 | 2.32 | R-410A | 9.25
7628623 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN |  |  |  | REYQ120TYDN | Ducted Indoor Units | 111000 | 12.6 | 22.6 | 126000 | 3.51 | 86000 | 2.32 | R-410A | 9.25
7628952 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU |  |  |  | REYQ144TTJU | Non-Ducted Indoor Units | 134000 | 12.9 | 24.2 | 150000 | 3.81 | 106000 | 2.56 | R-410A | 11.1667
7628953 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN |  |  |  | REYQ144TYDN | Non-Ducted Indoor Units | 134000 | 12.9 | 24.2 | 150000 | 3.81 | 106000 | 2.56 | R-410A | 11.1667
7628979 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU |  |  |  | REYQ144TTJU | Ducted Indoor Units | 134000 | 11.9 | 22.2 | 150000 | 3.55 | 106000 | 2.35 | R-410A | 11.1667
7628982 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN |  |  |  | REYQ144TYDN | Ducted Indoor Units | 134000 | 11.9 | 22.2 | 150000 | 3.55 | 106000 | 2.35 | R-410A | 11.1667
7629573 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TTJU |  |  |  | REYQ72TTJU | Mixed Ducted and Non-Ducted Indoor Units | 67000 | 14.6 | 23.65 | 75000 | 4.05 | 54000 | 2.7 | R-410A | 5.5833
7629575 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TYDN |  |  |  | REYQ72TYDN | Mixed Ducted and Non-Ducted Indoor Units | 67000 | 14.6 | 23.65 | 75000 | 4.05 | 54000 | 2.7 | R-410A | 5.5833
7629577 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TTJU |  |  |  | REYQ96TTJU | Mixed Ducted and Non-Ducted Indoor Units | 90000 | 14.1 | 26.8 | 100000 | 3.98 | 70000 | 2.47 | R-410A | 7.5
7629579 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TYDN |  |  |  | REYQ96TYDN | Mixed Ducted and Non-Ducted Indoor Units | 90000 | 14.1 | 26.8 | 100000 | 3.98 | 70000 | 2.47 | R-410A | 7.5
7629581 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU |  |  |  | REYQ120TTJU | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 13.25 | 24 | 126000 | 3.74 | 86000 | 2.43 | R-410A | 9.25
7629584 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN |  |  |  | REYQ120TYDN | Mixed Ducted and Non-Ducted Indoor Units | 111000 | 13.25 | 24 | 126000 | 3.74 | 86000 | 2.43 | R-410A | 9.25
7629586 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU |  |  |  | REYQ144TTJU | Mixed Ducted and Non-Ducted Indoor Units | 134000 | 12.4 | 23.2 | 150000 | 3.68 | 106000 | 2.45 | R-410A | 11.1667
7629589 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN |  |  |  | REYQ144TYDN | Mixed Ducted and Non-Ducted Indoor Units | 134000 | 12.4 | 23.2 | 150000 | 3.68 | 106000 | 2.45 | R-410A | 11.1667
7849628 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) |  |  |  | GMV-72WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.2 | 22.25 | 77000 | 3.55 | 51000 | 2.42 | R-410A | 5.75
7849629 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) |  |  |  | GMV-96WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.9 | 23 | 103000 | 3.65 | 67000 | 2.44 | R-410A | 7.6667
7849630 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-F(U) |  |  |  | GMV-120WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.2 | 23.15 | 129000 | 3.4 | 87000 | 2.27 | R-410A | 9.5
7850819 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV |  |  |  | AOUA72TLCV | Ducted Indoor Units | 69000 | 12.3 | 20 | 77000 | 3.64 | 56000 | 2.38 | R-410A | 5.75
7850823 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV |  |  |  | AOUA120TLCV | Ducted Indoor Units | 114000 | 11.3 | 20.1 | 129000 | 3.49 | 87000 | 2.41 | R-410A | 9.5
7850839 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV |  |  |  | AOUA72RLCV | Ducted Indoor Units | 69000 | 12.3 | 20 | 77000 | 3.64 | 56000 | 2.38 | R-410A | 5.75
7850843 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV |  |  |  | AOUA120RLCV | Ducted Indoor Units | 114000 | 11.3 | 20.1 | 129000 | 3.49 | 87000 | 2.41 | R-410A | 9.5
7850858 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV |  |  |  | AOUA72TLCV | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.4 | 22.05 | 77000 | 3.85 | 56000 | 2.45 | R-410A | 5.75
7850859 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV |  |  |  | AOUA96TLCV | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 21.9 | 103000 | 3.66 | 73000 | 2.44 | R-410A | 7.6667
7850860 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV |  |  |  | AOUA120TLCV | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.3 | 21.95 | 129000 | 3.55 | 87000 | 2.42 | R-410A | 9.5
7850868 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV |  |  |  | AOUA72RLCV | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.4 | 22.05 | 77000 | 3.85 | 56000 | 2.45 | R-410A | 5.75
7850869 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV |  |  |  | AOUA96RLCV | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 21.9 | 103000 | 3.66 | 73000 | 2.44 | R-410A | 7.6667
7850870 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV |  |  |  | AOUA120RLCV | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.3 | 21.95 | 129000 | 3.55 | 87000 | 2.42 | R-410A | 9.5
7987126 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S |  |  |  | TVAHP072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
7987127 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S |  |  |  | TVAHP072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
7987128 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S |  |  |  | TVAHP096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
7987129 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S |  |  |  | TVAHP096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
7987130 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S |  |  |  | TVAHP120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
7987131 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S |  |  |  | TVAHP120B31S | Ducted Indoor Units | 115000 | 11.3 | 20.1 | 129000 | 3.56 | 89000 | 2.25 | R-410A | 9.5833
7987172 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S |  |  |  | TVAHP072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
7987173 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S |  |  |  | TVAHP072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
7987174 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S |  |  |  | TVAHP096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
7987176 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S |  |  |  | TVAHP120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
7987218 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S |  |  |  | HVAHP072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
7987219 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S |  |  |  | HVAHP072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
7987220 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S |  |  |  | HVAHP096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
7987221 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S |  |  |  | HVAHP096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
7987222 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S |  |  |  | HVAHP120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
7987223 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S |  |  |  | HVAHP120B31S | Ducted Indoor Units | 115000 | 11.3 | 20.1 | 129000 | 3.56 | 89000 | 2.25 | R-410A | 9.5833
7987264 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S |  |  |  | HVAHP072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
7987265 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S |  |  |  | HVAHP072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
7987266 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S |  |  |  | HVAHP096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
7987268 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S |  |  |  | HVAHP120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
7987310 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S |  |  |  | YVAHP072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
7987311 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S |  |  |  | YVAHP072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
7987312 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S |  |  |  | YVAHP096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
7987313 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S |  |  |  | YVAHP096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
7987314 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S |  |  |  | YVAHP120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
7987315 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S |  |  |  | YVAHP120B31S | Ducted Indoor Units | 115000 | 11.3 | 20.1 | 129000 | 3.56 | 89000 | 2.25 | R-410A | 9.5833
7987356 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S |  |  |  | YVAHP072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
7987357 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S |  |  |  | YVAHP072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
7987358 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S |  |  |  | YVAHP096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
7987360 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S |  |  |  | YVAHP120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
7987403 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S |  |  |  | TVAHR072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
7987404 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S |  |  |  | TVAHR072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
7987405 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S |  |  |  | TVAHR096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
7987406 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S |  |  |  | TVAHR096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
7987407 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S |  |  |  | TVAHR120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
7987408 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S |  |  |  | TVAHR120B31S | Ducted Indoor Units | 115000 | 11.1 | 19 | 129000 | 3.58 | 89000 | 2.25 | R-410A | 9.5833
7987409 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S |  |  |  | TVAHR072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
7987410 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S |  |  |  | TVAHR072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
7987411 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S |  |  |  | TVAHR096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
7987413 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S |  |  |  | TVAHR120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
7987415 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S |  |  |  | HVAHR072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
7987416 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S |  |  |  | HVAHR072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
7987417 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S |  |  |  | HVAHR096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
7987418 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S |  |  |  | HVAHR096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
7987419 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S |  |  |  | HVAHR120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
7987420 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S |  |  |  | HVAHR120B31S | Ducted Indoor Units | 115000 | 11.1 | 19 | 129000 | 3.58 | 89000 | 2.25 | R-410A | 9.5833
7987421 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S |  |  |  | HVAHR072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
7987422 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S |  |  |  | HVAHR072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
7987423 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S |  |  |  | HVAHR096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
7987425 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S |  |  |  | HVAHR120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
7987427 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S |  |  |  | YVAHR072B31S | Non-Ducted Indoor Units | 69000 | 15.6 | 25.2 | 76000 | 4.21 | 55000 | 2.56 | R-410A | 5.75
7987428 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S |  |  |  | YVAHR072B31S | Ducted Indoor Units | 69000 | 12.4 | 21.1 | 76000 | 3.83 | 55000 | 2.44 | R-410A | 5.75
7987429 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S |  |  |  | YVAHR096B31S | Non-Ducted Indoor Units | 92000 | 13.2 | 21.8 | 103000 | 3.96 | 76000 | 2.4 | R-410A | 7.6667
7987430 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S |  |  |  | YVAHR096B31S | Ducted Indoor Units | 92000 | 11.4 | 19.8 | 103000 | 3.5 | 76000 | 2.32 | R-410A | 7.6667
7987431 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S |  |  |  | YVAHR120B31S | Non-Ducted Indoor Units | 115000 | 11.1 | 20.8 | 129000 | 3.74 | 89000 | 2.36 | R-410A | 9.5833
7987432 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S |  |  |  | YVAHR120B31S | Ducted Indoor Units | 115000 | 11.1 | 19 | 129000 | 3.58 | 89000 | 2.25 | R-410A | 9.5833
7987433 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S |  |  |  | YVAHR072B41S | Non-Ducted Indoor Units | 69000 | 14.9 | 24.8 | 76000 | 4.1 | 55000 | 2.43 | R-410A | 5.75
7987434 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S |  |  |  | YVAHR072B41S | Ducted Indoor Units | 69000 | 11.8 | 20.3 | 76000 | 3.65 | 55000 | 2.37 | R-410A | 5.75
7987435 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S |  |  |  | YVAHR096B41S | Non-Ducted Indoor Units | 92000 | 13.1 | 21.4 | 103000 | 3.76 | 76000 | 2.28 | R-410A | 7.6667
7987437 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S |  |  |  | YVAHR120B41S | Non-Ducted Indoor Units | 115000 | 11.1 | 19.8 | 129000 | 3.66 | 89000 | 2.25 | R-410A | 9.5833
7990690 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S |  |  |  | TVAHP072B31S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14 | 23.15 | 76000 | 4.02 | 55000 | 2.5 | R-410A | 5.75
7990691 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S |  |  |  | TVAHP096B31S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 20.8 | 103000 | 3.73 | 76000 | 2.36 | R-410A | 7.6667
7990692 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S |  |  |  | TVAHP120B31S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 20.45 | 129000 | 3.65 | 89000 | 2.3 | R-410A | 9.5833
7990704 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S |  |  |  | TVAHR072B31S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14 | 23.15 | 76000 | 4.02 | 55000 | 2.5 | R-410A | 5.75
7990705 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S |  |  |  | TVAHR096B31S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 20.8 | 103000 | 3.73 | 76000 | 2.36 | R-410A | 7.6667
7990706 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S |  |  |  | TVAHR120B31S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.1 | 19.9 | 129000 | 3.66 | 89000 | 2.3 | R-410A | 9.5833
7990717 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S |  |  |  | TVAHP072B41S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.35 | 22.55 | 76000 | 3.87 | 55000 | 2.4 | R-410A | 5.75
7990731 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S |  |  |  | TVAHR072B41S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.35 | 22.55 | 76000 | 3.87 | 55000 | 2.4 | R-410A | 5.75
7990744 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S |  |  |  | HVAHP072B31S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14 | 23.15 | 76000 | 4.02 | 55000 | 2.5 | R-410A | 5.75
7990745 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S |  |  |  | HVAHP096B31S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 20.8 | 103000 | 3.73 | 76000 | 2.36 | R-410A | 7.6667
7990746 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S |  |  |  | HVAHP120B31S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 20.45 | 129000 | 3.65 | 89000 | 2.3 | R-410A | 9.5833
7990757 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S |  |  |  | HVAHR072B31S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14 | 23.15 | 76000 | 4.02 | 55000 | 2.5 | R-410A | 5.75
7990758 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S |  |  |  | HVAHR096B31S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 20.8 | 103000 | 3.73 | 76000 | 2.36 | R-410A | 7.6667
7990759 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S |  |  |  | HVAHR120B31S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.1 | 19.9 | 129000 | 3.66 | 89000 | 2.3 | R-410A | 9.5833
7990771 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S |  |  |  | HVAHP072B41S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.35 | 22.55 | 76000 | 3.87 | 55000 | 2.4 | R-410A | 5.75
7990784 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S |  |  |  | HVAHR072B41S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.35 | 22.55 | 76000 | 3.87 | 55000 | 2.4 | R-410A | 5.75
7990798 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S |  |  |  | YVAHP072B31S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14 | 23.15 | 76000 | 4.02 | 55000 | 2.5 | R-410A | 5.75
7990799 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S |  |  |  | YVAHP096B31S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 20.8 | 103000 | 3.73 | 76000 | 2.36 | R-410A | 7.6667
7990800 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S |  |  |  | YVAHP120B31S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.2 | 20.45 | 129000 | 3.65 | 89000 | 2.3 | R-410A | 9.5833
7990811 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S |  |  |  | YVAHR072B31S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14 | 23.15 | 76000 | 4.02 | 55000 | 2.5 | R-410A | 5.75
7990812 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S |  |  |  | YVAHR096B31S | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.3 | 20.8 | 103000 | 3.73 | 76000 | 2.36 | R-410A | 7.6667
7990813 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S |  |  |  | YVAHR120B31S | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 11.1 | 19.9 | 129000 | 3.66 | 89000 | 2.3 | R-410A | 9.5833
7990824 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S |  |  |  | YVAHP072B41S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.35 | 22.55 | 76000 | 3.87 | 55000 | 2.4 | R-410A | 5.75
7990837 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S |  |  |  | YVAHR072B41S | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.35 | 22.55 | 76000 | 3.87 | 55000 | 2.4 | R-410A | 5.75
8175478 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YLMU-A |  |  |  | PUHY-P72YLMU-A | Ducted Indoor Units | 69000 | 13.7 | 23.1 | 76000 | 3.84 | 56000 | 2.46 | R-410A | 5.75
8175479 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YLMU-A |  |  |  | PUHY-P72YLMU-A | Non-Ducted Indoor Units | 69000 | 14.8 | 26.6 | 76000 | 4.01 | 56000 | 2.25 | R-410A | 5.75
8175480 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YLMU-A |  |  |  | PUHY-P96YLMU-A | Ducted Indoor Units | 92000 | 13.1 | 23.1 | 103000 | 3.79 | 76000 | 2.57 | R-410A | 7.6667
8175481 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YLMU-A |  |  |  | PUHY-P96YLMU-A | Non-Ducted Indoor Units | 92000 | 14 | 26.7 | 103000 | 3.85 | 76000 | 2.42 | R-410A | 7.6667
8175482 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A |  |  |  | PUHY-P120YLMU-A | Ducted Indoor Units | 114000 | 13.2 | 21.9 | 129000 | 3.71 | 92000 | 2.38 | R-410A | 9.5
8175483 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A |  |  |  | PUHY-P120YLMU-A | Non-Ducted Indoor Units | 114000 | 14.4 | 24.9 | 129000 | 4.03 | 92000 | 2.3 | R-410A | 9.5
8175508 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TLMU-A |  |  |  | PUHY-P72TLMU-A | Ducted Indoor Units | 69000 | 13.7 | 23.1 | 76000 | 3.84 | 56000 | 2.46 | R-410A | 5.75
8175509 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TLMU-A |  |  |  | PUHY-P72TLMU-A | Non-Ducted Indoor Units | 69000 | 14.8 | 26.6 | 76000 | 4.01 | 56000 | 2.25 | R-410A | 5.75
8175510 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TLMU-A |  |  |  | PUHY-P96TLMU-A | Ducted Indoor Units | 92000 | 13.1 | 23.1 | 103000 | 3.79 | 76000 | 2.57 | R-410A | 7.6667
8175511 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TLMU-A |  |  |  | PUHY-P96TLMU-A | Non-Ducted Indoor Units | 92000 | 14 | 26.7 | 103000 | 3.85 | 76000 | 2.42 | R-410A | 7.6667
8175512 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A |  |  |  | PUHY-P120TLMU-A | Ducted Indoor Units | 114000 | 13.2 | 21.9 | 129000 | 3.71 | 92000 | 2.38 | R-410A | 9.5
8175513 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A |  |  |  | PUHY-P120TLMU-A | Non-Ducted Indoor Units | 114000 | 14.4 | 24.9 | 129000 | 4.03 | 92000 | 2.3 | R-410A | 9.5
8175891 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YLMU-A |  |  |  | PURY-P72YLMU-A | Ducted Indoor Units | 69000 | 13.5 | 23.1 | 76000 | 3.65 | 56000 | 2.26 | R-410A | 5.75
8175892 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YLMU-A |  |  |  | PURY-P72YLMU-A | Non-Ducted Indoor Units | 69000 | 13.3 | 25.1 | 76000 | 3.8 | 56000 | 2.26 | R-410A | 5.75
8175893 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A |  |  |  | PURY-P96YLMU-A | Ducted Indoor Units | 92000 | 12 | 24.1 | 103000 | 3.53 | 71000 | 2.28 | R-410A | 7.6667
8175894 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A |  |  |  | PURY-P96YLMU-A | Non-Ducted Indoor Units | 92000 | 12.7 | 24.5 | 103000 | 3.55 | 71000 | 2.26 | R-410A | 7.6667
8175895 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A |  |  |  | PURY-P120YLMU-A | Ducted Indoor Units | 114000 | 12.8 | 19.9 | 129000 | 3.52 | 87000 | 2.26 | R-410A | 9.5
8175896 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A |  |  |  | PURY-P120YLMU-A | Non-Ducted Indoor Units | 114000 | 14.1 | 23.6 | 129000 | 3.8 | 87000 | 2.26 | R-410A | 9.5
8175919 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TLMU-A |  |  |  | PURY-P72TLMU-A | Ducted Indoor Units | 69000 | 13.5 | 23.1 | 76000 | 3.65 | 56000 | 2.26 | R-410A | 5.75
8175920 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TLMU-A |  |  |  | PURY-P72TLMU-A | Non-Ducted Indoor Units | 69000 | 13.3 | 25.1 | 76000 | 3.8 | 56000 | 2.26 | R-410A | 5.75
8175921 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A |  |  |  | PURY-P96TLMU-A | Ducted Indoor Units | 92000 | 12 | 24.1 | 103000 | 3.53 | 71000 | 2.28 | R-410A | 7.6667
8175922 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A |  |  |  | PURY-P96TLMU-A | Non-Ducted Indoor Units | 92000 | 12.7 | 24.5 | 103000 | 3.55 | 71000 | 2.26 | R-410A | 7.6667
8175923 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A |  |  |  | PURY-P120TLMU-A | Ducted Indoor Units | 114000 | 12.8 | 19.9 | 129000 | 3.52 | 87000 | 2.26 | R-410A | 9.5
8175924 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A |  |  |  | PURY-P120TLMU-A | Non-Ducted Indoor Units | 114000 | 14.1 | 23.6 | 129000 | 3.8 | 87000 | 2.26 | R-410A | 9.5
4677057 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ |  |  |  | RXYQ72PBTJ | Non-Ducted Indoor Units | 69000 | 14.1 | 25.8 | 77000 | 4 | 51000 | 2.65 | R-410A | 5.75
4677058 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ |  |  |  | RXYQ72PBTJ | Ducted Indoor Units | 69000 | 12.8 | 21.5 | 77000 | 3.71 | 51000 | 2.4 | R-410A | 5.75
4677059 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ |  |  |  | RXYQ72PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.65 | 77000 | 3.85 | 51000 | 2.52 | R-410A | 5.75
4677060 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBTJ |  |  |  | RXYQ96PBTJ | Non-Ducted Indoor Units | 92000 | 13.5 | 23 | 103000 | 4.2 | 67000 | 2.85 | R-410A | 7.6667
4677062 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBTJ |  |  |  | RXYQ96PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13 | 20.9 | 103000 | 3.92 | 67000 | 2.67 | R-410A | 7.6667
4677063 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ120PBTJ |  |  |  | RXYQ120PBTJ | Non-Ducted Indoor Units | 114000 | 12.5 | 20.4 | 129000 | 3.8 | 84000 | 2.65 | R-410A | 9.5
4677090 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD |  |  |  | RXYQ72PBYD | Non-Ducted Indoor Units | 69000 | 14.1 | 25.8 | 77000 | 4 | 51000 | 2.65 | R-410A | 5.75
4677091 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD |  |  |  | RXYQ72PBYD | Ducted Indoor Units | 69000 | 12.8 | 21.5 | 77000 | 3.71 | 51000 | 2.4 | R-410A | 5.75
4677092 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD |  |  |  | RXYQ72PBYD | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.45 | 23.65 | 77000 | 3.85 | 51000 | 2.52 | R-410A | 5.75
4677093 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBYD |  |  |  | RXYQ96PBYD | Non-Ducted Indoor Units | 92000 | 13.5 | 23 | 103000 | 4.2 | 67000 | 2.85 | R-410A | 7.6667
4677095 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBYD |  |  |  | RXYQ96PBYD | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13 | 20.9 | 103000 | 3.92 | 67000 | 2.67 | R-410A | 7.6667
4677096 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ120PBYD |  |  |  | RXYQ120PBYD | Non-Ducted Indoor Units | 114000 | 12.5 | 20.4 | 129000 | 3.8 | 84000 | 2.65 | R-410A | 9.5
4677123 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ120PBTJ |  |  |  | REYQ120PBTJ | Non-Ducted Indoor Units | 114000 | 12.1 | 21.3 | 129000 | 3.6 | 87000 | 2.6 | R-410A | 9.5
4679526 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 |  |  |  | ARUB072BT3 | Ducted Indoor Units | 69000 | 12.4 | 21.8 | 77000 | 3.62 | 51000 | 2.47 | R-410A | 5.75
4679527 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 |  |  |  | ARUB072BT3 | Non-Ducted Indoor Units | 69000 | 13.6 | 24.5 | 77000 | 3.87 | 51000 | 2.59 | R-410A | 5.75
4679528 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 |  |  |  | ARUB072DT3 | Ducted Indoor Units | 69000 | 12.4 | 21.8 | 77000 | 3.62 | 51000 | 2.47 | R-410A | 5.75
4679529 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 |  |  |  | ARUB072DT3 | Non-Ducted Indoor Units | 69000 | 13.6 | 24.5 | 77000 | 3.87 | 51000 | 2.59 | R-410A | 5.75
4679530 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BT3 |  |  |  | ARUB096BT3 | Ducted Indoor Units | 92000 | 12.6 | 20.2 | 103000 | 3.57 | 67000 | 2.63 | R-410A | 7.6667
4679531 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BT3 |  |  |  | ARUB096BT3 | Non-Ducted Indoor Units | 92000 | 14.3 | 23.2 | 103000 | 3.88 | 67000 | 2.75 | R-410A | 7.6667
4679532 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DT3 |  |  |  | ARUB096DT3 | Ducted Indoor Units | 92000 | 12.6 | 20.2 | 103000 | 3.57 | 67000 | 2.63 | R-410A | 7.6667
4679533 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DT3 |  |  |  | ARUB096DT3 | Non-Ducted Indoor Units | 92000 | 14.3 | 23.2 | 103000 | 3.88 | 67000 | 2.75 | R-410A | 7.6667
4679534 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BT3 |  |  |  | ARUB121BT3 | Ducted Indoor Units | 114000 | 12 | 19.6 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
4679535 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BT3 |  |  |  | ARUB121BT3 | Non-Ducted Indoor Units | 114000 | 12.9 | 20.6 | 129000 | 3.73 | 84000 | 2.67 | R-410A | 9.5
4679536 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DT3 |  |  |  | ARUB121DT3 | Ducted Indoor Units | 114000 | 12 | 19.6 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
4679537 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DT3 |  |  |  | ARUB121DT3 | Non-Ducted Indoor Units | 114000 | 12.9 | 20.6 | 129000 | 3.73 | 84000 | 2.67 | R-410A | 9.5
4679570 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 |  |  |  | ARUN072BT3 | Ducted Indoor Units | 69000 | 12.4 | 21.8 | 77000 | 3.62 | 51000 | 2.47 | R-410A | 5.75
4679571 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 |  |  |  | ARUN072BT3 | Non-Ducted Indoor Units | 69000 | 13.6 | 24.5 | 77000 | 3.87 | 51000 | 2.59 | R-410A | 5.75
4679572 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 |  |  |  | ARUN072DT3 | Ducted Indoor Units | 69000 | 12.4 | 21.8 | 77000 | 3.62 | 51000 | 2.47 | R-410A | 5.75
4679573 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 |  |  |  | ARUN072DT3 | Non-Ducted Indoor Units | 69000 | 13.6 | 24.5 | 77000 | 3.87 | 51000 | 2.59 | R-410A | 5.75
4679574 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BT3 |  |  |  | ARUN096BT3 | Ducted Indoor Units | 92000 | 12.6 | 20.2 | 103000 | 3.57 | 67000 | 2.63 | R-410A | 7.6667
4679575 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BT3 |  |  |  | ARUN096BT3 | Non-Ducted Indoor Units | 92000 | 14.3 | 23.2 | 103000 | 3.88 | 67000 | 2.75 | R-410A | 7.6667
4679576 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DT3 |  |  |  | ARUN096DT3 | Ducted Indoor Units | 92000 | 12.6 | 20.2 | 103000 | 3.57 | 67000 | 2.63 | R-410A | 7.6667
4679577 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DT3 |  |  |  | ARUN096DT3 | Non-Ducted Indoor Units | 92000 | 14.3 | 23.2 | 103000 | 3.88 | 67000 | 2.75 | R-410A | 7.6667
4679578 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BT3 |  |  |  | ARUN121BT3 | Ducted Indoor Units | 114000 | 12 | 19.6 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
4679579 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BT3 |  |  |  | ARUN121BT3 | Non-Ducted Indoor Units | 114000 | 12.9 | 20.6 | 129000 | 3.73 | 84000 | 2.67 | R-410A | 9.5
4679580 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DT3 |  |  |  | ARUN121DT3 | Ducted Indoor Units | 114000 | 12 | 19.6 | 129000 | 3.48 | 84000 | 2.54 | R-410A | 9.5
4679581 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DT3 |  |  |  | ARUN121DT3 | Non-Ducted Indoor Units | 114000 | 12.9 | 20.6 | 129000 | 3.73 | 84000 | 2.67 | R-410A | 9.5
5039448 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBTJ |  |  |  | REYQ72PBTJ | Non-Ducted Indoor Units | 69000 | 15.4 | 25.1 | 77000 | 4.2 | 52000 | 2.95 | R-410A | 5.75
5039449 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBTJ |  |  |  | REYQ72PBTJ | Ducted Indoor Units | 69000 | 13.8 | 21.3 | 77000 | 3.8 | 52000 | 2.6 | R-410A | 5.75
5039450 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBTJ |  |  |  | REYQ72PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.6 | 23.2 | 77000 | 4 | 52000 | 2.77 | R-410A | 5.75
5039451 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ120PBYD |  |  |  | REYQ120PBYD | Non-Ducted Indoor Units | 114000 | 12.1 | 21.3 | 129000 | 3.6 | 87000 | 2.6 | R-410A | 9.5
5198211 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV |  |  |  | AOUA72RLBV | Non-Ducted Indoor Units | 69000 | 12.5 | 21.7 | 77000 | 3.76 | 56000 | 2.3 | R-410A | 5.75
5198213 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV |  |  |  | AOUA72RLBV | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.4 | 19.95 | 77000 | 3.7 | 56000 | 2.3 | R-410A | 5.75
5198214 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV |  |  |  | AOUA96RLBV | Non-Ducted Indoor Units | 92000 | 11.7 | 20.8 | 103000 | 3.55 | 73000 | 2.5 | R-410A | 7.6667
5198216 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV |  |  |  | AOUA96RLBV | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.65 | 19.3 | 103000 | 3.51 | 73000 | 2.45 | R-410A | 7.6667
5358519 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-A |  |  |  | PUHY-P72YKMU-A | Ducted Indoor Units | 69000 | 13 | 19.8 | 76000 | 3.83 | 56000 | 2.59 | R-410A | 5.75
5358520 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-A |  |  |  | PUHY-P72YKMU-A | Non-Ducted Indoor Units | 69000 | 14.2 | 21.3 | 76000 | 4.19 | 56000 | 2.39 | R-410A | 5.75
5358521 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-A |  |  |  | PUHY-P72YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 20.55 | 76000 | 4.01 | 56000 | 2.49 | R-410A | 5.75
5358522 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-A |  |  |  | PUHY-P96YKMU-A | Ducted Indoor Units | 92000 | 12.6 | 19.7 | 103000 | 3.95 | 76000 | 2.71 | R-410A | 7.6667
5358523 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-A |  |  |  | PUHY-P96YKMU-A | Non-Ducted Indoor Units | 92000 | 13.7 | 20.7 | 103000 | 4.22 | 76000 | 2.68 | R-410A | 7.6667
5358524 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-A |  |  |  | PUHY-P96YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.15 | 20.2 | 103000 | 4.08 | 76000 | 2.69 | R-410A | 7.6667
5358525 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A |  |  |  | PUHY-P120YKMU-A | Ducted Indoor Units | 114000 | 12.5 | 19.1 | 129000 | 3.66 | 92000 | 2.51 | R-410A | 9.5
5358526 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A |  |  |  | PUHY-P120YKMU-A | Non-Ducted Indoor Units | 114000 | 12.7 | 19.1 | 129000 | 3.83 | 92000 | 2.38 | R-410A | 9.5
5358527 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A |  |  |  | PUHY-P120YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.6 | 19.1 | 129000 | 3.74 | 92000 | 2.44 | R-410A | 9.5
5358561 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TKMU-A |  |  |  | PUHY-P72TKMU-A | Ducted Indoor Units | 69000 | 13 | 19.8 | 76000 | 3.83 | 56000 | 2.59 | R-410A | 5.75
5358562 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TKMU-A |  |  |  | PUHY-P72TKMU-A | Non-Ducted Indoor Units | 69000 | 14.2 | 21.3 | 76000 | 4.19 | 56000 | 2.39 | R-410A | 5.75
5358563 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TKMU-A |  |  |  | PUHY-P72TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.6 | 20.55 | 76000 | 4.01 | 56000 | 2.49 | R-410A | 5.75
5358564 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-A |  |  |  | PUHY-P96TKMU-A | Ducted Indoor Units | 92000 | 12.6 | 19.7 | 103000 | 3.95 | 76000 | 2.71 | R-410A | 7.6667
5358565 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-A |  |  |  | PUHY-P96TKMU-A | Non-Ducted Indoor Units | 92000 | 13.7 | 20.7 | 103000 | 4.22 | 76000 | 2.68 | R-410A | 7.6667
5358566 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-A |  |  |  | PUHY-P96TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.15 | 20.2 | 103000 | 4.08 | 76000 | 2.69 | R-410A | 7.6667
5358567 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A |  |  |  | PUHY-P120TKMU-A | Ducted Indoor Units | 114000 | 12.5 | 19.1 | 129000 | 3.66 | 92000 | 2.51 | R-410A | 9.5
5358568 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A |  |  |  | PUHY-P120TKMU-A | Non-Ducted Indoor Units | 114000 | 12.7 | 19.1 | 129000 | 3.83 | 92000 | 2.38 | R-410A | 9.5
5358569 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A |  |  |  | PUHY-P120TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.6 | 19.1 | 129000 | 3.74 | 92000 | 2.44 | R-410A | 9.5
5358600 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-A |  |  |  | PURY-P72YKMU-A | Ducted Indoor Units | 69000 | 13.9 | 21.1 | 76000 | 3.81 | 56000 | 2.62 | R-410A | 5.75
5358601 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-A |  |  |  | PURY-P72YKMU-A | Non-Ducted Indoor Units | 69000 | 15.5 | 20.9 | 76000 | 3.66 | 56000 | 2.45 | R-410A | 5.75
5358602 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-A |  |  |  | PURY-P72YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.7 | 21.6 | 76000 | 3.73 | 56000 | 2.53 | R-410A | 5.75
5358603 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A |  |  |  | PURY-P96YKMU-A | Ducted Indoor Units | 92000 | 12.2 | 19.7 | 103000 | 3.64 | 76000 | 2.47 | R-410A | 7.6667
5358604 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A |  |  |  | PURY-P96YKMU-A | Non-Ducted Indoor Units | 92000 | 13.6 | 20.1 | 103000 | 3.66 | 76000 | 2.46 | R-410A | 7.6667
5358605 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A |  |  |  | PURY-P96YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.9 | 20.3 | 103000 | 3.65 | 76000 | 2.46 | R-410A | 7.6667
5358607 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-A |  |  |  | PURY-P120YKMU-A | Non-Ducted Indoor Units | 114000 | 12.2 | 20.3 | 129000 | 3.57 | 92000 | 2.4 | R-410A | 9.5
5358608 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-A |  |  |  | PURY-P120YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.95 | 19.7 | 129000 | 3.51 | 92000 | 2.35 | R-410A | 9.5
5358633 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A |  |  |  | PURY-P96TKMU-A | Ducted Indoor Units | 92000 | 12.2 | 19.7 | 103000 | 3.64 | 76000 | 2.47 | R-410A | 7.6667
5358634 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A |  |  |  | PURY-P96TKMU-A | Non-Ducted Indoor Units | 92000 | 13.6 | 20.1 | 103000 | 3.66 | 76000 | 2.46 | R-410A | 7.6667
5358635 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A |  |  |  | PURY-P96TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.9 | 20.3 | 103000 | 3.65 | 76000 | 2.46 | R-410A | 7.6667
5358637 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-A |  |  |  | PURY-P120TKMU-A | Non-Ducted Indoor Units | 114000 | 12.2 | 20.3 | 129000 | 3.57 | 92000 | 2.4 | R-410A | 9.5
5358638 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-A |  |  |  | PURY-P120TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.95 | 19.7 | 129000 | 3.51 | 92000 | 2.35 | R-410A | 9.5
5359039 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TKMU-A |  |  |  | PURY-P72TKMU-A | Ducted Indoor Units | 69000 | 13.9 | 21.1 | 76000 | 3.81 | 56000 | 2.62 | R-410A | 5.75
5359040 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TKMU-A |  |  |  | PURY-P72TKMU-A | Non-Ducted Indoor Units | 69000 | 15.5 | 20.9 | 76000 | 3.66 | 56000 | 2.45 | R-410A | 5.75
5359041 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TKMU-A |  |  |  | PURY-P72TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.7 | 21.6 | 76000 | 3.73 | 56000 | 2.53 | R-410A | 5.75
5360172 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBYD |  |  |  | REYQ72PBYD | Non-Ducted Indoor Units | 69000 | 15.4 | 25.1 | 77000 | 4.2 | 52000 | 2.95 | R-410A | 5.75
5360173 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBYD |  |  |  | REYQ72PBYD | Ducted Indoor Units | 69000 | 13.8 | 21.3 | 77000 | 3.8 | 52000 | 2.6 | R-410A | 5.75
5360174 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ72PBYD |  |  |  | REYQ72PBYD | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 14.6 | 23.2 | 77000 | 4 | 52000 | 2.77 | R-410A | 5.75
5360175 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBTJ |  |  |  | REYQ96PBTJ | Non-Ducted Indoor Units | 92000 | 13.2 | 22.9 | 103000 | 3.7 | 69000 | 2.7 | R-410A | 7.6667
5360176 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBTJ |  |  |  | REYQ96PBTJ | Ducted Indoor Units | 92000 | 12.1 | 19.7 | 103000 | 3.6 | 69000 | 2.65 | R-410A | 7.6667
5360177 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBTJ |  |  |  | REYQ96PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.65 | 21.3 | 103000 | 3.65 | 69000 | 2.67 | R-410A | 7.6667
5360178 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBYD |  |  |  | REYQ96PBYD | Non-Ducted Indoor Units | 92000 | 13.2 | 22.9 | 103000 | 3.7 | 69000 | 2.7 | R-410A | 7.6667
5360179 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBYD |  |  |  | REYQ96PBYD | Ducted Indoor Units | 92000 | 12.1 | 19.7 | 103000 | 3.6 | 69000 | 2.65 | R-410A | 7.6667
5360180 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ96PBYD |  |  |  | REYQ96PBYD | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.65 | 21.3 | 103000 | 3.65 | 69000 | 2.67 | R-410A | 7.6667
5733023 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096FXVAFH |  |  |  | AM096FXVAFH | Non-Ducted Indoor Units | 92000 | 11.5 | 27.9 | 103000 | 3.47 | 67000 | 2.25 | R-410A | 7.6667
5733027 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAFR |  |  |  | AM096FXVAFR | Non-Ducted Indoor Units | 92000 | 11.5 | 27.9 | 103000 | 3.47 | 67000 | 2.25 | R-410A | 7.6667
5924239 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0724HT9UL |  |  |  | MMY-MAP0724HT9UL | Mixed Ducted and Non-Ducted Indoor Units | 70000 | 11.25 | 19.3 | 81000 | 3.48 | 42000 | 2.44 | R-410A | 5.8333
5924240 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0724HT6UL |  |  |  | MMY-MAP0724HT6UL | Mixed Ducted and Non-Ducted Indoor Units | 70000 | 11.25 | 18.9 | 81000 | 3.48 | 42000 | 2.44 | R-410A | 5.8333
6334547 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0724FT9UL |  |  |  | MMY-MAP0724FT9UL | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.7 | 19.05 | 77000 | 3.41 | 55000 | 2.33 | R-410A | 5.75
6334567 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0724FT9UL |  |  |  | MMY-MAP0724FT9UL | Non-Ducted Indoor Units | 69000 | 11.7 | 21.5 | 77000 | 3.46 | 55000 | 2.34 | R-410A | 5.75
6334568 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0964FT9UL |  |  |  | MMY-MAP0964FT9UL | Non-Ducted Indoor Units | 92000 | 11.7 | 20 | 103000 | 3.4 | 60000 | 2.27 | R-410A | 7.6667
6334574 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0724FT6UL |  |  |  | MMY-MAP0724FT6UL | Non-Ducted Indoor Units | 69000 | 11.7 | 20.9 | 77000 | 3.46 | 55000 | 2.34 | R-410A | 5.75
6334575 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0964FT6UL |  |  |  | MMY-MAP0964FT6UL | Non-Ducted Indoor Units | 92000 | 11.7 | 19.6 | 103000 | 3.4 | 60000 | 2.27 | R-410A | 7.6667
6687540 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV |  |  |  | AOUA72TLBV | Ducted Indoor Units | 69000 | 12.3 | 20 | 77000 | 3.64 | 56000 | 2.38 | R-410A | 5.75
6687544 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV |  |  |  | AOUA120TLBV | Ducted Indoor Units | 114000 | 11.3 | 20.1 | 129000 | 3.49 | 87000 | 2.41 | R-410A | 9.5
6691437 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV |  |  |  | AOUA72TLBV | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 12.4 | 22.05 | 77000 | 3.85 | 56000 | 2.45 | R-410A | 5.75
6691438 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV |  |  |  | AOUA96TLBV | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 11.5 | 21.9 | 103000 | 3.66 | 73000 | 2.44 | R-410A | 7.6667
6691439 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV |  |  |  | AOUA120TLBV | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.3 | 21.95 | 129000 | 3.55 | 87000 | 2.42 | R-410A | 9.5
8656991 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72ZKMU-A |  |  |  | PURY-P72ZKMU-A | Ducted Indoor Units | 69000 | 12.5 | 21.6 | 76000 | 3.51 | 56000 | 2.26 | R-410A | 5.75
8657015 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A |  |  |  | PUHY-P120ZKMU-A | Ducted Indoor Units | 114000 | 12.5 | 21.4 | 129000 | 3.62 | 92000 | 2.51 | R-410A | 9.5
8657013 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96ZKMU-A |  |  |  | PUHY-P96ZKMU-A | Ducted Indoor Units | 92000 | 12.3 | 22.4 | 103000 | 3.73 | 76000 | 2.71 | R-410A | 7.6667
8657011 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72ZKMU-A |  |  |  | PUHY-P72ZKMU-A | Ducted Indoor Units | 69000 | 13 | 22.5 | 76000 | 3.74 | 56000 | 2.59 | R-410A | 5.75
8656995 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120ZKMU-A |  |  |  | PURY-P120ZKMU-A | Ducted Indoor Units | 114000 | 12.2 | 19.5 | 129000 | 3.4 | 87000 | 2.26 | R-410A | 9.5
8656993 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96ZKMU-A |  |  |  | PURY-P96ZKMU-A | Ducted Indoor Units | 92000 | 11.8 | 20.5 | 103000 | 3.5 | 71000 | 2.26 | R-410A | 7.6667
205281460 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
205281457 | 1/1/2027 | LG | HMSR-A-CB | ARUM072CTE5 |  |  |  | ARUM072CTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
205287345 | 1/1/2027 | LG | HMSR-A-CB | ARUM072CTE5 |  |  |  | ARUM072CTE5 | Non-Ducted Indoor Units | 69000 | 13.4 | 28.4 | 77000 | 3.83 | 51000 | 2.66 | R-410A | 5.75
202515498 | 1/1/2027 | LG | HMSV-A-CB | ARUN072CTE4 |  |  |  | ARUN072CTE4 | Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 3.81 | 51000 | 2.52 | R-410A | 5.75
202515499 | 1/1/2027 | LG | HMSV-A-CB | ARUN072CTE4 |  |  |  | ARUN072CTE4 | Non-Ducted Indoor Units | 69000 | 13.4 | 27.5 | 77000 | 3.8 | 51000 | 2.6 | R-410A | 5.75
202566095 | 1/1/2027 | LG | HMSR-A-CB | ARUM072CTE5 |  |  |  | ARUM072CTE5 | Ducted Indoor Units | 69000 | 13 | 23.6 | 77000 | 3.48 | 51000 | 2.49 | R-410A | 5.75
202566098 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.33 | 67000 | 2.85 | R-410A | 7.6667
202566099 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Ducted Indoor Units | 92000 | 13.5 | 25.1 | 103000 | 3.66 | 67000 | 2.73 | R-410A | 7.6667
202566100 | 1/1/2027 | LG | HMSR-A-CB | ARUM121CTE5 |  |  |  | ARUM121CTE5 | Non-Ducted Indoor Units | 114000 | 13.1 | 29.6 | 129000 | 3.97 | 84000 | 2.74 | R-410A | 9.5
202566101 | 1/1/2027 | LG | HMSR-A-CB | ARUM121CTE5 |  |  |  | ARUM121CTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
202534320 | 1/1/2027 | LG | HMSR-A-CB | ARUB096CTE4 |  |  |  | ARUB096CTE4 | Non-Ducted Indoor Units | 92000 | 13.5 | 32 | 103000 | 3.98 | 67000 | 2.66 | R-410A | 7.6667
202534321 | 1/1/2027 | LG | HMSR-A-CB | ARUB121CTE4 |  |  |  | ARUB121CTE4 | Non-Ducted Indoor Units | 114000 | 13.2 | 24.3 | 129000 | 3.68 | 84000 | 2.57 | R-410A | 9.5
202534332 | 1/1/2027 | LG | HMSR-A-CB | ARUB096CTE4 |  |  |  | ARUB096CTE4 | Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.71 | 67000 | 2.71 | R-410A | 7.6667
202534333 | 1/1/2027 | LG | HMSR-A-CB | ARUB121CTE4 |  |  |  | ARUB121CTE4 | Ducted Indoor Units | 114000 | 12.5 | 21.8 | 129000 | 3.5 | 84000 | 2.57 | R-410A | 9.5
202534344 | 1/1/2027 | LG | HMSV-A-CB | ARUN096CTE4 |  |  |  | ARUN096CTE4 | Non-Ducted Indoor Units | 92000 | 13.5 | 32 | 103000 | 3.98 | 67000 | 2.66 | R-410A | 7.6667
202534345 | 1/1/2027 | LG | HMSV-A-CB | ARUN121CTE4 |  |  |  | ARUN121CTE4 | Non-Ducted Indoor Units | 114000 | 13.2 | 24.3 | 129000 | 3.68 | 84000 | 2.57 | R-410A | 9.5
202534356 | 1/1/2027 | LG | HMSV-A-CB | ARUN096CTE4 |  |  |  | ARUN096CTE4 | Ducted Indoor Units | 92000 | 12.7 | 23.5 | 103000 | 3.71 | 67000 | 2.71 | R-410A | 7.6667
202534357 | 1/1/2027 | LG | HMSV-A-CB | ARUN121CTE4 |  |  |  | ARUN121CTE4 | Ducted Indoor Units | 114000 | 12.5 | 21.8 | 129000 | 3.5 | 84000 | 2.57 | R-410A | 9.5
202515495 | 1/1/2027 | LG | HMSR-A-CB | ARUB072CTE4 |  |  |  | ARUB072CTE4 | Ducted Indoor Units | 69000 | 13 | 23 | 77000 | 3.81 | 51000 | 2.52 | R-410A | 5.75
202515496 | 1/1/2027 | LG | HMSR-A-CB | ARUB072CTE4 |  |  |  | ARUB072CTE4 | Non-Ducted Indoor Units | 69000 | 13.4 | 27.5 | 77000 | 3.8 | 51000 | 2.6 | R-410A | 5.75
10619421 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120ZKMU-A |  |  |  | PURY-P120ZKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.7 | 20.9 | 129000 | 3.45 | 87000 | 2.26 | R-410A | 9.5
10619422 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96ZKMU-A |  |  |  | PURY-P96ZKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12.1 | 21.6 | 103000 | 3.48 | 71000 | 2.26 | R-410A | 7.6667
206453576 | 1/1/2027 | LG | HMSR-A-CB | ARUM072CTE5 |  |  |  | ARUM072CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.2 | 26 | 77000 | 3.65 | 51000 | 2.57 | R-410A | 5.75
206453544 | 1/1/2027 | LG | HMSR-A-CB | ARUM121CTE5 |  |  |  | ARUM121CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 12.8 | 27.1 | 129000 | 3.71 | 84000 | 2.63 | R-410A | 9.5
206453541 | 1/1/2027 | LG | HMSR-A-CB | ARUM096CTE5 |  |  |  | ARUM096CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.95 | 29.05 | 103000 | 3.99 | 67000 | 2.79 | R-410A | 7.6667
205281463 | 1/1/2027 | LG | HMSR-A-CB | ARUM121CTE5 |  |  |  | ARUM121CTE5 | Ducted Indoor Units | 114000 | 12.5 | 24.6 | 129000 | 3.46 | 84000 | 2.53 | R-410A | 9.5
208102083 | 1/1/2027 | LENNOX | HMSR-A-CB | VER072C432G | VER072C432G |  |  | VER144C432G | Non-Ducted Indoor Units | 134000 | 11.6 | 23 | 150000 | 3.65 | 106000 | 2.35 | R-410A | 11.1667
208102085 | 1/1/2027 | LENNOX | HMSR-A-CB | VER072C432Y | VER072C432Y |  |  | VER144C432Y | Non-Ducted Indoor Units | 134000 | 11.6 | 23 | 150000 | 3.65 | 106000 | 2.35 | R-410A | 11.1667
203400954 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q120WM/B-U(U) |  |  |  | GMV-Q120WM/B-U(U) | Non-Ducted Indoor Units | 114000 | 11.5 | 22 | 126000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
208102016 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432Y |  |  |  | VEP120C432Y | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
208102010 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
208102004 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
208102008 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
208102001 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
208102002 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
208102073 | 1/1/2027 | LENNOX | HMSR-A-CB | VER072C432Y |  |  |  | VER072C432Y | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
208102075 | 1/1/2027 | LENNOX | HMSR-A-CB | VER096C432G |  |  |  | VER096C432G | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
208102078 | 1/1/2027 | LENNOX | HMSR-A-CB | VER096C432Y |  |  |  | VER096C432Y | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
200084008 | 1/1/2027 | MAMMOTH | HMSR-A-CB | V5BV-R72WMBK |  |  |  | V5BV-R72WMBK | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
200084009 | 1/1/2027 | REZNOR | HMSR-A-CB | V5BV-R72WMBK |  |  |  | V5BV-R72WMBK | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
200084010 | 1/1/2027 | NORTEK | HMSR-A-CB | V5BV-R72WMBK |  |  |  | V5BV-R72WMBK | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
10509439 | 1/1/2027 | AC PRO.COM | HMSV-A-CB | GMV-72WM/B-F(U) |  |  |  | GMV-72WM/B-F(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
10509440 | 1/1/2027 | AC PRO.COM | HMSV-A-CB | GMV-72WM/B-F(U) |  |  |  | GMV-72WM/B-F(U) | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
10509441 | 1/1/2027 | AC PRO.COM | HMSV-A-CB | GMV-96WM/B-F(U) |  |  |  | GMV-96WM/B-F(U) | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
10509442 | 1/1/2027 | AC PRO.COM | HMSV-A-CB | GMV-96WM/B-F(U) |  |  |  | GMV-96WM/B-F(U) | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
10509445 | 1/1/2027 | AC PRO.COM | HMSR-A-CB | GMV-Q72WM/B-F(U) |  |  |  | GMV-Q72WM/B-F(U) | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
10509447 | 1/1/2027 | AC PRO.COM | HMSR-A-CB | GMV-Q96WM/B-F(U) |  |  |  | GMV-Q96WM/B-F(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
10306464 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H6CDC712(A) |  |  |  | IOV072H6CDC712(A) | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
10306462 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H6CDC712(A) |  |  |  | IOV072H6CDC712(A) | Ducted Indoor Units | 69000 | 11.1 | 20 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
200084017 | 1/1/2027 | MAMMOTH | HMSR-A-CB | V5BV-R96WMBK |  |  |  | V5BV-R96WMBK | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
200084018 | 1/1/2027 | REZNOR | HMSR-A-CB | V5BV-R96WMBK |  |  |  | V5BV-R96WMBK | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
200084019 | 1/1/2027 | NORTEK | HMSR-A-CB | V5BV-R96WMBK |  |  |  | V5BV-R96WMBK | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
200084026 | 1/1/2027 | MAMMOTH | HMSR-A-CB | V5BV-R120WMBK |  |  |  | V5BV-R120WMBK | Non-Ducted Indoor Units | 111000 | 11.5 | 24 | 126000 | 3.5 | 83000 | 2.25 | R-410A | 9.25
200084027 | 1/1/2027 | REZNOR | HMSR-A-CB | V5BV-R120WMBK |  |  |  | V5BV-R120WMBK | Non-Ducted Indoor Units | 111000 | 11.5 | 24 | 126000 | 3.5 | 83000 | 2.25 | R-410A | 9.25
200084028 | 1/1/2027 | NORTEK | HMSR-A-CB | V5BV-R120WMBK |  |  |  | V5BV-R120WMBK | Non-Ducted Indoor Units | 111000 | 11.5 | 24 | 126000 | 3.5 | 83000 | 2.25 | R-410A | 9.25
10342541 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q72WM/B-F(U) | GMV-Q72WM/B-F(U) |  |  | GMV-Q144WM/B-F(U) | Non-Ducted Indoor Units | 134000 | 11.6 | 23 | 150000 | 3.65 | 106000 | 2.35 | R-410A | 11.1667
10341435 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/B-U(U) |  |  |  | GMV-Q96WM/B-U(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
10341439 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q72WM/B-U(U) | GMV-Q72WM/B-U(U) |  |  | GMV-Q144WM/B-U(U) | Non-Ducted Indoor Units | 134000 | 11.6 | 23 | 150000 | 3.65 | 106000 | 2.35 | R-410A | 11.1667
10306437 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) |  |  |  | IOV096H3CDC716(A) | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
10306434 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) |  |  |  | IOV072H3CDC712(A) | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
10306435 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) |  |  |  | IOV096H3CDC716(A) | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
10306432 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) |  |  |  | IOV072H3CDC712(A) | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
10267500 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) |  |  |  | GMV-72WM/B-U(U) | Ducted Indoor Units | 69000 | 11.1 | 20 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
10267501 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) |  |  |  | GMV-72WM/B-U(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
202515493 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 |  |  |  | ARUB072BTE4 | Ducted Indoor Units | 69000 | 13 | 23.5 | 77000 | 3.82 | 51000 | 2.7 | R-410A | 5.75
202515494 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 |  |  |  | ARUB072BTE4 | Non-Ducted Indoor Units | 69000 | 13.4 | 27.5 | 77000 | 3.8 | 51000 | 2.6 | R-410A | 5.75
201903141 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER096C432G |  |  |  | VER096C432G | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
201903147 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER072C432G | VER072C432G |  |  | VER144C432G | Non-Ducted Indoor Units | 134000 | 11.6 | 23 | 150000 | 3.65 | 106000 | 2.35 | R-410A | 11.1667
201902894 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Ducted Indoor Units | 69000 | 11.1 | 20 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
201902896 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
202515518 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 |  |  |  | ARUB072DTE4 | Ducted Indoor Units | 69000 | 13 | 23.5 | 77000 | 3.82 | 51000 | 2.7 | R-410A | 5.75
202515519 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 |  |  |  | ARUB072DTE4 | Non-Ducted Indoor Units | 69000 | 13.4 | 27.5 | 77000 | 3.8 | 51000 | 2.6 | R-410A | 5.75
202519343 | 1/1/2027 | GREE | HMSV-A-CB | GMV-Y72WM/C-F(U) |  |  |  | GMV-Y72WM/C-F(U) | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
202519344 | 1/1/2027 | GREE | HMSV-A-CB | GMV-Y72WM/C-F(U) |  |  |  | GMV-Y72WM/C-F(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 22 | 77000 | 3.5 | 51000 | 2.4 | R-410A | 5.75
202519346 | 1/1/2027 | GREE | HMSV-A-CB | GMV-Y96WM/C-F(U) |  |  |  | GMV-Y96WM/C-F(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 22 | 103000 | 3.5 | 67000 | 2.3 | R-410A | 7.6667
203266412 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q120WM/B-F(U) |  |  |  | GMV-Q120WM/B-F(U) | Non-Ducted Indoor Units | 114000 | 11.5 | 22 | 126000 | 3.5 | 81000 | 2.25 | R-410A | 9.5
203266414 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-F(U) |  |  |  | GMV-120WM/B-F(U) | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
203266443 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC720(A) |  |  |  | IOV120H3CDC720(A) | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
203266444 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432Y |  |  |  | VEP120C432Y | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
203266445 | 1/1/2027 | AC PRO.COM | HMSV-A-CB | GMV-120WM/B-F(U) |  |  |  | GMV-120WM/B-F(U) | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
203293238 | 1/1/2027 | GREE | HMSV-A-CB | GMV-V72W/A-F(U) |  |  |  | GMV-V72W/A-F(U) | Ducted Indoor Units | 69000 | 11.2 | 20 | 77000 | 3.4 | 60000 | 2.25 | R-410A | 5.75
203360784 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC120KHP/220V |  |  |  | TVRF-OC120KHP/220V | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
204442791 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR |  |  |  | AM072KXVTFR | Non-Ducted Indoor Units | 69000 | 14.1 | 32.6 | 77000 | 4.35 | 77000 | 2.58 | R-410A | 5.75
204442759 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR |  |  |  | AM072FXVAJR | Non-Ducted Indoor Units | 69000 | 13 | 29.7 | 77000 | 3.71 | 51000 | 2.73 | R-410A | 5.75
204442760 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096FXVAJR |  |  |  | AM096FXVAJR | Non-Ducted Indoor Units | 92000 | 12.7 | 28.6 | 103000 | 3.86 | 67000 | 2.65 | R-410A | 7.6667
203398521 | 1/1/2027 | GREE | HMSR-A-CB | GMV-VQ72W/A-F(U) |  |  |  | GMV-VQ72W/A-F(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 21 | 77000 | 3.4 | 60000 | 2.25 | R-410A | 5.75
204442799 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR |  |  |  | AM072KXVTJR | Non-Ducted Indoor Units | 69000 | 14.1 | 32.6 | 77000 | 4.35 | 77000 | 2.58 | R-410A | 5.75
204442800 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR |  |  |  | AM096KXVTJR | Non-Ducted Indoor Units | 92000 | 14.4 | 33 | 103000 | 4.32 | 103000 | 2.45 | R-410A | 7.6667
207337153 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G |  |  |  | VEP072C432G | Ducted Indoor Units | 69000 | 11.1 | 20 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
8849292 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/B-F(U) |  |  |  | GMV-Q96WM/B-F(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
9088672 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712 |  |  |  | IOV072H3CDC712 | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
9133441 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/220V |  |  |  | TVRF-OC72KHP/220V | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
9133442 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/220V |  |  |  | TVRF-OC72KHP/220V | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
9133449 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V |  |  |  | TVRF-OC96KHP/220V | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
9133480 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V |  |  |  | TVRF-OC96KHP/220V | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
9088681 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC713 |  |  |  | IOV096H3CDC736 | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
9088674 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712 |  |  |  | IOV072H3CDC712 | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
9088679 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC713 |  |  |  | IOV096H3CDC736 | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
9088684 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC714 |  |  |  | IOV120H3CDC714 | Non-Ducted Indoor Units | 114000 | 11.2 | 24 | 129000 | 3.5 | 87000 | 2.25 | R-410A | 9.5
8849290 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q72WM/B-F(U) |  |  |  | GMV-Q72WM/B-F(U) | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
10479766 | 1/1/2027 | GREE | HMSV-A-CB | GMV-V72W/A-F(U) |  |  |  | GMV-V72W/A-F(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 21 | 77000 | 3.5 | 60000 | 2.25 | R-410A | 5.75
10479767 | 1/1/2027 | GREE | HMSV-A-CB | GMV-V72W/A-F(U) |  |  |  | GMV-V72W/A-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 11.25 | 20.5 | 77000 | 3.55 | 60000 | 2.25 | R-410A | 5.75
10479769 | 1/1/2027 | GREE | HMSV-A-CB | GMV-V96W/A-F(U) |  |  |  | GMV-V96W/A-F(U) | Non-Ducted Indoor Units | 92000 | 11.2 | 21 | 103000 | 3.5 | 68000 | 2.25 | R-410A | 7.6667
9956605 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER072C432Y |  |  |  | VER072C432Y | Non-Ducted Indoor Units | 67000 | 11.5 | 22 | 75000 | 3.4 | 51000 | 2.4 | R-410A | 5.5833
9956572 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
9956563 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
9956565 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y |  |  |  | VEP072C432Y | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
9956570 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y |  |  |  | VEP096C432Y | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
9956608 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER096C432Y |  |  |  | VER096C432Y | Non-Ducted Indoor Units | 92000 | 11.2 | 23.5 | 100000 | 3.5 | 67000 | 2.4 | R-410A | 7.6667
7793597 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) |  |  |  | GMV-72WM/B-F(U) | Ducted Indoor Units | 69000 | 11.1 | 21.5 | 77000 | 3.4 | 51000 | 2.4 | R-410A | 5.75
7793598 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) |  |  |  | GMV-72WM/B-F(U) | Non-Ducted Indoor Units | 69000 | 11.3 | 23 | 77000 | 3.7 | 51000 | 2.45 | R-410A | 5.75
7835428 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) |  |  |  | GMV-96WM/B-F(U) | Non-Ducted Indoor Units | 92000 | 12.6 | 26 | 103000 | 3.9 | 67000 | 2.5 | R-410A | 7.6667
7845593 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) |  |  |  | GMV-96WM/B-F(U) | Ducted Indoor Units | 92000 | 11.2 | 20 | 103000 | 3.4 | 67000 | 2.38 | R-410A | 7.6667
9119332 | 1/1/2027 | LG | HMSV-A-CB | ARUN072QTE4 |  |  |  | ARUN072QTE4 | Ducted Indoor Units | 69000 | 13 | 23.5 | 77000 | 3.82 | 51000 | 2.7 | R-410A | 5.75
9119333 | 1/1/2027 | LG | HMSV-A-CB | ARUN072QTE4 |  |  |  | ARUN072QTE4 | Non-Ducted Indoor Units | 69000 | 14.5 | 29 | 77000 | 4.3 | 51000 | 2.75 | R-410A | 5.75
9119334 | 1/1/2027 | LG | HMSV-A-CB | ARUN096QTE4 |  |  |  | ARUN096QTE4 | Ducted Indoor Units | 92000 | 12.7 | 25 | 103000 | 3.73 | 67000 | 2.71 | R-410A | 7.6667
9119335 | 1/1/2027 | LG | HMSV-A-CB | ARUN096QTE4 |  |  |  | ARUN096QTE4 | Non-Ducted Indoor Units | 92000 | 15.1 | 38.5 | 103000 | 4.3 | 67000 | 2.82 | R-410A | 7.6667
9119336 | 1/1/2027 | LG | HMSV-A-CB | ARUN121QTE4 |  |  |  | ARUN121QTE4 | Ducted Indoor Units | 114000 | 12.6 | 23 | 129000 | 3.53 | 84000 | 2.57 | R-410A | 9.5
9119337 | 1/1/2027 | LG | HMSV-A-CB | ARUN121QTE4 |  |  |  | ARUN121QTE4 | Non-Ducted Indoor Units | 114000 | 14.5 | 29 | 129000 | 3.9 | 84000 | 2.72 | R-410A | 9.5
203400951 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-72U8SNB |  |  |  | AVWT-72U8SNB | Ducted Indoor Units | 69000 | 12.3 | 23 | 76000 | 3.55 | 52000 | 2.35 | R-410A | 5.75
203400952 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-72U8SNB |  |  |  | AVWT-72U8SNB | Non-Ducted Indoor Units | 69000 | 15 | 30.7 | 76000 | 4.2 | 52000 | 2.84 | R-410A | 5.75
203400953 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-72U8SNB |  |  |  | AVWT-72U8SNB | Mixed Ducted and Non-Ducted Indoor Units | 69000 | 13.65 | 26.85 | 76000 | 3.87 | 52000 | 2.59 | R-410A | 5.75
10274220 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-072UHSPB |  |  |  | AVWT-072UHSPB | Ducted Indoor Units | 69000 | 13.2 | 23.5 | 76000 | 4 | 55000 | 2.6 | R-410A | 5.75
10274221 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-072UHSPB |  |  |  | AVWT-072UHSPB | Non-Ducted Indoor Units | 69000 | 15.6 | 31.8 | 76000 | 4.9 | 55000 | 3 | R-410A | 5.75
10274222 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-096UHSQB |  |  |  | AVWT-096UHSQB | Ducted Indoor Units | 92000 | 11.8 | 23.8 | 103000 | 3.7 | 76000 | 2.5 | R-410A | 7.6667
10274223 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-096UHSQB |  |  |  | AVWT-096UHSQB | Non-Ducted Indoor Units | 92000 | 12.2 | 26.4 | 103000 | 4.5 | 76000 | 2.9 | R-410A | 7.6667
10274224 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-120UHSQB |  |  |  | AVWT-120UHSQB | Ducted Indoor Units | 114000 | 11.5 | 23.5 | 126000 | 3.7 | 89000 | 2.3 | R-410A | 9.5
10274225 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-120UHSQB |  |  |  | AVWT-120UHSQB | Non-Ducted Indoor Units | 114000 | 12.1 | 26.5 | 126000 | 4.2 | 89000 | 2.6 | R-410A | 9.5
10274227 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-096UHSQB |  |  |  | AVWT-096UHSQB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 12 | 25.1 | 103000 | 4.1 | 76000 | 2.7 | R-410A | 7.6667
10274228 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-120UHSQB |  |  |  | AVWT-120UHSQB | Mixed Ducted and Non-Ducted Indoor Units | 114000 | 11.8 | 25 | 126000 | 3.95 | 89000 | 2.45 | R-410A | 9.5
10567397 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-120U8STB |  |  |  | AVWT-120U8STB | Non-Ducted Indoor Units | 115000 | 13.2 | 30.55 | 129000 | 4.12 | 83000 | 2.72 | R-410A | 9.5833
10567398 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-120U8STB |  |  |  | AVWT-120U8STB | Mixed Ducted and Non-Ducted Indoor Units | 115000 | 12.4 | 26.97 | 129000 | 3.73 | 83000 | 2.51 | R-410A | 9.5833
10594382 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-96U8STB |  |  |  | AVWT-96U8STB | Ducted Indoor Units | 92000 | 12.25 | 23.3 | 103000 | 3.45 | 67000 | 2.3 | R-410A | 7.6667
10594383 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-96U8STB |  |  |  | AVWT-96U8STB | Non-Ducted Indoor Units | 92000 | 14.15 | 31.65 | 103000 | 4.1 | 67000 | 2.6 | R-410A | 7.6667
10594384 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-96U8STB |  |  |  | AVWT-96U8STB | Mixed Ducted and Non-Ducted Indoor Units | 92000 | 13.2 | 27.47 | 103000 | 3.77 | 67000 | 2.45 | R-410A | 7.6667
10562601 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-072U8SNB |  |  |  | AVWT-072U8SNB | Ducted Indoor Units | 69000 | 12.3 | 23 | 76000 | 3.55 | 52000 | 2.35 | R-410A | 5.75
10562602 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-072U8SNB |  |  |  | AVWT-072U8SNB | Non-Ducted Indoor Units | 69000 | 15 | 30.7 | 76000 | 4.2 | 52000 | 2.84 | R-410A | 5.75
208812545 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA96ULBV5 |  |  | AOUA216ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208812546 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULBV5 | AOUA120ULBV5 |  |  | AOUA240ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208931865 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 |  |  |  | AOUA144ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.3 | 24.3 | 154000 | 3.94 | 106000 | 2.44 | R-410A | 11.5
208931867 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 |  |  |  | AOUA168ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.85 | 22.8 | 180000 | 3.69 | 124000 | 2.31 | R-410A | 13.3333
208931869 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 |  |  |  | AOUA192ULBV5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 21.95 | 206000 | 3.48 | 140000 | 2.19 | R-410A | 15.3333
208812550 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA96ULCV5 |  |  | AOUA216ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
208812551 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120ULCV5 | AOUA120ULCV5 |  |  | AOUA240ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19.1667
208931887 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 |  |  |  | AOUA144ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.3 | 24.3 | 154000 | 3.94 | 106000 | 2.44 | R-410A | 11.5
208931889 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 |  |  |  | AOUA168ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.85 | 22.8 | 180000 | 3.69 | 124000 | 2.31 | R-410A | 13.3333
208931891 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 |  |  |  | AOUA192ULCV5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 21.95 | 206000 | 3.48 | 140000 | 2.19 | R-410A | 15.3333
213895054 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP1921HT6P-UL | Ducted Indoor Units | 184000 | 11.3 | 22.4 | 206000 | 4 | 154000 | 2.51 | R-410A | 15.3333
213895059 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP1921HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 22.3 | 206000 | 4.13 | 154000 | 2.6 | R-410A | 15.3333
213894130 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL |  |  |  | MMY-MUP1441HT6P-UL | Ducted Indoor Units | 138000 | 11.4 | 21.6 | 154000 | 3.64 | 109000 | 2.53 | R-410A | 11.5
213894136 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0721HT6P-UL |  |  | MMY-UP2161HT6P-UL | Ducted Indoor Units | 206000 | 11.6 | 20.9 | 232000 | 4.01 | 164000 | 2.74 | R-410A | 17.1667
213894093 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL |  |  |  | MMY-MUP1441HT6P-UL | Non-Ducted Indoor Units | 138000 | 11.1 | 22.7 | 154000 | 3.93 | 109000 | 2.66 | R-410A | 11.5
213894095 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0721HT6P-UL |  |  | MMY-UP2161HT6P-UL | Non-Ducted Indoor Units | 206000 | 10.9 | 21.7 | 232000 | 4.04 | 164000 | 2.76 | R-410A | 17.1667
213895023 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0721HT6P-UL |  |  | MMY-UP2161HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.15 | 232000 | 4.02 | 164000 | 2.74 | R-410A | 17.1667
213895014 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL |  |  |  | MMY-MUP1441HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.25 | 22.15 | 154000 | 3.78 | 109000 | 2.59 | R-410A | 11.5
213895067 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2401HT6P-UL | Ducted Indoor Units | 230000 | 11.2 | 19.9 | 258000 | 3.88 | 182000 | 2.6 | R-410A | 19.1667
213895071 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2401HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.95 | 22 | 258000 | 3.93 | 182000 | 2.63 | R-410A | 19.1667
213895020 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL |  |  |  | MMY-MUP1681HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.35 | 180000 | 3.59 | 132000 | 2.25 | R-410A | 13.3333
213894094 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL |  |  |  | MMY-MUP1681HT6P-UL | Non-Ducted Indoor Units | 160000 | 11.4 | 21.7 | 180000 | 3.63 | 132000 | 2.16 | R-410A | 13.3333
213895016 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL | MMY-MUP072H1HT6PUL |  |  | MMY-UP144H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.95 | 23.1 | 154000 | 4.47 | 128000 | 2.74 | R-410A | 11.5
213894132 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL | MMY-MUP072H1HT6PUL |  |  | MMY-UP144H1HT6PUL | Ducted Indoor Units | 138000 | 11.6 | 22.3 | 154000 | 4.21 | 128000 | 2.64 | R-410A | 11.5
213894128 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT6PUL | MMY-MUP072H1HT6PUL |  |  | MMY-UP144H1HT6PUL | Non-Ducted Indoor Units | 138000 | 12.3 | 23.9 | 154000 | 4.74 | 128000 | 2.84 | R-410A | 11.5
213895061 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  |  | MMY-UP192H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 21.3 | 206000 | 4.37 | 174000 | 2.66 | R-410A | 15.3333
213895056 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  |  | MMY-UP192H1HT6PUL | Ducted Indoor Units | 184000 | 10.8 | 21 | 206000 | 4.33 | 174000 | 2.58 | R-410A | 15.3333
213895051 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  |  | MMY-UP192H1HT6PUL | Non-Ducted Indoor Units | 184000 | 10.8 | 21.6 | 206000 | 4.41 | 174000 | 2.75 | R-410A | 15.3333
213895069 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  |  | MMY-UP240H1HT6PUL | Ducted Indoor Units | 230000 | 11.3 | 20.1 | 258000 | 3.99 | 232000 | 2.61 | R-410A | 19.1667
213895065 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  |  | MMY-UP240H1HT6PUL | Non-Ducted Indoor Units | 230000 | 12 | 22.5 | 258000 | 3.92 | 232000 | 2.44 | R-410A | 19.1667
213895073 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  |  | MMY-UP240H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.65 | 21.3 | 258000 | 3.95 | 232000 | 2.52 | R-410A | 19.1667
213895055 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP1921HT9P-UL | Ducted Indoor Units | 184000 | 11.3 | 22.4 | 206000 | 4 | 154000 | 2.51 | R-410A | 15.3333
213895060 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP1921HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 22.3 | 206000 | 4.13 | 154000 | 2.6 | R-410A | 15.3333
213895068 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2401HT9P-UL | Ducted Indoor Units | 230000 | 11.2 | 19.9 | 258000 | 3.88 | 182000 | 2.6 | R-410A | 19.1667
213895072 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2401HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.75 | 20.65 | 258000 | 3.91 | 182000 | 2.63 | R-410A | 19.1667
213895024 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0721HT9P-UL |  |  | MMY-UP2161HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.15 | 232000 | 4.02 | 164000 | 2.74 | R-410A | 17.1667
213895015 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL |  |  |  | MMY-MUP1441HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.25 | 22.15 | 154000 | 3.78 | 109000 | 2.59 | R-410A | 11.5
213894131 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL |  |  |  | MMY-MUP1441HT9P-UL | Ducted Indoor Units | 138000 | 11.4 | 21.6 | 154000 | 3.64 | 109000 | 2.53 | R-410A | 11.5
213894137 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0721HT9P-UL |  |  | MMY-UP2161HT9P-UL | Ducted Indoor Units | 206000 | 11.6 | 20.9 | 232000 | 4.01 | 164000 | 2.74 | R-410A | 17.1667
213894127 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL |  |  |  | MMY-MUP1441HT9P-UL | Non-Ducted Indoor Units | 138000 | 11.1 | 22.7 | 154000 | 3.93 | 109000 | 2.66 | R-410A | 11.5
213894135 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP0721HT9P-UL |  |  | MMY-UP2161HT9P-UL | Non-Ducted Indoor Units | 206000 | 10.9 | 21.7 | 232000 | 4.04 | 164000 | 2.76 | R-410A | 17.1667
213894134 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL |  |  |  | MMY-MUP1681HT9P-UL | Non-Ducted Indoor Units | 160000 | 11.4 | 21.7 | 180000 | 3.63 | 132000 | 2.16 | R-410A | 13.3333
213895021 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL |  |  |  | MMY-MUP1681HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.35 | 180000 | 3.59 | 132000 | 2.25 | R-410A | 13.3333
213895017 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL | MMY-MUP072H1HT9PUL |  |  | MMY-UP144H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.95 | 23.1 | 154000 | 4.47 | 128000 | 2.74 | R-410A | 11.5
213894133 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL | MMY-MUP072H1HT9PUL |  |  | MMY-UP144H1HT9PUL | Ducted Indoor Units | 138000 | 11.6 | 22.3 | 154000 | 4.21 | 128000 | 2.64 | R-410A | 11.5
213894129 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP072H1HT9PUL | MMY-MUP072H1HT9PUL |  |  | MMY-UP144H1HT9PUL | Non-Ducted Indoor Units | 138000 | 12.3 | 23.9 | 154000 | 4.74 | 128000 | 2.84 | R-410A | 11.5
213895052 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  |  | MMY-UP192H1HT9PUL | Non-Ducted Indoor Units | 184000 | 10.8 | 21.6 | 206000 | 4.41 | 174000 | 2.75 | R-410A | 15.3333
213895062 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  |  | MMY-UP192H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 21.3 | 206000 | 4.37 | 174000 | 2.66 | R-410A | 15.3333
213895057 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  |  | MMY-UP192H1HT9PUL | Ducted Indoor Units | 184000 | 10.8 | 21 | 206000 | 4.33 | 174000 | 2.58 | R-410A | 15.3333
213895070 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  |  | MMY-UP240H1HT9PUL | Ducted Indoor Units | 230000 | 11.3 | 20.1 | 258000 | 3.99 | 232000 | 2.61 | R-410A | 19.1667
213895066 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  |  | MMY-UP240H1HT9PUL | Non-Ducted Indoor Units | 230000 | 12 | 22.5 | 258000 | 3.92 | 232000 | 2.44 | R-410A | 19.1667
213895074 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  |  | MMY-UP240H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.65 | 21.3 | 258000 | 3.95 | 232000 | 2.52 | R-410A | 19.1667
213885192 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP1921FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.8 | 23.35 | 206000 | 4.1 | 148000 | 2.46 | R-410A | 15.3333
213884928 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP1921FT6P-UL | Non-Ducted Indoor Units | 184000 | 12.1 | 24.7 | 206000 | 4.4 | 148000 | 2.48 | R-410A | 15.3333
213884932 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP1921FT6P-UL | Ducted Indoor Units | 184000 | 11.5 | 22 | 206000 | 3.81 | 148000 | 2.45 | R-410A | 15.3333
213884942 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2401FT6P-UL | Non-Ducted Indoor Units | 230000 | 11.9 | 22.9 | 258000 | 4.18 | 174000 | 2.55 | R-410A | 19.1667
213884946 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2401FT6P-UL | Ducted Indoor Units | 230000 | 11.2 | 21.8 | 258000 | 3.47 | 174000 | 2.53 | R-410A | 19.1667
213885186 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL |  |  |  | MMY-MUP1441FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.6 | 22.95 | 154000 | 3.9 | 100000 | 2.62 | R-410A | 11.5
213885197 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0721FT6P-UL |  |  | MMY-UP2161FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 22.9 | 232000 | 3.98 | 156000 | 2.7 | R-410A | 17.1667
213885199 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2401FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.55 | 22.35 | 258000 | 3.82 | 174000 | 2.54 | R-410A | 19.1667
213884916 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL |  |  |  | MMY-MUP1441FT6P-UL | Non-Ducted Indoor Units | 138000 | 11.9 | 24.3 | 154000 | 4 | 100000 | 2.65 | R-410A | 11.5
213884918 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL |  |  |  | MMY-MUP1441FT6P-UL | Ducted Indoor Units | 138000 | 11.3 | 21.6 | 154000 | 3.81 | 100000 | 2.6 | R-410A | 11.5
213884938 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0721FT6P-UL |  |  | MMY-UP2161FT6P-UL | Non-Ducted Indoor Units | 206000 | 12 | 23.9 | 232000 | 4.33 | 156000 | 2.75 | R-410A | 17.1667
213884940 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP0721FT6P-UL |  |  | MMY-UP2161FT6P-UL | Ducted Indoor Units | 206000 | 11.3 | 21.9 | 232000 | 3.63 | 156000 | 2.65 | R-410A | 17.1667
213884926 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL |  |  |  | MMY-MUP1681FT6P-UL | Ducted Indoor Units | 160000 | 10.7 | 21.5 | 180000 | 3.54 | 122000 | 2.47 | R-410A | 13.3333
213884924 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL |  |  |  | MMY-MUP1681FT6P-UL | Non-Ducted Indoor Units | 160000 | 11.2 | 24.2 | 180000 | 3.85 | 122000 | 2.57 | R-410A | 13.3333
213885189 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL |  |  |  | MMY-MUP1681FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 22.85 | 180000 | 3.69 | 122000 | 2.52 | R-410A | 13.3333
213885195 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1921FT6P-UL |  |  |  | MMY-MUP1921FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.7 | 21.05 | 206000 | 3.5 | 146000 | 2.27 | R-410A | 15.3333
213884936 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1921FT6P-UL |  |  |  | MMY-MUP1921FT6P-UL | Non-Ducted Indoor Units | 184000 | 10.7 | 21.4 | 206000 | 3.64 | 146000 | 2.29 | R-410A | 15.3333
213884937 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1921FT6P-UL |  |  |  | MMY-MUP1921FT6P-UL | Ducted Indoor Units | 184000 | 10.7 | 20.7 | 206000 | 3.37 | 146000 | 2.25 | R-410A | 15.3333
213884922 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL | MMY-MUP072H1FT6PUL |  |  | MMY-UP144H1FT6PUL | Ducted Indoor Units | 138000 | 12.9 | 23.4 | 154000 | 4.12 | 128000 | 2.73 | R-410A | 11.5
213884920 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL | MMY-MUP072H1FT6PUL |  |  | MMY-UP144H1FT6PUL | Non-Ducted Indoor Units | 138000 | 13.4 | 25 | 154000 | 4.87 | 128000 | 2.77 | R-410A | 11.5
213885187 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT6PUL | MMY-MUP072H1FT6PUL |  |  | MMY-UP144H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.15 | 24.2 | 154000 | 4.49 | 128000 | 2.75 | R-410A | 11.5
213885193 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  |  | MMY-UP192H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.85 | 22.9 | 206000 | 4.22 | 172000 | 2.62 | R-410A | 15.3333
213884934 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  |  | MMY-UP192H1FT6PUL | Ducted Indoor Units | 184000 | 12.5 | 22.5 | 206000 | 3.92 | 172000 | 2.62 | R-410A | 15.3333
213884930 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  |  | MMY-UP192H1FT6PUL | Non-Ducted Indoor Units | 184000 | 13.2 | 23.3 | 206000 | 4.53 | 172000 | 2.63 | R-410A | 15.3333
213885200 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  |  | MMY-UP240H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.35 | 22.9 | 258000 | 4 | 220000 | 2.48 | R-410A | 19.1667
213884948 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  |  | MMY-UP240H1FT6PUL | Ducted Indoor Units | 230000 | 12.1 | 22.5 | 258000 | 3.6 | 220000 | 2.43 | R-410A | 19.1667
213884944 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  |  | MMY-UP240H1FT6PUL | Non-Ducted Indoor Units | 230000 | 12.6 | 23.3 | 258000 | 4.4 | 220000 | 2.54 | R-410A | 19.1667
213884933 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP1921FT9P-UL | Ducted Indoor Units | 184000 | 11.5 | 22 | 206000 | 3.81 | 148000 | 2.45 | R-410A | 15.3333
213884929 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP1921FT9P-UL | Non-Ducted Indoor Units | 184000 | 12.1 | 24.7 | 206000 | 4.4 | 148000 | 2.48 | R-410A | 15.3333
213885191 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP0961FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP1921FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.8 | 23.35 | 206000 | 4.1 | 148000 | 2.46 | R-410A | 15.3333
213884917 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL |  |  |  | MMY-MUP1441FT9P-UL | Non-Ducted Indoor Units | 138000 | 11.9 | 24.3 | 154000 | 4 | 100000 | 2.65 | R-410A | 11.5
213884919 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL |  |  |  | MMY-MUP1441FT9P-UL | Ducted Indoor Units | 138000 | 11.3 | 21.6 | 154000 | 3.81 | 100000 | 2.6 | R-410A | 11.5
213884941 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0721FT9P-UL |  |  | MMY-UP2161FT9P-UL | Ducted Indoor Units | 206000 | 11.3 | 21.9 | 232000 | 3.63 | 156000 | 2.65 | R-410A | 17.1667
213884939 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0721FT9P-UL |  |  | MMY-UP2161FT9P-UL | Non-Ducted Indoor Units | 206000 | 12 | 23.9 | 232000 | 4.33 | 156000 | 2.75 | R-410A | 17.1667
213884943 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2401FT9P-UL | Non-Ducted Indoor Units | 230000 | 11.9 | 22.9 | 258000 | 4.18 | 174000 | 2.55 | R-410A | 19.1667
213884947 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2401FT9P-UL | Ducted Indoor Units | 230000 | 11.2 | 21.8 | 258000 | 3.47 | 174000 | 2.53 | R-410A | 19.1667
213885185 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL |  |  |  | MMY-MUP1441FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.6 | 22.95 | 154000 | 3.9 | 100000 | 2.62 | R-410A | 11.5
213885196 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0721FT9P-UL |  |  | MMY-UP2161FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 22.9 | 232000 | 3.98 | 156000 | 2.7 | R-410A | 17.1667
213885198 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2401FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.55 | 22.35 | 258000 | 3.82 | 174000 | 2.54 | R-410A | 19.1667
213885190 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL |  |  |  | MMY-MUP1681FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 22.85 | 180000 | 3.69 | 122000 | 2.52 | R-410A | 13.3333
213884927 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL |  |  |  | MMY-MUP1681FT9P-UL | Ducted Indoor Units | 160000 | 10.7 | 21.5 | 180000 | 3.54 | 122000 | 2.47 | R-410A | 13.3333
213884925 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL |  |  |  | MMY-MUP1681FT9P-UL | Non-Ducted Indoor Units | 160000 | 11.2 | 24.2 | 180000 | 3.85 | 122000 | 2.57 | R-410A | 13.3333
213884923 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL | MMY-MUP072H1FT9PUL |  |  | MMY-UP144H1FT9PUL | Ducted Indoor Units | 138000 | 12.9 | 23.4 | 154000 | 4.12 | 128000 | 2.73 | R-410A | 11.5
213884921 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL | MMY-MUP072H1FT9PUL |  |  | MMY-UP144H1FT9PUL | Non-Ducted Indoor Units | 138000 | 13.4 | 25 | 154000 | 4.87 | 128000 | 2.77 | R-410A | 11.5
213885188 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP072H1FT9PUL | MMY-MUP072H1FT9PUL |  |  | MMY-UP144H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.15 | 24.2 | 154000 | 4.49 | 128000 | 2.75 | R-410A | 11.5
213885194 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  |  | MMY-UP192H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.85 | 22.9 | 206000 | 4.22 | 172000 | 2.62 | R-410A | 15.3333
213884931 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  |  | MMY-UP192H1FT9PUL | Non-Ducted Indoor Units | 184000 | 13.2 | 23.3 | 206000 | 4.53 | 172000 | 2.63 | R-410A | 15.3333
213884935 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  |  | MMY-UP192H1FT9PUL | Ducted Indoor Units | 184000 | 12.5 | 22.5 | 206000 | 3.92 | 172000 | 2.62 | R-410A | 15.3333
213884949 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  |  | MMY-UP240H1FT9PUL | Ducted Indoor Units | 230000 | 12.1 | 22.5 | 258000 | 3.6 | 220000 | 2.43 | R-410A | 19.1667
213884945 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  |  | MMY-UP240H1FT9PUL | Non-Ducted Indoor Units | 230000 | 12.6 | 23.3 | 258000 | 4.4 | 220000 | 2.54 | R-410A | 19.1667
213885201 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  |  | MMY-UP240H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.35 | 22.9 | 258000 | 4 | 220000 | 2.48 | R-410A | 19.1667
213893744 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE1203AN41AN |  |  | TUHYE2163BN41AN | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213916727 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN41AN | TUHYE1203AN41AN |  |  | TUHYE2163BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213916731 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE1204AN41AN |  |  | TUHYE2164BN41AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893745 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN41AN | TUHYE1204AN41AN |  |  | TUHYE2164BN41AN | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
207591022 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
207591023 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
207591024 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
207591025 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
204723044 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
204723045 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
204723046 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
204723047 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
202073589 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H72DXN1 |  |  | MV5-H168DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 11.35 | 19.73 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
202073590 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H96DXN1 |  |  | MV5-H192DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 10.8 | 19.3 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
201994665 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201994667 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201994668 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201994670 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201850244 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201850245 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201850246 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201850247 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201850127 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201850128 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201850129 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201850130 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201830237 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H72DXN1 |  |  | MV5-H168DXN1* | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201830238 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H72DXN1 |  |  | MV5-H168DXN1* | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201830239 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H96DXN1 |  |  | MV5-H192DXN1* | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201830240 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H96DXN1 |  |  | MV5-H192DXN1* | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
207591054 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
207591055 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
207591056 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
207591057 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
204723076 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
204723077 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
204723078 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
204723079 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
202073605 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H72DZN1 |  |  | MV5-H168DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 11.35 | 19.73 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
202073606 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H96DZN1 |  |  | MV5-H192DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 10.8 | 19.3 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
201850276 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201850277 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201850278 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201850279 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201994719 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201994721 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201994723 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201994724 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201850159 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201850160 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201850161 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201850162 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
201830269 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H72DZN1 |  |  | MV5-H168DZN1* | Non-Ducted Indoor Units | 156000 | 11.39 | 19.31 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
201830270 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H72DZN1 |  |  | MV5-H168DZN1* | Ducted Indoor Units | 156000 | 11.4 | 20.15 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
201830271 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H96DZN1 |  |  | MV5-H192DZN1* | Non-Ducted Indoor Units | 176000 | 10.87 | 19.06 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
201830272 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H96DZN1 |  |  | MV5-H192DZN1* | Ducted Indoor Units | 176000 | 10.73 | 19.55 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
207591094 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
202073625 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DXN1 |  |  |  | MV5-2R241DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 21.05 | 256000 | 3.45 | 172000 | 2.31 | R-410A | 19.1667
201994787 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201830309 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DXN1 |  |  |  | MV5-2R241DXN1* | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201850316 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201850199 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
204723116 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
204723142 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201850226 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201830335 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DZN1 |  |  |  | MV5-2R241DZN1* | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201994829 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
201850342 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
202073638 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DZN1 |  |  |  | MV5-2R241DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 21.05 | 256000 | 3.45 | 172000 | 2.31 | R-410A | 19.1667
207591120 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 230000 | 11.2 | 21.3 | 256000 | 3.54 | 172000 | 2.36 | R-410A | 19.1667
202918869 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y | VPB096H4M-3Y |  |  | VPB216H4M-3Y | Non-Ducted Indoor Units | 206000 | 10.8 | 19.9 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202918870 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y | VPB096H4M-3Y |  |  | VPB216H4M-3Y | Ducted Indoor Units | 206000 | 10.9 | 20.2 | 232000 | 3.57 | 164000 | 2.36 | R-410A | 17.1667
202918871 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3Y | VPB096H4M-3Y |  |  | VPB216H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.85 | 20.05 | 232000 | 3.61 | 164000 | 2.36 | R-410A | 17.1667
202897234 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 | MV6-X96DXN1 |  |  | MV6-X216DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.85 | 20.05 | 232000 | 3.61 | 164000 | 2.36 | R-410A | 17.1667
202897164 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 | MV6-X96DXN1 |  |  | MV6-X216DXN1 | Non-Ducted Indoor Units | 206000 | 10.8 | 19.9 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202897165 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1 | MV6-X96DXN1 |  |  | MV6-X216DXN1 | Ducted Indoor Units | 206000 | 10.9 | 20.2 | 232000 | 3.57 | 164000 | 2.36 | R-410A | 17.1667
202897235 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 | MV6-X96DZN1 |  |  | MV6-X216DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.85 | 20.05 | 232000 | 3.61 | 164000 | 2.36 | R-410A | 17.1667
202897194 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 | MV6-X96DZN1 |  |  | MV6-X216DZN1 | Non-Ducted Indoor Units | 206000 | 10.8 | 19.9 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202897195 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1 | MV6-X96DZN1 |  |  | MV6-X216DZN1 | Ducted Indoor Units | 206000 | 10.9 | 20.2 | 232000 | 3.57 | 164000 | 2.36 | R-410A | 17.1667
202918866 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G | VPB096H4M-3G |  |  | VPB216H4M-3G | Non-Ducted Indoor Units | 206000 | 10.8 | 19.9 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202918867 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G | VPB096H4M-3G |  |  | VPB216H4M-3G | Ducted Indoor Units | 206000 | 10.9 | 20.2 | 232000 | 3.57 | 164000 | 2.36 | R-410A | 17.1667
202918868 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120H4M-3G | VPB096H4M-3G |  |  | VPB216H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.85 | 20.05 | 232000 | 3.61 | 164000 | 2.36 | R-410A | 17.1667
202918977 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y | VRB096H4M-3Y |  |  | VRB216H4M-3Y | Non-Ducted Indoor Units | 206000 | 10.9 | 19.5 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202918978 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y | VRB096H4M-3Y |  |  | VRB216H4M-3Y | Ducted Indoor Units | 206000 | 11 | 19.8 | 232000 | 3.54 | 164000 | 2.33 | R-410A | 17.1667
202918979 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y | VRB096H4M-3Y |  |  | VRB216H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.65 | 232000 | 3.6 | 164000 | 2.34 | R-410A | 17.1667
202918984 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3Y | VRB120H4M-3Y |  |  | VRB240H4M-3Y | Ducted Indoor Units | 230000 | 10.8 | 19.2 | 258000 | 3.37 | 182000 | 2.27 | R-410A | 19.1667
202897196 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 | MV6-R96DXN1 |  |  | MV6-R216DXN1 | Non-Ducted Indoor Units | 206000 | 10.9 | 19.5 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202897197 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 | MV6-R96DXN1 |  |  | MV6-R216DXN1 | Ducted Indoor Units | 206000 | 11 | 19.8 | 232000 | 3.54 | 164000 | 2.33 | R-410A | 17.1667
202897236 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 | MV6-R96DXN1 |  |  | MV6-R216DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.65 | 232000 | 3.6 | 164000 | 2.34 | R-410A | 17.1667
202897203 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1 | MV6-R120DXN1 |  |  | MV6-R240DXN1 | Ducted Indoor Units | 230000 | 10.8 | 19.2 | 258000 | 3.37 | 182000 | 2.27 | R-410A | 19.1667
202897205 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 | MV6-R120DZN1 |  |  | MV6-R240DZN1 | Ducted Indoor Units | 230000 | 10.8 | 19.2 | 258000 | 3.37 | 182000 | 2.27 | R-410A | 19.1667
202897237 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 | MV6-R96DZN1 |  |  | MV6-R216DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.65 | 232000 | 3.6 | 164000 | 2.34 | R-410A | 17.1667
202897198 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 | MV6-R96DZN1 |  |  | MV6-R216DZN1 | Non-Ducted Indoor Units | 206000 | 10.9 | 19.5 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202897199 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1 | MV6-R96DZN1 |  |  | MV6-R216DZN1 | Ducted Indoor Units | 206000 | 11 | 19.8 | 232000 | 3.54 | 164000 | 2.33 | R-410A | 17.1667
202918981 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G | VRB120H4M-3G |  |  | VRB240H4M-3G | Ducted Indoor Units | 230000 | 10.8 | 19.2 | 258000 | 3.37 | 182000 | 2.27 | R-410A | 19.1667
202918974 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G | VRB096H4M-3G |  |  | VRB216H4M-3G | Non-Ducted Indoor Units | 206000 | 10.9 | 19.5 | 232000 | 3.66 | 164000 | 2.36 | R-410A | 17.1667
202918975 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G | VRB096H4M-3G |  |  | VRB216H4M-3G | Ducted Indoor Units | 206000 | 11 | 19.8 | 232000 | 3.54 | 164000 | 2.33 | R-410A | 17.1667
202918976 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120H4M-3G | VRB096H4M-3G |  |  | VRB216H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.65 | 232000 | 3.6 | 164000 | 2.34 | R-410A | 17.1667
202918851 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y |  |  |  | VPB144H4M-3Y | Non-Ducted Indoor Units | 138000 | 11.1 | 21.1 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202918852 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y |  |  |  | VPB144H4M-3Y | Ducted Indoor Units | 138000 | 11.3 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202918853 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y |  |  |  | VPB144H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202897140 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 |  |  |  | MV6-X144DXN1 | Non-Ducted Indoor Units | 138000 | 11.1 | 21.1 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202897141 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 |  |  |  | MV6-X144DXN1 | Ducted Indoor Units | 138000 | 11.3 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202897180 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 |  |  |  | MV6-X144DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202897181 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 |  |  |  | MV6-X144DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202897150 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 |  |  |  | MV6-X144DZN1 | Non-Ducted Indoor Units | 138000 | 11.1 | 21.1 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202897151 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 |  |  |  | MV6-X144DZN1 | Ducted Indoor Units | 138000 | 11.3 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202918848 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G |  |  |  | VPB144H4M-3G | Non-Ducted Indoor Units | 138000 | 11.1 | 21.1 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202918849 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G |  |  |  | VPB144H4M-3G | Ducted Indoor Units | 138000 | 11.3 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202918850 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G |  |  |  | VPB144H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202918959 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y |  |  |  | VRB144H4M-3Y | Non-Ducted Indoor Units | 138000 | 11.3 | 19.9 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202918960 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y |  |  |  | VRB144H4M-3Y | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202918961 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y |  |  |  | VRB144H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 20.6 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202897152 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 |  |  |  | MV6-R144DXN1 | Non-Ducted Indoor Units | 138000 | 11.3 | 19.9 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202897153 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 |  |  |  | MV6-R144DXN1 | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202897182 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 |  |  |  | MV6-R144DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 20.6 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202897183 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 |  |  |  | MV6-R144DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 20.6 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202897154 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 |  |  |  | MV6-R144DZN1 | Non-Ducted Indoor Units | 138000 | 11.3 | 19.9 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202897155 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 |  |  |  | MV6-R144DZN1 | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202918956 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G |  |  |  | VRB144H4M-3G | Non-Ducted Indoor Units | 138000 | 11.3 | 19.9 | 154000 | 3.75 | 109000 | 2.43 | R-410A | 11.5
202918957 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G |  |  |  | VRB144H4M-3G | Ducted Indoor Units | 138000 | 11.5 | 21.3 | 154000 | 3.6 | 109000 | 2.45 | R-410A | 11.5
202918958 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G |  |  |  | VRB144H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 20.6 | 154000 | 3.67 | 109000 | 2.44 | R-410A | 11.5
202918857 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y |  |  |  | VPB168H4M-3Y | Non-Ducted Indoor Units | 160000 | 10.7 | 20.4 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202918858 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y |  |  |  | VPB168H4M-3Y | Ducted Indoor Units | 160000 | 10.9 | 20.6 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202918859 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y |  |  |  | VPB168H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.8 | 20.5 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202897142 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 |  |  |  | MV6-X168DXN1 | Non-Ducted Indoor Units | 160000 | 10.7 | 20.4 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202897143 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 |  |  |  | MV6-X168DXN1 | Ducted Indoor Units | 160000 | 10.9 | 20.6 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202897184 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 |  |  |  | MV6-X168DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.8 | 20.5 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202897185 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 |  |  |  | MV6-X168DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.8 | 20.5 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202897156 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 |  |  |  | MV6-X168DZN1 | Non-Ducted Indoor Units | 160000 | 10.7 | 20.4 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202897157 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 |  |  |  | MV6-X168DZN1 | Ducted Indoor Units | 160000 | 10.9 | 20.6 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202918854 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G |  |  |  | VPB168H4M-3G | Non-Ducted Indoor Units | 160000 | 10.7 | 20.4 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202918855 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G |  |  |  | VPB168H4M-3G | Ducted Indoor Units | 160000 | 10.9 | 20.6 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202918856 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G |  |  |  | VPB168H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.8 | 20.5 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202918965 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y |  |  |  | VRB168H4M-3Y | Non-Ducted Indoor Units | 160000 | 11 | 19.5 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202918966 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y |  |  |  | VRB168H4M-3Y | Ducted Indoor Units | 160000 | 11.2 | 20.7 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202918967 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y |  |  |  | VRB168H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 20.1 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202897158 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 |  |  |  | MV6-R168DXN1 | Non-Ducted Indoor Units | 160000 | 11 | 19.5 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202897159 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 |  |  |  | MV6-R168DXN1 | Ducted Indoor Units | 160000 | 11.2 | 20.7 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202897186 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 |  |  |  | MV6-R168DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 20.1 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202897187 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 |  |  |  | MV6-R168DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 20.1 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
202897160 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 |  |  |  | MV6-R168DZN1 | Non-Ducted Indoor Units | 160000 | 11 | 19.5 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202897161 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 |  |  |  | MV6-R168DZN1 | Ducted Indoor Units | 160000 | 11.2 | 20.7 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202918962 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G |  |  |  | VRB168H4M-3G | Non-Ducted Indoor Units | 160000 | 11 | 19.5 | 180000 | 3.5 | 128000 | 2.24 | R-410A | 13.3333
202918963 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G |  |  |  | VRB168H4M-3G | Ducted Indoor Units | 160000 | 11.2 | 20.7 | 180000 | 3.45 | 128000 | 2.3 | R-410A | 13.3333
202918964 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G |  |  |  | VRB168H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 20.1 | 180000 | 3.47 | 128000 | 2.27 | R-410A | 13.3333
213893574 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A | PUHY-P96YNU-A |  |  | PUHY-P192YSNU-A | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213893572 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A | PUHY-P96TNU-A |  |  | PUHY-P192TSNU-A | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213916614 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  |  | PUHY-EP192YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916616 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP120YNU-A |  |  | PUHY-EP216YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893466 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  |  | PUHY-EP192YSNU-A | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893467 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  |  | PUHY-EP192YSNU-A | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213893472 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP120YNU-A |  |  | PUHY-EP216YSNU-A | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213893460 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A |  |  |  | PUHY-EP144YNU-A | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213893470 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP120TNU-A |  |  | PUHY-EP216TSNU-A | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213893462 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  |  | PUHY-EP192TSNU-A | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893463 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  |  | PUHY-EP192TSNU-A | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213916575 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  |  | PUHY-EP192TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916577 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP120TNU-A |  |  | PUHY-EP216TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893458 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A |  |  |  | PUHY-EP144TNU-A | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213893833 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A | PUHY-HP72YNU-A |  |  | PUHY-HP144YSNU-A | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213893844 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A | PUHY-HP72YNU-A |  |  | PUHY-HP144YSNU-A | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213916630 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72YNU-A | PUHY-HP72YNU-A |  |  | PUHY-HP144YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213916631 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A | PUHY-HP96YNU-A |  |  | PUHY-HP192YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893550 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A | PUHY-HP96YNU-A |  |  | PUHY-HP192YSNU-A | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893551 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96YNU-A | PUHY-HP96YNU-A |  |  | PUHY-HP192YSNU-A | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213893556 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120YNU-A | PUHY-HP120YNU-A |  |  | PUHY-HP240YSNU-A | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213893835 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A | PUHY-HP72TNU-A |  |  | PUHY-HP144TSNU-A | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893831 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A | PUHY-HP72TNU-A |  |  | PUHY-HP144TSNU-A | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213916591 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP72TNU-A | PUHY-HP72TNU-A |  |  | PUHY-HP144TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213916592 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A | PUHY-HP96TNU-A |  |  | PUHY-HP192TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893546 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A | PUHY-HP96TNU-A |  |  | PUHY-HP192TSNU-A | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893547 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP96TNU-A | PUHY-HP96TNU-A |  |  | PUHY-HP192TSNU-A | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213893554 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-HP120TNU-A | PUHY-HP120TNU-A |  |  | PUHY-HP240TSNU-A | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213893711 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN | TUHYP0964AN40AN |  |  | TUHYP1924BN40AN | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213893710 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN | TUHYP0963AN40AN |  |  | TUHYP1923BN40AN | Non-Ducted Indoor Units | 184000 | 10.7 | 22.8 | 206000 | 4.06 | 152000 | 2.64 | R-410A | 15.3333
213916730 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE1204AN40AN |  |  | TUHYE2164BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213916722 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE0964AN40AN |  |  | TUHYE1924BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213893652 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE0964AN40AN |  |  | TUHYE1924BN40AN | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893653 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE0964AN40AN |  |  | TUHYE1924BN40AN | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213893655 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE1204AN40AN |  |  | TUHYE2164BN40AN | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213893649 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN40AN |  |  |  | TUHYE1444AN40AN | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213893650 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE0963AN40AN |  |  | TUHYE1923BN40AN | Ducted Indoor Units | 184000 | 11.2 | 22.4 | 206000 | 3.75 | 160000 | 2.12 | R-410A | 15.3333
213893651 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE0963AN40AN |  |  | TUHYE1923BN40AN | Non-Ducted Indoor Units | 184000 | 11.4 | 24.5 | 206000 | 4.11 | 160000 | 2.27 | R-410A | 15.3333
213893654 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE1203AN40AN |  |  | TUHYE2163BN40AN | Non-Ducted Indoor Units | 206000 | 11.1 | 24.8 | 232000 | 4.03 | 196000 | 2.31 | R-410A | 17.1667
213916719 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE0963AN40AN |  |  | TUHYE1923BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.3 | 23.45 | 206000 | 3.93 | 160000 | 2.19 | R-410A | 15.3333
213916726 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE1203AN40AN |  |  | TUHYE2163BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 23 | 232000 | 3.84 | 196000 | 2.21 | R-410A | 17.1667
213893648 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN40AN |  |  |  | TUHYE1443AN40AN | Non-Ducted Indoor Units | 138000 | 10.7 | 23.2 | 152000 | 4.01 | 134000 | 2.61 | R-410A | 11.5
213893694 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN | TUHYH0724AN40AN |  |  | TUHYH1444BN40AN | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893695 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN | TUHYH0724AN40AN |  |  | TUHYH1444BN40AN | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213916786 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0724AN40AN | TUHYH0724AN40AN |  |  | TUHYH1444BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213916789 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN | TUHYH0964AN40AN |  |  | TUHYH1924BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893698 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN | TUHYH0964AN40AN |  |  | TUHYH1924BN40AN | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893699 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0964AN40AN | TUHYH0964AN40AN |  |  | TUHYH1924BN40AN | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213893701 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1204AN40AN | TUHYH1204AN40AN |  |  | TUHYH2404BN40AN | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213916784 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN | TUHYH0723AN40AN |  |  | TUHYH1443BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 21.25 | 152000 | 3.89 | 128000 | 2.23 | R-410A | 11.5
213893692 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN | TUHYH0723AN40AN |  |  | TUHYH1443BN40AN | Ducted Indoor Units | 138000 | 10.8 | 19.4 | 152000 | 3.69 | 128000 | 2.12 | R-410A | 11.5
213893693 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0723AN40AN | TUHYH0723AN40AN |  |  | TUHYH1443BN40AN | Non-Ducted Indoor Units | 138000 | 11.6 | 23.1 | 152000 | 4.1 | 128000 | 2.34 | R-410A | 11.5
213893696 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN40AN | TUHYH0963AN40AN |  |  | TUHYH1923BN40AN | Ducted Indoor Units | 184000 | 11.6 | 19.8 | 206000 | 3.71 | 174000 | 2.22 | R-410A | 15.3333
213893697 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN40AN | TUHYH0963AN40AN |  |  | TUHYH1923BN40AN | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 4.07 | 174000 | 2.4 | R-410A | 15.3333
213916787 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH0963AN40AN | TUHYH0963AN40AN |  |  | TUHYH1923BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.55 | 20.7 | 206000 | 3.89 | 174000 | 2.31 | R-410A | 15.3333
213893700 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYH1203AN40AN | TUHYH1203AN40AN |  |  | TUHYH2403BN40AN | Ducted Indoor Units | 230000 | 10.9 | 19.1 | 258000 | 3.5 | 174000 | 2.19 | R-410A | 19.1667
213896137 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YNU-A | PURY-P96YNU-A |  |  | PURY-P192YSNU-A | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896135 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TNU-A | PURY-P96TNU-A |  |  | PURY-P192TSNU-A | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896213 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0964AN40AN | TURYP0964AN40AN |  |  | TURYP1924BN40AN | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896211 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYP0963AN40AN | TURYP0963AN40AN |  |  | TURYP1923BN40AN | Non-Ducted Indoor Units | 184000 | 10.7 | 21.5 | 204000 | 3.88 | 142000 | 2.16 | R-410A | 15.3333
213896077 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A | PURY-EP96YNU-A |  |  | PURY-EP192YSNU-A | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213895965 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96YNU-A | PURY-EP96YNU-A |  |  | PURY-EP192YSNU-A | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896075 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A | PURY-EP96TNU-A |  |  | PURY-EP192TSNU-A | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213895963 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-EP96TNU-A | PURY-EP96TNU-A |  |  | PURY-EP192TSNU-A | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896165 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN40AN | TURYE0964AN40AN |  |  | TURYE1924BN40AN | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213896029 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0964AN40AN | TURYE0964AN40AN |  |  | TURYE1924BN40AN | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896027 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN40AN | TURYE0963AN40AN |  |  | TURYE1923BN40AN | Ducted Indoor Units | 184000 | 11 | 20.5 | 204000 | 3.66 | 158000 | 2.08 | R-410A | 15.3333
213896163 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYE0963AN40AN | TURYE0963AN40AN |  |  | TURYE1923BN40AN | Non-Ducted Indoor Units | 184000 | 11.3 | 22.4 | 204000 | 3.99 | 158000 | 2.15 | R-410A | 15.3333
213896110 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A | PURY-HP72YNU-A |  |  | PURY-HP144YSNU-A | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213895989 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72YNU-A | PURY-HP72YNU-A |  |  | PURY-HP144YSNU-A | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213895993 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A | PURY-HP96YNU-A |  |  | PURY-HP192YSNU-A | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896120 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96YNU-A | PURY-HP96YNU-A |  |  | PURY-HP192YSNU-A | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
213896107 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A | PURY-HP72TNU-A |  |  | PURY-HP144TSNU-A | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213895987 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP72TNU-A | PURY-HP72TNU-A |  |  | PURY-HP144TSNU-A | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213895991 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A | PURY-HP96TNU-A |  |  | PURY-HP192TSNU-A | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896115 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-HP96TNU-A | PURY-HP96TNU-A |  |  | PURY-HP192TSNU-A | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
213896197 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN40AN | TURYH0724AN40AN |  |  | TURYH1444BN40AN | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213896053 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0724AN40AN | TURYH0724AN40AN |  |  | TURYH1444BN40AN | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213896057 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN40AN | TURYH0964AN40AN |  |  | TURYH1924BN40AN | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896201 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0964AN40AN | TURYH0964AN40AN |  |  | TURYH1924BN40AN | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
213896195 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN40AN | TURYH0723AN40AN |  |  | TURYH1443BN40AN | Non-Ducted Indoor Units | 138000 | 11.5 | 21.6 | 152000 | 3.82 | 128000 | 2.14 | R-410A | 11.5
213896051 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0723AN40AN | TURYH0723AN40AN |  |  | TURYH1443BN40AN | Ducted Indoor Units | 138000 | 10.8 | 19.7 | 152000 | 3.45 | 128000 | 2.08 | R-410A | 11.5
213896055 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN40AN | TURYH0963AN40AN |  |  | TURYH1923BN40AN | Ducted Indoor Units | 184000 | 10.8 | 19.4 | 206000 | 3.6 | 174000 | 2.09 | R-410A | 15.3333
213896199 | 1/1/2027 | Trane / Mitsubishi Electric | HMSR-A-CB | TURYH0963AN40AN | TURYH0963AN40AN |  |  | TURYH1923BN40AN | Non-Ducted Indoor Units | 184000 | 11.2 | 21.4 | 206000 | 3.88 | 174000 | 2.15 | R-410A | 15.3333
205818940 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y | VPB072L4M-3Y |  |  | VPB144L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 22.06 | 154000 | 3.9 | 131000 | 2.54 | R-410A | 11.5
205811882 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X144DXN1C-(A) | Non-Ducted Indoor Units | 138000 | 11.3 | 22.07 | 154000 | 4.04 | 131000 | 2.58 | R-410A | 11.5
205811883 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X144DXN1C-(A) | Ducted Indoor Units | 138000 | 11.1 | 22.05 | 154000 | 3.76 | 131000 | 2.51 | R-410A | 11.5
205811966 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X144DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 22.06 | 154000 | 3.9 | 131000 | 2.54 | R-410A | 11.5
205818856 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y | VPB072L4M-3Y |  |  | VPB144L4M-3Y | Non-Ducted Indoor Units | 138000 | 11.3 | 22.07 | 154000 | 4.04 | 131000 | 2.58 | R-410A | 11.5
205818857 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3Y | VPB072L4M-3Y |  |  | VPB144L4M-3Y | Ducted Indoor Units | 138000 | 11.1 | 22.05 | 154000 | 3.76 | 131000 | 2.51 | R-410A | 11.5
205818858 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G | VPB072L4M-3G |  |  | VPB144L4M-3G | Non-Ducted Indoor Units | 138000 | 11.3 | 22.07 | 154000 | 4.04 | 131000 | 2.58 | R-410A | 11.5
205818859 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G | VPB072L4M-3G |  |  | VPB144L4M-3G | Ducted Indoor Units | 138000 | 11.1 | 22.05 | 154000 | 3.76 | 131000 | 2.51 | R-410A | 11.5
205811967 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X144DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 22.06 | 154000 | 3.9 | 131000 | 2.54 | R-410A | 11.5
205811884 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X144DZN1C-(A) | Non-Ducted Indoor Units | 138000 | 11.3 | 22.07 | 154000 | 4.04 | 131000 | 2.58 | R-410A | 11.5
205811885 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X144DZN1C-(A) | Ducted Indoor Units | 138000 | 11.1 | 22.05 | 154000 | 3.76 | 131000 | 2.51 | R-410A | 11.5
205818941 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB072L4M-3G | VPB072L4M-3G |  |  | VPB144L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.2 | 22.06 | 154000 | 3.9 | 131000 | 2.54 | R-410A | 11.5
205818942 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y | VRB072L4M-3Y |  |  | VRB144L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 21.24 | 154000 | 3.77 | 131000 | 2.46 | R-410A | 11.5
205811886 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R144DXN1C-(A) | Non-Ducted Indoor Units | 138000 | 11.55 | 20.55 | 154000 | 3.91 | 131000 | 2.54 | R-410A | 11.5
205811887 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R144DXN1C-(A) | Ducted Indoor Units | 138000 | 11.35 | 21.93 | 154000 | 3.63 | 131000 | 2.38 | R-410A | 11.5
205811968 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R144DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 21.24 | 154000 | 3.77 | 131000 | 2.46 | R-410A | 11.5
205818860 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y | VRB072L4M-3Y |  |  | VRB144L4M-3Y | Non-Ducted Indoor Units | 138000 | 11.55 | 20.55 | 154000 | 3.91 | 131000 | 2.54 | R-410A | 11.5
205818861 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3Y | VRB072L4M-3Y |  |  | VRB144L4M-3Y | Ducted Indoor Units | 138000 | 11.35 | 21.93 | 154000 | 3.63 | 131000 | 2.38 | R-410A | 11.5
205818862 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G | VRB072L4M-3G |  |  | VRB144L4M-3G | Non-Ducted Indoor Units | 138000 | 11.55 | 20.55 | 154000 | 3.91 | 131000 | 2.54 | R-410A | 11.5
205818863 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G | VRB072L4M-3G |  |  | VRB144L4M-3G | Ducted Indoor Units | 138000 | 11.35 | 21.93 | 154000 | 3.63 | 131000 | 2.38 | R-410A | 11.5
205811969 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R144DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 21.24 | 154000 | 3.77 | 131000 | 2.46 | R-410A | 11.5
205811888 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R144DZN1C-(A) | Non-Ducted Indoor Units | 138000 | 11.55 | 20.55 | 154000 | 3.91 | 131000 | 2.54 | R-410A | 11.5
205811889 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R144DZN1C-(A) | Ducted Indoor Units | 138000 | 11.35 | 21.93 | 154000 | 3.63 | 131000 | 2.38 | R-410A | 11.5
205818943 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB072L4M-3G | VRB072L4M-3G |  |  | VRB144L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.45 | 21.24 | 154000 | 3.77 | 131000 | 2.46 | R-410A | 11.5
205818944 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y | VPB072L4M-3Y |  |  | VPB168L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 21.72 | 180000 | 3.92 | 154000 | 2.58 | R-410A | 13.3333
205811890 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X168DXN1C-(A) | Non-Ducted Indoor Units | 160000 | 11.55 | 21.49 | 180000 | 4.08 | 154000 | 2.63 | R-410A | 13.3333
205811891 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X168DXN1C-(A) | Ducted Indoor Units | 160000 | 11.3 | 21.96 | 180000 | 3.76 | 154000 | 2.54 | R-410A | 13.3333
205811970 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X168DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 21.72 | 180000 | 3.92 | 154000 | 2.58 | R-410A | 13.3333
205818864 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y | VPB072L4M-3Y |  |  | VPB168L4M-3Y | Non-Ducted Indoor Units | 160000 | 11.55 | 21.49 | 180000 | 4.08 | 154000 | 2.63 | R-410A | 13.3333
205818865 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3Y | VPB072L4M-3Y |  |  | VPB168L4M-3Y | Ducted Indoor Units | 160000 | 11.3 | 21.96 | 180000 | 3.76 | 154000 | 2.54 | R-410A | 13.3333
205818866 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G | VPB072L4M-3G |  |  | VPB168L4M-3G | Non-Ducted Indoor Units | 160000 | 11.55 | 21.49 | 180000 | 4.08 | 154000 | 2.63 | R-410A | 13.3333
205818867 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G | VPB072L4M-3G |  |  | VPB168L4M-3G | Ducted Indoor Units | 160000 | 11.3 | 21.96 | 180000 | 3.76 | 154000 | 2.54 | R-410A | 13.3333
205811971 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X168DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 21.72 | 180000 | 3.92 | 154000 | 2.58 | R-410A | 13.3333
205811892 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X168DZN1C-(A) | Non-Ducted Indoor Units | 160000 | 11.55 | 21.49 | 180000 | 4.08 | 154000 | 2.63 | R-410A | 13.3333
205811893 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X168DZN1C-(A) | Ducted Indoor Units | 160000 | 11.3 | 21.96 | 180000 | 3.76 | 154000 | 2.54 | R-410A | 13.3333
205818945 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB096L4M-3G | VPB072L4M-3G |  |  | VPB168L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 21.72 | 180000 | 3.92 | 154000 | 2.58 | R-410A | 13.3333
205818946 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y | VRB072L4M-3Y |  |  | VRB168L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 20.75 | 180000 | 3.84 | 154000 | 2.55 | R-410A | 13.3333
205811894 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R168DXN1C-(A) | Non-Ducted Indoor Units | 160000 | 11.4 | 20.31 | 180000 | 3.98 | 154000 | 2.6 | R-410A | 13.3333
205811895 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R168DXN1C-(A) | Ducted Indoor Units | 160000 | 11.45 | 21.19 | 180000 | 3.7 | 154000 | 2.51 | R-410A | 13.3333
205811972 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R168DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 20.75 | 180000 | 3.84 | 154000 | 2.55 | R-410A | 13.3333
205818868 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y | VRB072L4M-3Y |  |  | VRB168L4M-3Y | Non-Ducted Indoor Units | 160000 | 11.4 | 20.31 | 180000 | 3.98 | 154000 | 2.6 | R-410A | 13.3333
205818869 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3Y | VRB072L4M-3Y |  |  | VRB168L4M-3Y | Ducted Indoor Units | 160000 | 11.45 | 21.19 | 180000 | 3.7 | 154000 | 2.51 | R-410A | 13.3333
205818870 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G | VRB072L4M-3G |  |  | VRB168L4M-3G | Non-Ducted Indoor Units | 160000 | 11.4 | 20.31 | 180000 | 3.98 | 154000 | 2.6 | R-410A | 13.3333
205818871 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G | VRB072L4M-3G |  |  | VRB168L4M-3G | Ducted Indoor Units | 160000 | 11.45 | 21.19 | 180000 | 3.7 | 154000 | 2.51 | R-410A | 13.3333
205811973 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R168DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 20.75 | 180000 | 3.84 | 154000 | 2.55 | R-410A | 13.3333
205811896 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R168DZN1C-(A) | Non-Ducted Indoor Units | 160000 | 11.4 | 20.31 | 180000 | 3.98 | 154000 | 2.6 | R-410A | 13.3333
205811897 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R168DZN1C-(A) | Ducted Indoor Units | 160000 | 11.45 | 21.19 | 180000 | 3.7 | 154000 | 2.51 | R-410A | 13.3333
205818947 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB096L4M-3G | VRB072L4M-3G |  |  | VRB168L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 20.75 | 180000 | 3.84 | 154000 | 2.55 | R-410A | 13.3333
205818948 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y |  |  | VPB192L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 20.93 | 206000 | 3.87 | 176000 | 2.53 | R-410A | 15.3333
205818952 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y |  |  | VPB216L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.6 | 20.71 | 232000 | 3.86 | 198000 | 2.59 | R-410A | 17.1667
205818956 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y |  |  | VPB240L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.33 | 258000 | 3.72 | 218000 | 2.44 | R-410A | 19.1667
205811898 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X192DXN1C-(A) | Non-Ducted Indoor Units | 184000 | 11 | 20.86 | 206000 | 4 | 176000 | 2.62 | R-410A | 15.3333
205811899 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X192DXN1C-(A) | Ducted Indoor Units | 184000 | 10.7 | 21 | 206000 | 3.75 | 176000 | 2.44 | R-410A | 15.3333
205811906 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  |  | MV6-X216DXN1C-(A) | Non-Ducted Indoor Units | 206000 | 11.8 | 20.54 | 232000 | 4 | 198000 | 2.64 | R-410A | 17.1667
205811907 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  |  | MV6-X216DXN1C-(A) | Ducted Indoor Units | 206000 | 11.4 | 20.88 | 232000 | 3.73 | 198000 | 2.54 | R-410A | 17.1667
205811914 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  |  | MV6-X240DXN1C-(A) | Non-Ducted Indoor Units | 230000 | 10.9 | 19.74 | 258000 | 3.75 | 218000 | 2.38 | R-410A | 19.1667
205811915 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  |  | MV6-X240DXN1C-(A) | Ducted Indoor Units | 230000 | 10.95 | 20.93 | 258000 | 3.7 | 218000 | 2.5 | R-410A | 19.1667
205811974 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  |  | MV6-X192DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 20.93 | 206000 | 3.87 | 176000 | 2.53 | R-410A | 15.3333
205811978 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  |  | MV6-X216DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.6 | 20.71 | 232000 | 3.86 | 198000 | 2.59 | R-410A | 17.1667
205811982 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  |  | MV6-X240DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.33 | 258000 | 3.72 | 218000 | 2.44 | R-410A | 19.1667
205818872 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y |  |  | VPB192L4M-3Y | Non-Ducted Indoor Units | 184000 | 11 | 20.86 | 206000 | 4 | 176000 | 2.62 | R-410A | 15.3333
205818873 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y |  |  | VPB192L4M-3Y | Ducted Indoor Units | 184000 | 10.7 | 21 | 206000 | 3.75 | 176000 | 2.44 | R-410A | 15.3333
205818880 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y |  |  | VPB216L4M-3Y | Non-Ducted Indoor Units | 206000 | 11.8 | 20.54 | 232000 | 4 | 198000 | 2.64 | R-410A | 17.1667
205818881 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y |  |  | VPB216L4M-3Y | Ducted Indoor Units | 206000 | 11.4 | 20.88 | 232000 | 3.73 | 198000 | 2.54 | R-410A | 17.1667
205818888 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y |  |  | VPB240L4M-3Y | Non-Ducted Indoor Units | 230000 | 10.9 | 19.74 | 258000 | 3.75 | 218000 | 2.38 | R-410A | 19.1667
205818889 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y |  |  | VPB240L4M-3Y | Ducted Indoor Units | 230000 | 10.95 | 20.93 | 258000 | 3.7 | 218000 | 2.5 | R-410A | 19.1667
205818890 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G |  |  | VPB240L4M-3G | Non-Ducted Indoor Units | 230000 | 10.9 | 19.74 | 258000 | 3.75 | 218000 | 2.38 | R-410A | 19.1667
205818891 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G |  |  | VPB240L4M-3G | Ducted Indoor Units | 230000 | 10.95 | 20.93 | 258000 | 3.7 | 218000 | 2.5 | R-410A | 19.1667
205818882 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G |  |  | VPB216L4M-3G | Non-Ducted Indoor Units | 206000 | 11.8 | 20.54 | 232000 | 4 | 198000 | 2.64 | R-410A | 17.1667
205818883 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G |  |  | VPB216L4M-3G | Ducted Indoor Units | 206000 | 11.4 | 20.88 | 232000 | 3.73 | 198000 | 2.54 | R-410A | 17.1667
205818874 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G |  |  | VPB192L4M-3G | Non-Ducted Indoor Units | 184000 | 11 | 20.86 | 206000 | 4 | 176000 | 2.62 | R-410A | 15.3333
205818875 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G |  |  | VPB192L4M-3G | Ducted Indoor Units | 184000 | 10.7 | 21 | 206000 | 3.75 | 176000 | 2.44 | R-410A | 15.3333
205811983 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  |  | MV6-X240DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.33 | 258000 | 3.72 | 218000 | 2.44 | R-410A | 19.1667
205811979 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  |  | MV6-X216DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.6 | 20.71 | 232000 | 3.86 | 198000 | 2.59 | R-410A | 17.1667
205811975 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X192DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 20.93 | 206000 | 3.87 | 176000 | 2.53 | R-410A | 15.3333
205811916 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  |  | MV6-X240DZN1C-(A) | Non-Ducted Indoor Units | 230000 | 10.9 | 19.74 | 258000 | 3.75 | 218000 | 2.38 | R-410A | 19.1667
205811917 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  |  | MV6-X240DZN1C-(A) | Ducted Indoor Units | 230000 | 10.95 | 20.93 | 258000 | 3.7 | 218000 | 2.5 | R-410A | 19.1667
205811908 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  |  | MV6-X216DZN1C-(A) | Non-Ducted Indoor Units | 206000 | 11.8 | 20.54 | 232000 | 4 | 198000 | 2.64 | R-410A | 17.1667
205811909 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  |  | MV6-X216DZN1C-(A) | Ducted Indoor Units | 206000 | 11.4 | 20.88 | 232000 | 3.73 | 198000 | 2.54 | R-410A | 17.1667
205811900 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X192DZN1C-(A) | Non-Ducted Indoor Units | 184000 | 11 | 20.86 | 206000 | 4 | 176000 | 2.62 | R-410A | 15.3333
205811901 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  |  | MV6-X192DZN1C-(A) | Ducted Indoor Units | 184000 | 10.7 | 21 | 206000 | 3.75 | 176000 | 2.44 | R-410A | 15.3333
205818957 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G |  |  | VPB240L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 20.33 | 258000 | 3.72 | 218000 | 2.44 | R-410A | 19.1667
205818953 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G |  |  | VPB216L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.6 | 20.71 | 232000 | 3.86 | 198000 | 2.59 | R-410A | 17.1667
205818949 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G |  |  | VPB192L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 20.93 | 206000 | 3.87 | 176000 | 2.53 | R-410A | 15.3333
205818950 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y |  |  | VRB192L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 19.89 | 206000 | 3.78 | 176000 | 2.51 | R-410A | 15.3333
205818954 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y |  |  | VRB216L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.34 | 232000 | 3.78 | 198000 | 2.55 | R-410A | 17.1667
205818958 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y |  |  | VRB240L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 20.22 | 258000 | 3.68 | 218000 | 2.43 | R-410A | 19.1667
205811902 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R192DXN1C-(A) | Non-Ducted Indoor Units | 184000 | 11.05 | 19.63 | 206000 | 3.92 | 176000 | 2.59 | R-410A | 15.3333
205811903 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R192DXN1C-(A) | Ducted Indoor Units | 184000 | 11 | 20.15 | 206000 | 3.65 | 176000 | 2.44 | R-410A | 15.3333
205811910 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  |  | MV6-R216DXN1C-(A) | Non-Ducted Indoor Units | 206000 | 11.75 | 20.23 | 232000 | 3.91 | 198000 | 2.61 | R-410A | 17.1667
205811911 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  |  | MV6-R216DXN1C-(A) | Ducted Indoor Units | 206000 | 11.55 | 20.46 | 232000 | 3.66 | 198000 | 2.49 | R-410A | 17.1667
205811918 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  |  | MV6-R240DXN1C-(A) | Non-Ducted Indoor Units | 230000 | 10.9 | 19.63 | 258000 | 3.74 | 218000 | 2.4 | R-410A | 19.1667
205811919 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  |  | MV6-R240DXN1C-(A) | Ducted Indoor Units | 230000 | 11.1 | 20.81 | 258000 | 3.63 | 218000 | 2.46 | R-410A | 19.1667
205811976 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  |  | MV6-R192DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 19.89 | 206000 | 3.78 | 176000 | 2.51 | R-410A | 15.3333
205811980 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  |  | MV6-R216DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.34 | 232000 | 3.78 | 198000 | 2.55 | R-410A | 17.1667
205811984 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  |  | MV6-R240DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 20.22 | 258000 | 3.68 | 218000 | 2.43 | R-410A | 19.1667
205818876 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y |  |  | VRB192L4M-3Y | Non-Ducted Indoor Units | 184000 | 11.05 | 19.63 | 206000 | 3.92 | 176000 | 2.59 | R-410A | 15.3333
205818877 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y |  |  | VRB192L4M-3Y | Ducted Indoor Units | 184000 | 11 | 20.15 | 206000 | 3.65 | 176000 | 2.44 | R-410A | 15.3333
205818884 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y |  |  | VRB216L4M-3Y | Non-Ducted Indoor Units | 206000 | 11.75 | 20.23 | 232000 | 3.91 | 198000 | 2.61 | R-410A | 17.1667
205818885 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y |  |  | VRB216L4M-3Y | Ducted Indoor Units | 206000 | 11.55 | 20.46 | 232000 | 3.66 | 198000 | 2.49 | R-410A | 17.1667
205818892 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y |  |  | VRB240L4M-3Y | Non-Ducted Indoor Units | 230000 | 10.9 | 19.63 | 258000 | 3.74 | 218000 | 2.4 | R-410A | 19.1667
205818893 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y |  |  | VRB240L4M-3Y | Ducted Indoor Units | 230000 | 11.1 | 20.81 | 258000 | 3.63 | 218000 | 2.46 | R-410A | 19.1667
205818894 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G |  |  | VRB240L4M-3G | Non-Ducted Indoor Units | 230000 | 10.9 | 19.63 | 258000 | 3.74 | 218000 | 2.4 | R-410A | 19.1667
205818895 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G |  |  | VRB240L4M-3G | Ducted Indoor Units | 230000 | 11.1 | 20.81 | 258000 | 3.63 | 218000 | 2.46 | R-410A | 19.1667
205818886 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G |  |  | VRB216L4M-3G | Non-Ducted Indoor Units | 206000 | 11.75 | 20.23 | 232000 | 3.91 | 198000 | 2.61 | R-410A | 17.1667
205818887 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G |  |  | VRB216L4M-3G | Ducted Indoor Units | 206000 | 11.55 | 20.46 | 232000 | 3.66 | 198000 | 2.49 | R-410A | 17.1667
205818878 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G |  |  | VRB192L4M-3G | Non-Ducted Indoor Units | 184000 | 11.05 | 19.63 | 206000 | 3.92 | 176000 | 2.59 | R-410A | 15.3333
205818879 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G |  |  | VRB192L4M-3G | Ducted Indoor Units | 184000 | 11 | 20.15 | 206000 | 3.65 | 176000 | 2.44 | R-410A | 15.3333
205811985 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  |  | MV6-R240DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 20.22 | 258000 | 3.68 | 218000 | 2.43 | R-410A | 19.1667
205811981 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  |  | MV6-R216DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.34 | 232000 | 3.78 | 198000 | 2.55 | R-410A | 17.1667
205811977 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R192DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 19.89 | 206000 | 3.78 | 176000 | 2.51 | R-410A | 15.3333
205811920 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  |  | MV6-R240DZN1C-(A) | Non-Ducted Indoor Units | 230000 | 10.9 | 19.63 | 258000 | 3.74 | 218000 | 2.4 | R-410A | 19.1667
205811921 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  |  | MV6-R240DZN1C-(A) | Ducted Indoor Units | 230000 | 11.1 | 20.81 | 258000 | 3.63 | 218000 | 2.46 | R-410A | 19.1667
205811912 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  |  | MV6-R216DZN1C-(A) | Non-Ducted Indoor Units | 206000 | 11.75 | 20.23 | 232000 | 3.91 | 198000 | 2.61 | R-410A | 17.1667
205811913 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  |  | MV6-R216DZN1C-(A) | Ducted Indoor Units | 206000 | 11.55 | 20.46 | 232000 | 3.66 | 198000 | 2.49 | R-410A | 17.1667
205811904 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R192DZN1C-(A) | Non-Ducted Indoor Units | 184000 | 11.05 | 19.63 | 206000 | 3.92 | 176000 | 2.59 | R-410A | 15.3333
205811905 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  |  | MV6-R192DZN1C-(A) | Ducted Indoor Units | 184000 | 11 | 20.15 | 206000 | 3.65 | 176000 | 2.44 | R-410A | 15.3333
205818959 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G |  |  | VRB240L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 20.22 | 258000 | 3.68 | 218000 | 2.43 | R-410A | 19.1667
205818955 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G |  |  | VRB216L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.34 | 232000 | 3.78 | 198000 | 2.55 | R-410A | 17.1667
205818951 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G |  |  | VRB192L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11 | 19.89 | 206000 | 3.78 | 176000 | 2.51 | R-410A | 15.3333
213896319 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A |  |  | PUHY-P168ZSKMU-A | Ducted Indoor Units | 160000 | 11.3 | 19.2 | 178000 | 3.54 | 132000 | 2.6 | R-410A | 13.3333
213896321 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A |  |  | PUHY-P192ZSKMU-A | Ducted Indoor Units | 184000 | 11 | 18.7 | 204000 | 3.48 | 150000 | 2.45 | R-410A | 15.3333
213896358 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A |  |  | PUHY-P168ZSKMU-A | Non-Ducted Indoor Units | 160000 | 11.4 | 20.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
213916468 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A |  |  | PUHY-P168ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.35 | 19.95 | 178000 | 3.68 | 132000 | 2.39 | R-410A | 13.3333
213916469 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A |  |  | PUHY-P192ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.8 | 18.25 | 204000 | 3.58 | 150000 | 2.31 | R-410A | 15.3333
213916470 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A |  |  | PUHY-P216ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 18.8 | 232000 | 3.53 | 164000 | 2.28 | R-410A | 17.1667
213896323 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A |  |  | PUHY-P216ZSKMU-A | Ducted Indoor Units | 206000 | 10.8 | 19.8 | 232000 | 3.51 | 164000 | 2.48 | R-410A | 17.1667
8175950 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YLMU-A |  |  |  | PUHY-P144YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.25 | 22.95 | 152000 | 3.71 | 109000 | 2.21 | R-410A | 11.3333
8175951 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P144YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.6 | 23.65 | 152000 | 3.85 | 109000 | 2.28 | R-410A | 11.3333
8175952 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P168YLMU-A |  |  |  | PUHY-P168YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.05 | 20.45 | 178000 | 3.62 | 132000 | 2.33 | R-410A | 13.3333
8175953 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P168YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 13 | 23 | 178000 | 3.7 | 132000 | 2.33 | R-410A | 13.3333
8175954 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P192YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.95 | 22.8 | 204000 | 3.65 | 150000 | 2.25 | R-410A | 15.1667
8175955 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  |  | PUHY-P216YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.7 | 22.75 | 232000 | 3.6 | 164000 | 2.22 | R-410A | 17.1667
8175956 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A |  |  | PUHY-P240YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.6 | 22.15 | 258000 | 3.59 | 182000 | 2.17 | R-410A | 19
8175965 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TLMU-A |  |  |  | PUHY-P144TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.25 | 22.95 | 152000 | 3.71 | 109000 | 2.21 | R-410A | 11.3333
8175966 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P144TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.6 | 23.65 | 152000 | 3.85 | 109000 | 2.28 | R-410A | 11.3333
8175967 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P168TLMU-A |  |  |  | PUHY-P168TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.05 | 20.45 | 178000 | 3.62 | 132000 | 2.33 | R-410A | 13.3333
8175968 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P168TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 13 | 23 | 178000 | 3.7 | 132000 | 2.33 | R-410A | 13.3333
8175969 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P192TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.95 | 22.8 | 204000 | 3.65 | 150000 | 2.25 | R-410A | 15.1667
8175970 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  |  | PUHY-P216TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.7 | 22.75 | 232000 | 3.6 | 164000 | 2.22 | R-410A | 17.1667
8175971 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A |  |  | PUHY-P240TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.6 | 22.15 | 258000 | 3.59 | 182000 | 2.17 | R-410A | 19
8175980 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YLMU-A |  |  |  | PURY-P144YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.1 | 21.75 | 152000 | 3.53 | 97000 | 2.11 | R-410A | 11.3333
8175981 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YLMU-A | PURY-P72YLMU-A |  |  | PURY-P144YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.25 | 23.9 | 152000 | 3.8 | 97000 | 2.18 | R-410A | 11.3333
8175983 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A | PURY-P72YLMU-A |  |  | PURY-P168YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.8 | 22.35 | 178000 | 3.56 | 119000 | 2.28 | R-410A | 13.3333
8175984 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A | PURY-P96YLMU-A |  |  | PURY-P192YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 23.7 | 204000 | 3.55 | 142000 | 2.18 | R-410A | 15.1667
8175985 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A | PURY-P96YLMU-A |  |  | PURY-P216YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.2 | 232000 | 3.54 | 158000 | 2.14 | R-410A | 17.1667
8175986 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A | PURY-P120YLMU-A |  |  | PURY-P240YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.35 | 20.65 | 258000 | 3.53 | 174000 | 2.1 | R-410A | 19
8175994 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TLMU-A |  |  |  | PURY-P144TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.1 | 22 | 152000 | 3.53 | 97000 | 2.11 | R-410A | 11.3333
8175995 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TLMU-A | PURY-P72TLMU-A |  |  | PURY-P144TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.25 | 23.9 | 152000 | 3.8 | 97000 | 2.18 | R-410A | 11.3333
8175997 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A | PURY-P72TLMU-A |  |  | PURY-P168TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.8 | 22.35 | 178000 | 3.56 | 119000 | 2.28 | R-410A | 13.3333
8175998 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A | PURY-P96TLMU-A |  |  | PURY-P192TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 23.7 | 204000 | 3.55 | 142000 | 2.18 | R-410A | 15.1667
8175999 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A | PURY-P96TLMU-A |  |  | PURY-P216TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.2 | 232000 | 3.54 | 158000 | 2.14 | R-410A | 17.1667
8176000 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A | PURY-P120TLMU-A |  |  | PURY-P240TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.35 | 20.65 | 258000 | 3.53 | 174000 | 2.1 | R-410A | 19
8578648 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R144DZN1-(A) |  |  |  | MV5-R144DZN1-(A) | Non-Ducted Indoor Units | 136000 | 11 | 19.5 | 150000 | 3.4 | 102000 | 2.25 | R-410A | 11.3333
9133171 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R145DXN1 |  |  |  | MV5-2R145DXN1 | Non-Ducted Indoor Units | 136000 | 13 | 24.4 | 150000 | 3.98 | 108000 | 2.5 | R-410A | 11.3333
9133172 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R145DXN1 |  |  |  | MV5-2R145DXN1 | Ducted Indoor Units | 136000 | 12.3 | 24 | 150000 | 3.6 | 108000 | 2.42 | R-410A | 11.3333
9133173 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R168DXN1 |  |  |  | MV5-2R168DXN1 | Non-Ducted Indoor Units | 158000 | 11.8 | 23.1 | 180000 | 3.59 | 130000 | 2.35 | R-410A | 13.1667
9133174 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R168DXN1 |  |  |  | MV5-2R168DXN1 | Ducted Indoor Units | 158000 | 11.5 | 22.9 | 180000 | 3.54 | 130000 | 2.35 | R-410A | 13.1667
9133175 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R192DXN1 |  |  |  | MV5-2R192DXN1 | Non-Ducted Indoor Units | 182000 | 11.3 | 23.9 | 204000 | 3.38 | 144000 | 2.3 | R-410A | 15.1667
9133176 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R192DXN1 |  |  |  | MV5-2R192DXN1 | Ducted Indoor Units | 182000 | 11.1 | 23.6 | 204000 | 3.33 | 144000 | 2.3 | R-410A | 15.1667
9133177 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R216DXN1 |  |  |  | MV5-2R216DXN1 | Non-Ducted Indoor Units | 204000 | 11.2 | 23 | 222000 | 3.34 | 152000 | 2.3 | R-410A | 17
9133178 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R216DXN1 |  |  |  | MV5-2R216DXN1 | Ducted Indoor Units | 204000 | 11 | 21.7 | 222000 | 3.29 | 152000 | 2.3 | R-410A | 17
9133187 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R145DZN1 |  |  |  | MV5-2R145DZN1 | Non-Ducted Indoor Units | 136000 | 13 | 24.4 | 150000 | 3.98 | 108000 | 2.5 | R-410A | 11.3333
9133188 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R145DZN1 |  |  |  | MV5-2R145DZN1 | Ducted Indoor Units | 136000 | 12.3 | 24 | 150000 | 3.6 | 108000 | 2.42 | R-410A | 11.3333
9133189 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R168DZN1 |  |  |  | MV5-2R168DZN1 | Non-Ducted Indoor Units | 158000 | 11.8 | 23.1 | 180000 | 3.59 | 130000 | 2.35 | R-410A | 13.1667
9133190 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R168DZN1 |  |  |  | MV5-2R168DZN1 | Ducted Indoor Units | 158000 | 11.5 | 22.9 | 180000 | 3.54 | 130000 | 2.35 | R-410A | 13.1667
9133191 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R192DZN1 |  |  |  | MV5-2R192DZN1 | Non-Ducted Indoor Units | 182000 | 11.3 | 23.9 | 204000 | 3.38 | 144000 | 2.3 | R-410A | 15.1667
9133192 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R192DZN1 |  |  |  | MV5-2R192DZN1 | Ducted Indoor Units | 182000 | 11.1 | 23.6 | 204000 | 3.33 | 144000 | 2.3 | R-410A | 15.1667
9133193 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R216DZN1 |  |  |  | MV5-2R216DZN1 | Non-Ducted Indoor Units | 204000 | 11.2 | 23 | 222000 | 3.34 | 152000 | 2.3 | R-410A | 17
9133194 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R216DZN1 |  |  |  | MV5-2R216DZN1 | Ducted Indoor Units | 204000 | 11 | 21.7 | 222000 | 3.29 | 152000 | 2.3 | R-410A | 17
9133200 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R145DXN1 |  |  |  | MV5-2R145DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.65 | 24.2 | 150000 | 3.79 | 108000 | 2.46 | R-410A | 11.3333
9133201 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R168DXN1 |  |  |  | MV5-2R168DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 158000 | 11.65 | 23 | 180000 | 3.56 | 130000 | 2.35 | R-410A | 13.1667
9133202 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R192DXN1 |  |  |  | MV5-2R192DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 23.75 | 204000 | 3.35 | 144000 | 2.3 | R-410A | 15.1667
9133203 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R216DXN1 |  |  |  | MV5-2R216DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 204000 | 11.1 | 22.35 | 222000 | 3.31 | 152000 | 2.3 | R-410A | 17
9133208 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R145DZN1 |  |  |  | MV5-2R145DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.65 | 24.2 | 150000 | 3.79 | 108000 | 2.46 | R-410A | 11.3333
9133209 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R168DZN1 |  |  |  | MV5-2R168DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 158000 | 11.65 | 23 | 180000 | 3.56 | 130000 | 2.35 | R-410A | 13.1667
9133210 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R192DZN1 |  |  |  | MV5-2R192DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 23.75 | 204000 | 3.35 | 144000 | 2.3 | R-410A | 15.1667
9133211 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R216DZN1 |  |  |  | MV5-2R216DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 204000 | 11.1 | 22.35 | 222000 | 3.31 | 152000 | 2.3 | R-410A | 17
9487697 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA144RDL5-1 |  |  |  | 38VMA144RDL5-1 | Ducted Indoor Units | 136000 | 12.3 | 24 | 150000 | 3.6 | 108000 | 2.42 | R-410A | 11.3333
9487698 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA144RDL5-1 |  |  |  | 38VMA144RDL5-1 | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.65 | 24.2 | 150000 | 3.79 | 108000 | 2.46 | R-410A | 11.3333
9487699 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA144RDL5-1 |  |  |  | 38VMA144RDL5-1 | Non-Ducted Indoor Units | 136000 | 13 | 24.4 | 150000 | 3.98 | 108000 | 2.5 | R-410A | 11.3333
9487701 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA144RDL6-1 |  |  |  | 38VMA144RDL6-1 | Ducted Indoor Units | 136000 | 12.3 | 24 | 150000 | 3.6 | 108000 | 2.42 | R-410A | 11.3333
9487702 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA144RDL6-1 |  |  |  | 38VMA144RDL6-1 | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.65 | 24.2 | 150000 | 3.79 | 108000 | 2.46 | R-410A | 11.3333
9487703 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA144RDL6-1 |  |  |  | 38VMA144RDL6-1 | Non-Ducted Indoor Units | 136000 | 13 | 24.4 | 150000 | 3.98 | 108000 | 2.5 | R-410A | 11.3333
9487704 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA168RDS5-1 |  |  |  | 38VMA168RDS5-1 | Ducted Indoor Units | 158000 | 11.5 | 22.9 | 180000 | 3.54 | 130000 | 2.35 | R-410A | 13.1667
9487705 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA168RDS5-1 |  |  |  | 38VMA168RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 158000 | 11.65 | 23 | 180000 | 3.56 | 130000 | 2.35 | R-410A | 13.1667
9487706 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA168RDS5-1 |  |  |  | 38VMA168RDS5-1 | Non-Ducted Indoor Units | 158000 | 11.8 | 23.1 | 180000 | 3.59 | 130000 | 2.35 | R-410A | 13.1667
9487707 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA168RDS6-1 |  |  |  | 38VMA168RDS6-1 | Ducted Indoor Units | 158000 | 11.5 | 22.9 | 180000 | 3.54 | 130000 | 2.35 | R-410A | 13.1667
9487708 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA168RDS6-1 |  |  |  | 38VMA168RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 158000 | 11.65 | 23 | 180000 | 3.56 | 130000 | 2.35 | R-410A | 13.1667
9487710 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA168RDS6-1 |  |  |  | 38VMA168RDS6-1 | Non-Ducted Indoor Units | 158000 | 11.8 | 23.1 | 180000 | 3.59 | 130000 | 2.35 | R-410A | 13.1667
9487711 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA192RDS5-1 |  |  |  | 38VMA192RDS5-1 | Ducted Indoor Units | 182000 | 11.1 | 23.6 | 204000 | 3.33 | 144000 | 2.3 | R-410A | 15.1667
9487712 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA192RDS5-1 |  |  |  | 38VMA192RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 23.75 | 204000 | 3.35 | 144000 | 2.3 | R-410A | 15.1667
9487713 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA192RDS5-1 |  |  |  | 38VMA192RDS5-1 | Non-Ducted Indoor Units | 182000 | 11.3 | 23.9 | 204000 | 3.38 | 144000 | 2.3 | R-410A | 15.1667
9487714 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA192RDS6-1 |  |  |  | 38VMA192RDS6-1 | Ducted Indoor Units | 182000 | 11.1 | 23.6 | 204000 | 3.33 | 144000 | 2.3 | R-410A | 15.1667
9487715 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA192RDS6-1 |  |  |  | 38VMA192RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 23.75 | 204000 | 3.35 | 144000 | 2.3 | R-410A | 15.1667
9487716 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA192RDS6-1 |  |  |  | 38VMA192RDS6-1 | Non-Ducted Indoor Units | 182000 | 11.3 | 23.9 | 204000 | 3.38 | 144000 | 2.3 | R-410A | 15.1667
9487717 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA216RDS5-1 |  |  |  | 38VMA216RDS5-1 | Ducted Indoor Units | 204000 | 11 | 21.7 | 222000 | 3.29 | 152000 | 2.3 | R-410A | 17
9487719 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA216RDS5-1 |  |  |  | 38VMA216RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 204000 | 11.1 | 22.35 | 222000 | 3.31 | 152000 | 2.3 | R-410A | 17
9487720 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA216RDS5-1 |  |  |  | 38VMA216RDS5-1 | Non-Ducted Indoor Units | 204000 | 11.2 | 23 | 222000 | 3.34 | 152000 | 2.3 | R-410A | 17
9487721 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA216RDS6-1 |  |  |  | 38VMA216RDS6-1 | Ducted Indoor Units | 204000 | 11 | 21.7 | 222000 | 3.29 | 152000 | 2.3 | R-410A | 17
9487722 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA216RDS6-1 |  |  |  | 38VMA216RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 204000 | 11.1 | 22.35 | 222000 | 3.31 | 152000 | 2.3 | R-410A | 17
9487723 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA216RDS6-1 |  |  |  | 38VMA216RDS6-1 | Non-Ducted Indoor Units | 204000 | 11.2 | 23 | 222000 | 3.34 | 152000 | 2.3 | R-410A | 17
9487752 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA144RDL5-1 |  |  |  | 38VMA144RDL5-1 | Ducted Indoor Units | 136000 | 12.3 | 24 | 150000 | 3.6 | 108000 | 2.42 | R-410A | 11.3333
9487753 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA144RDL5-1 |  |  |  | 38VMA144RDL5-1 | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.65 | 24.2 | 150000 | 3.79 | 108000 | 2.46 | R-410A | 11.3333
9487754 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA144RDL5-1 |  |  |  | 38VMA144RDL5-1 | Non-Ducted Indoor Units | 136000 | 13 | 24.4 | 150000 | 3.98 | 108000 | 2.5 | R-410A | 11.3333
9487755 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA144RDL6-1 |  |  |  | 38VMA144RDL6-1 | Ducted Indoor Units | 136000 | 12.3 | 24 | 150000 | 3.6 | 108000 | 2.42 | R-410A | 11.3333
9487756 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA144RDL6-1 |  |  |  | 38VMA144RDL6-1 | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.65 | 24.2 | 150000 | 3.79 | 108000 | 2.46 | R-410A | 11.3333
9487757 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA144RDL6-1 |  |  |  | 38VMA144RDL6-1 | Non-Ducted Indoor Units | 136000 | 13 | 24.4 | 150000 | 3.98 | 108000 | 2.5 | R-410A | 11.3333
9487758 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA168RDS5-1 |  |  |  | 38VMA168RDS5-1 | Ducted Indoor Units | 158000 | 11.5 | 22.9 | 180000 | 3.54 | 130000 | 2.35 | R-410A | 13.1667
9487759 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA168RDS5-1 |  |  |  | 38VMA168RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 158000 | 11.65 | 23 | 180000 | 3.56 | 130000 | 2.35 | R-410A | 13.1667
9487760 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA168RDS5-1 |  |  |  | 38VMA168RDS5-1 | Non-Ducted Indoor Units | 158000 | 11.8 | 23.1 | 180000 | 3.59 | 130000 | 2.35 | R-410A | 13.1667
9487762 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA168RDS6-1 |  |  |  | 38VMA168RDS6-1 | Ducted Indoor Units | 158000 | 11.5 | 22.9 | 180000 | 3.54 | 130000 | 2.35 | R-410A | 13.1667
9487763 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA168RDS6-1 |  |  |  | 38VMA168RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 158000 | 11.65 | 23 | 180000 | 3.56 | 130000 | 2.35 | R-410A | 13.1667
9487764 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA168RDS6-1 |  |  |  | 38VMA168RDS6-1 | Non-Ducted Indoor Units | 158000 | 11.8 | 23.1 | 180000 | 3.59 | 130000 | 2.35 | R-410A | 13.1667
9487765 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA192RDS5-1 |  |  |  | 38VMA192RDS5-1 | Ducted Indoor Units | 182000 | 11.1 | 23.6 | 204000 | 3.33 | 144000 | 2.3 | R-410A | 15.1667
9487766 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA192RDS5-1 |  |  |  | 38VMA192RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 23.75 | 204000 | 3.35 | 144000 | 2.3 | R-410A | 15.1667
9487767 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA192RDS5-1 |  |  |  | 38VMA192RDS5-1 | Non-Ducted Indoor Units | 182000 | 11.3 | 23.9 | 204000 | 3.38 | 144000 | 2.3 | R-410A | 15.1667
9487768 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA192RDS6-1 |  |  |  | 38VMA192RDS6-1 | Ducted Indoor Units | 182000 | 11.1 | 23.6 | 204000 | 3.33 | 144000 | 2.3 | R-410A | 15.1667
9487769 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA192RDS6-1 |  |  |  | 38VMA192RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 23.75 | 204000 | 3.35 | 144000 | 2.3 | R-410A | 15.1667
9487771 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA192RDS6-1 |  |  |  | 38VMA192RDS6-1 | Non-Ducted Indoor Units | 182000 | 11.3 | 23.9 | 204000 | 3.38 | 144000 | 2.3 | R-410A | 15.1667
9487772 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA216RDS5-1 |  |  |  | 38VMA216RDS5-1 | Ducted Indoor Units | 204000 | 11 | 21.7 | 222000 | 3.29 | 152000 | 2.3 | R-410A | 17
9487773 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA216RDS5-1 |  |  |  | 38VMA216RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 204000 | 11.1 | 22.35 | 222000 | 3.31 | 152000 | 2.3 | R-410A | 17
9487774 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA216RDS5-1 |  |  |  | 38VMA216RDS5-1 | Non-Ducted Indoor Units | 204000 | 11.2 | 23 | 222000 | 3.34 | 152000 | 2.3 | R-410A | 17
9487775 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA216RDS6-1 |  |  |  | 38VMA216RDS6-1 | Ducted Indoor Units | 204000 | 11 | 21.7 | 222000 | 3.29 | 152000 | 2.3 | R-410A | 17
9487776 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA216RDS6-1 |  |  |  | 38VMA216RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 204000 | 11.1 | 22.35 | 222000 | 3.31 | 152000 | 2.3 | R-410A | 17
9487777 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA216RDS6-1 |  |  |  | 38VMA216RDS6-1 | Non-Ducted Indoor Units | 204000 | 11.2 | 23 | 222000 | 3.34 | 152000 | 2.3 | R-410A | 17
10091387 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DXN1 |  |  |  | MV5-2R241DXN1 | Non-Ducted Indoor Units | 228000 | 11.2 | 22.4 | 256000 | 3.71 | 172000 | 2.48 | R-410A | 19
10091388 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DXN1 |  |  |  | MV5-2R241DXN1 | Ducted Indoor Units | 228000 | 11 | 21.1 | 256000 | 3.57 | 172000 | 2.39 | R-410A | 19
200084125 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 228000 | 11.2 | 22.4 | 256000 | 3.71 | 172000 | 2.48 | R-410A | 19
200084126 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Non-Ducted Indoor Units | 228000 | 11.2 | 22.4 | 256000 | 3.71 | 172000 | 2.48 | R-410A | 19
200084127 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Ducted Indoor Units | 228000 | 11 | 21.1 | 256000 | 3.57 | 172000 | 2.39 | R-410A | 19
200084128 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Ducted Indoor Units | 228000 | 11 | 21.1 | 256000 | 3.57 | 172000 | 2.39 | R-410A | 19
208480482 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XATJ* |  |  |  | REYQ168XATJ* | Non-Ducted Indoor Units | 156000 | 10.8 | 22.3 | 174000 | 3.55 | 122000 | 2.08 | R-410A | 13
208480483 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYD* |  |  |  | REYQ168XAYD* | Non-Ducted Indoor Units | 156000 | 10.8 | 22.3 | 174000 | 3.55 | 122000 | 2.08 | R-410A | 13
208480484 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYC* |  |  |  | REYQ168XAYC* | Non-Ducted Indoor Units | 156000 | 10.8 | 22.3 | 174000 | 3.55 | 122000 | 2.08 | R-410A | 13
208685681 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFH | AVWT-120FFFH |  |  | AVWT-216FFFH | Ducted Indoor Units | 206000 | 11.1 | 20.7 | 226000 | 3.4 | 150000 | 2.32 | R-410A | 17.1667
208685682 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFH | AVWT-120FFFH |  |  | AVWT-216FFFH | Non-Ducted Indoor Units | 206000 | 12.4 | 23.2 | 226000 | 3.88 | 150000 | 2.52 | R-410A | 17.1667
208685683 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFH | AVWT-120FFFH |  |  | AVWT-216FFFH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.75 | 21.95 | 226000 | 3.64 | 150000 | 2.42 | R-410A | 17.1667
208685684 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-120FFFH |  |  | AVWT-240FFFH | Non-Ducted Indoor Units | 228000 | 12.4 | 22.8 | 252000 | 3.8 | 162000 | 2.59 | R-410A | 19
208685712 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-120FFFH |  |  | AVWT-240FFFH | Ducted Indoor Units | 228000 | 11.1 | 20.4 | 252000 | 3.35 | 162000 | 2.32 | R-410A | 19
208685713 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-120FFFH |  |  | AVWT-240FFFH | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 21.6 | 252000 | 3.57 | 162000 | 2.45 | R-410A | 19
208758282 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB | CHV6-120URB |  |  | CHV6-216URB | Ducted Indoor Units | 206000 | 11.1 | 20.7 | 226000 | 3.4 | 150000 | 2.32 | R-410A | 17.1667
208758283 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB | CHV6-120URB |  |  | CHV6-216URB | Non-Ducted Indoor Units | 206000 | 12.4 | 23.2 | 226000 | 3.88 | 150000 | 2.52 | R-410A | 17.1667
208758284 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-096URB | CHV6-120URB |  |  | CHV6-216URB | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.75 | 21.95 | 226000 | 3.64 | 150000 | 2.42 | R-410A | 17.1667
208758285 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-120URB |  |  | CHV6-240URB | Ducted Indoor Units | 228000 | 11.1 | 20.4 | 252000 | 3.35 | 162000 | 2.32 | R-410A | 19
208758286 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-120URB |  |  | CHV6-240URB | Non-Ducted Indoor Units | 228000 | 12.4 | 22.8 | 252000 | 3.8 | 162000 | 2.59 | R-410A | 19
208758287 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-120URB |  |  | CHV6-240URB | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 21.6 | 252000 | 3.57 | 162000 | 2.45 | R-410A | 19
209842189 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR |  |  | AM192BXVTFR | Ducted Indoor Units | 182000 | 12.15 | 24.1 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.1667
209842190 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR |  |  | AM216BXVTFR | Ducted Indoor Units | 206000 | 12.1 | 24.1 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
209842191 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTFR | AM120BXVTFR |  |  | AM240BXVTFR | Ducted Indoor Units | 228000 | 12.05 | 24 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
209842199 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR |  |  | AM192BXVTFR | Non-Ducted Indoor Units | 182000 | 13.6 | 32.1 | 206000 | 4.13 | 206000 | 2.27 | R-410A | 15.1667
209842200 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR |  |  | AM216BXVTFR | Non-Ducted Indoor Units | 206000 | 13.6 | 31.7 | 232000 | 4.03 | 232000 | 2.18 | R-410A | 17.1667
209842407 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH |  |  | AM192BXVTFH | Ducted Indoor Units | 182000 | 12.15 | 24.1 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.1667
209842408 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH |  |  | AM216BXVTFH | Ducted Indoor Units | 206000 | 12.1 | 24.1 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
209842409 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTFH | AM120BXVTFH |  |  | AM240BXVTFH | Ducted Indoor Units | 228000 | 12.05 | 24 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
209842417 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH |  |  | AM192BXVTFH | Non-Ducted Indoor Units | 182000 | 13.6 | 32.1 | 206000 | 4.13 | 206000 | 2.27 | R-410A | 15.1667
209842418 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH |  |  | AM216BXVTFH | Non-Ducted Indoor Units | 206000 | 13.6 | 31.7 | 232000 | 4.03 | 232000 | 2.18 | R-410A | 17.1667
209842427 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH |  |  | AM192BXVTJH | Ducted Indoor Units | 182000 | 12.15 | 24.1 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.1667
209842428 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH |  |  | AM216BXVTJH | Ducted Indoor Units | 206000 | 12.1 | 24.1 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
209842429 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTJH | AM120BXVTJH |  |  | AM240BXVTJH | Ducted Indoor Units | 228000 | 12.05 | 24 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
209842437 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH |  |  | AM192BXVTJH | Non-Ducted Indoor Units | 182000 | 13.6 | 32.1 | 206000 | 4.13 | 206000 | 2.27 | R-410A | 15.1667
209842438 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH |  |  | AM216BXVTJH | Non-Ducted Indoor Units | 206000 | 13.6 | 31.7 | 232000 | 4.03 | 232000 | 2.18 | R-410A | 17.1667
209842447 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR |  |  | AM192BXVTJR | Ducted Indoor Units | 182000 | 12.15 | 24.1 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.1667
209842448 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR |  |  | AM216BXVTJR | Ducted Indoor Units | 206000 | 12.1 | 24.1 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
209842449 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTJR | AM120BXVTJR |  |  | AM240BXVTJR | Ducted Indoor Units | 228000 | 12.05 | 24 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
209842457 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR |  |  | AM192BXVTJR | Non-Ducted Indoor Units | 182000 | 13.6 | 32.1 | 206000 | 4.13 | 206000 | 2.27 | R-410A | 15.1667
209842458 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR |  |  | AM216BXVTJR | Non-Ducted Indoor Units | 206000 | 13.6 | 31.7 | 232000 | 4.03 | 232000 | 2.18 | R-410A | 17.1667
209863173 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR |  |  | AM192BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.87 | 28.1 | 206000 | 3.98 | 206000 | 2.27 | R-410A | 15.1667
209863174 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR |  |  | AM216BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.85 | 27.9 | 232000 | 3.92 | 232000 | 2.2 | R-410A | 17.1667
209863175 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTFR | AM120BXVTFR |  |  | AM240BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.62 | 27.8 | 258000 | 3.89 | 258000 | 2.11 | R-410A | 19
209863183 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH |  |  | AM192BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.87 | 28.1 | 206000 | 3.98 | 206000 | 2.27 | R-410A | 15.1667
209863184 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH |  |  | AM216BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.85 | 27.9 | 232000 | 3.92 | 232000 | 2.2 | R-410A | 17.1667
209863185 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTFH | AM120BXVTFH |  |  | AM240BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.62 | 27.8 | 258000 | 3.89 | 258000 | 2.11 | R-410A | 19
209863193 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH |  |  | AM192BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.87 | 28.1 | 206000 | 3.98 | 206000 | 2.27 | R-410A | 15.1667
209863194 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH |  |  | AM216BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.85 | 27.9 | 232000 | 3.92 | 232000 | 2.2 | R-410A | 17.1667
209863195 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120BXVTJH | AM120BXVTJH |  |  | AM240BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.62 | 27.8 | 258000 | 3.89 | 258000 | 2.11 | R-410A | 19
209863203 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR |  |  | AM192BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.87 | 28.1 | 206000 | 3.98 | 206000 | 2.27 | R-410A | 15.1667
209863204 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR |  |  | AM216BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.85 | 27.9 | 232000 | 3.92 | 232000 | 2.2 | R-410A | 17.1667
209863205 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120BXVTJR | AM120BXVTJR |  |  | AM240BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.62 | 27.8 | 258000 | 3.89 | 258000 | 2.11 | R-410A | 19
206453529 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 24.45 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
206453530 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 |  |  |  | ARUM216BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 23.6 | 230000 | 3.36 | 150000 | 2.5 | R-410A | 17.1667
206453532 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 24.45 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
206453533 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 |  |  |  | ARUM216DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 23.6 | 230000 | 3.36 | 150000 | 2.5 | R-410A | 17.1667
205281465 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
205281467 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
206453546 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.3 | 25.8 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
206453548 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.3 | 25.8 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
206453549 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 |  |  |  | ARUM168BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 23.65 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
206453551 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 |  |  |  | ARUM168DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 23.65 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
208102018 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y | VEP072C432Y |  |  | VEP140C432Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 23.3 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
208102025 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP096C432G |  |  | VEP168C432G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.75 | 21.5 | 180000 | 3.46 | 118000 | 2.34 | R-410A | 13.3333
208102030 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G |  |  | VEP192C432G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 21.5 | 206000 | 3.32 | 134000 | 2.18 | R-410A | 15.3333
208102035 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP120C432G |  |  | VEP216C432G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 21.5 | 230000 | 3.38 | 150000 | 2.24 | R-410A | 17.1667
208102040 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G | VEP120C432G |  |  | VEP240C432G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 20.5 | 256000 | 3.34 | 168000 | 2.17 | R-410A | 19
208102022 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP072C432G |  |  | VEP144C432G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 22.75 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
207382956 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR |  |  |  | AM144FXVAFR | Non-Ducted Indoor Units | 138000 | 11.5 | 23.9 | 154000 | 3.81 | 100000 | 2.55 | R-410A | 11.5
207385924 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR |  |  |  | AM144FXVAFR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 22.45 | 154000 | 3.62 | 100000 | 2.54 | R-410A | 11.5
207699038 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR |  |  | AM144KXVTFR | Non-Ducted Indoor Units | 138000 | 13.3 | 29.8 | 154000 | 3.71 | 154000 | 2.15 | R-410A | 11.5
207699039 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR |  |  | AM168KXVTFR | Non-Ducted Indoor Units | 160000 | 13.4 | 29.7 | 180000 | 3.74 | 180000 | 2.15 | R-410A | 13.3333
207699041 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR |  |  | AM192KXVTFR | Non-Ducted Indoor Units | 184000 | 13.1 | 29.1 | 206000 | 3.78 | 206000 | 2.15 | R-410A | 15.3333
207699042 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR |  |  | AM144KXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.35 | 26.4 | 154000 | 3.65 | 154000 | 2.22 | R-410A | 11.5
207699043 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR |  |  | AM168KXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.45 | 26.2 | 180000 | 3.67 | 180000 | 2.2 | R-410A | 13.3333
207699045 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR |  |  | AM192KXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.3 | 25.8 | 206000 | 3.66 | 206000 | 2.2 | R-410A | 15.3333
210691228 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA |  |  |  | AVWT-144FHFSHA | Non-Ducted Indoor Units | 138000 | 11.4 | 25.5 | 150000 | 3.5 | 105000 | 2.41 | R-410A | 11.5
210691229 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA |  |  |  | AVWT-144FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.95 | 23.25 | 150000 | 3.35 | 105000 | 2.34 | R-410A | 11.5
210691231 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-168FHFSHA |  |  |  | AVWT-168FHFSHA | Non-Ducted Indoor Units | 160000 | 11.1 | 24.1 | 170000 | 3.39 | 115000 | 2.28 | R-410A | 13.3333
210691232 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-168FHFSHA |  |  |  | AVWT-168FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.75 | 22.45 | 170000 | 3.29 | 115000 | 2.16 | R-410A | 13.3333
210691234 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-192FHFSHA |  |  |  | AVWT-192FHFSHA | Non-Ducted Indoor Units | 184000 | 11.2 | 24.5 | 200000 | 3.4 | 140000 | 2.43 | R-410A | 15.3333
210691235 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-192FHFSHA |  |  |  | AVWT-192FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.95 | 200000 | 3.31 | 140000 | 2.34 | R-410A | 15.3333
210691236 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA | AVWT-120FHFSHA |  |  | AVWT-216FHFSHA | Ducted Indoor Units | 206000 | 11.1 | 20.7 | 226000 | 3.4 | 150000 | 2.32 | R-410A | 17.1667
210691237 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA | AVWT-120FHFSHA |  |  | AVWT-216FHFSHA | Non-Ducted Indoor Units | 206000 | 12.4 | 23.2 | 226000 | 3.88 | 150000 | 2.52 | R-410A | 17.1667
210691238 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHA | AVWT-120FHFSHA |  |  | AVWT-216FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.75 | 21.95 | 226000 | 3.64 | 150000 | 2.42 | R-410A | 17.1667
210691239 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-120FHFSHA |  |  | AVWT-240FHFSHA | Ducted Indoor Units | 228000 | 11.1 | 20.4 | 252000 | 3.35 | 162000 | 2.32 | R-410A | 19
210691240 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-120FHFSHA |  |  | AVWT-240FHFSHA | Non-Ducted Indoor Units | 228000 | 12.4 | 22.8 | 252000 | 3.8 | 162000 | 2.59 | R-410A | 19
210691241 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-120FHFSHA |  |  | AVWT-240FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 21.6 | 252000 | 3.57 | 162000 | 2.45 | R-410A | 19
212511006 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
212511007 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
212511008 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Ducted Indoor Units | 160000 | 10.9 | 19 | 180000 | 3.63 | 132000 | 2.64 | R-410A | 13.3333
212511009 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Ducted Indoor Units | 184000 | 12.2 | 20.3 | 206000 | 4 | 150000 | 2.88 | R-410A | 15.3333
212511010 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Ducted Indoor Units | 184000 | 11.9 | 19.9 | 206000 | 3.83 | 150000 | 2.74 | R-410A | 15.3333
212511011 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Ducted Indoor Units | 230000 | 12.1 | 20.6 | 256000 | 3.95 | 182000 | 2.91 | R-410A | 19.1667
212511012 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Ducted Indoor Units | 230000 | 12 | 20.3 | 256000 | 3.9 | 182000 | 2.86 | R-410A | 19.1667
212511027 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Ducted Indoor Units | 138000 | 11.3 | 20 | 154000 | 3.91 | 109000 | 2.78 | R-410A | 11.5
212511028 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
212511029 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
212511030 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
212511031 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
212511037 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
212511038 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Ducted Indoor Units | 206000 | 12.1 | 20.3 | 232000 | 3.93 | 164000 | 2.86 | R-410A | 17.1667
212511042 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
212511043 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
212511044 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Ducted Indoor Units | 160000 | 10.9 | 19 | 180000 | 3.63 | 132000 | 2.64 | R-410A | 13.3333
212511045 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Ducted Indoor Units | 184000 | 12.2 | 20.3 | 206000 | 4 | 150000 | 2.88 | R-410A | 15.3333
212511046 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Ducted Indoor Units | 184000 | 11.9 | 19.9 | 206000 | 3.83 | 150000 | 2.74 | R-410A | 15.3333
212511047 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
212511048 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Ducted Indoor Units | 230000 | 12.1 | 20.6 | 256000 | 3.95 | 182000 | 2.91 | R-410A | 19.1667
212511049 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Ducted Indoor Units | 230000 | 12 | 20.3 | 256000 | 3.9 | 182000 | 2.86 | R-410A | 19.1667
212511064 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Ducted Indoor Units | 138000 | 11.3 | 20 | 154000 | 3.91 | 109000 | 2.78 | R-410A | 11.5
212511065 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
212511066 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
212511067 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Ducted Indoor Units | 206000 | 12.1 | 20.3 | 232000 | 3.93 | 164000 | 2.86 | R-410A | 17.1667
212511068 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
212511069 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
212511083 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Non-Ducted Indoor Units | 138000 | 12.2 | 25.9 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
212511084 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Ducted Indoor Units | 138000 | 11.4 | 20.2 | 154000 | 3.52 | 109000 | 2.48 | R-410A | 11.5
212511085 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Non-Ducted Indoor Units | 138000 | 12.2 | 25.9 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
212511086 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Ducted Indoor Units | 138000 | 11.4 | 20.2 | 154000 | 3.52 | 109000 | 2.48 | R-410A | 11.5
212511087 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL |  |  |  | MMY-MAP1686FT6P-UL | Non-Ducted Indoor Units | 160000 | 10.7 | 23.3 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
212511089 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL |  |  |  | MMY-MAP1686FT9P-UL | Non-Ducted Indoor Units | 160000 | 10.7 | 23.3 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
212511091 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Non-Ducted Indoor Units | 184000 | 12.2 | 26.1 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
212511092 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Ducted Indoor Units | 184000 | 11.5 | 20.4 | 206000 | 3.67 | 150000 | 2.45 | R-410A | 15.3333
212511093 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Non-Ducted Indoor Units | 184000 | 12.2 | 26.1 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
212511094 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Ducted Indoor Units | 184000 | 11.5 | 20.4 | 206000 | 3.67 | 150000 | 2.45 | R-410A | 15.3333
212511095 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Non-Ducted Indoor Units | 184000 | 11.7 | 25.3 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
212511096 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Ducted Indoor Units | 184000 | 11.3 | 19.9 | 206000 | 3.57 | 150000 | 2.4 | R-410A | 15.3333
212511097 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Non-Ducted Indoor Units | 184000 | 11.7 | 25.3 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
212511098 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Ducted Indoor Units | 184000 | 11.3 | 19.9 | 206000 | 3.57 | 150000 | 2.4 | R-410A | 15.3333
212511099 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Non-Ducted Indoor Units | 206000 | 11.6 | 24.2 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
212511100 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Ducted Indoor Units | 206000 | 11.2 | 20.5 | 232000 | 3.74 | 164000 | 2.44 | R-410A | 17.1667
212511101 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Non-Ducted Indoor Units | 206000 | 11.6 | 24.2 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
212511102 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Ducted Indoor Units | 206000 | 11.2 | 20.5 | 232000 | 3.74 | 164000 | 2.44 | R-410A | 17.1667
212511103 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.3 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
212511104 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Ducted Indoor Units | 230000 | 11.3 | 20.8 | 256000 | 3.56 | 182000 | 2.47 | R-410A | 19.1667
212511105 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.3 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
212511106 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Ducted Indoor Units | 230000 | 11.3 | 20.8 | 256000 | 3.56 | 182000 | 2.47 | R-410A | 19.1667
212511107 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP240S6FT6P-UL | Non-Ducted Indoor Units | 230000 | 10.7 | 22.8 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
212511109 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP240S6FT9P-UL | Non-Ducted Indoor Units | 230000 | 10.7 | 22.8 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
212512452 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Non-Ducted Indoor Units | 144000 | 11.8 | 23 | 162000 | 3.77 | 109000 | 2.57 | R-410A | 12
212512453 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Ducted Indoor Units | 144000 | 11.1 | 20 | 162000 | 3.57 | 109000 | 2.54 | R-410A | 12
212512463 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.85 | 22.8 | 154000 | 4.01 | 109000 | 2.75 | R-410A | 11.5
212512464 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.05 | 154000 | 3.63 | 109000 | 2.54 | R-410A | 11.5
212512465 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.05 | 154000 | 3.63 | 109000 | 2.54 | R-410A | 11.5
212512466 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 21.4 | 180000 | 3.68 | 132000 | 2.56 | R-410A | 13.3333
212512467 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 21.4 | 180000 | 3.68 | 132000 | 2.56 | R-410A | 13.3333
212512470 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 4.02 | 150000 | 2.82 | R-410A | 15.3333
212512471 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.25 | 22.5 | 206000 | 3.89 | 150000 | 2.71 | R-410A | 15.3333
212512472 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.85 | 23.25 | 206000 | 3.68 | 150000 | 2.47 | R-410A | 15.3333
212512473 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.85 | 23.25 | 206000 | 3.68 | 150000 | 2.47 | R-410A | 15.3333
212512474 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 22.6 | 206000 | 3.58 | 150000 | 2.42 | R-410A | 15.3333
212512475 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 22.6 | 206000 | 3.58 | 150000 | 2.42 | R-410A | 15.3333
212512476 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.45 | 232000 | 3.91 | 164000 | 2.8 | R-410A | 17.1667
212512477 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.35 | 232000 | 3.65 | 164000 | 2.45 | R-410A | 17.1667
212512478 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.35 | 232000 | 3.65 | 164000 | 2.45 | R-410A | 17.1667
212512479 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.05 | 22.35 | 256000 | 3.85 | 182000 | 2.78 | R-410A | 19.1667
212512480 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.8 | 21.95 | 256000 | 3.8 | 182000 | 2.74 | R-410A | 19.1667
212512481 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.45 | 22.05 | 256000 | 3.58 | 182000 | 2.5 | R-410A | 19.1667
212512482 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.45 | 22.05 | 256000 | 3.58 | 182000 | 2.5 | R-410A | 19.1667
212512526 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.85 | 22.8 | 154000 | 4.01 | 109000 | 2.75 | R-410A | 11.5
212512527 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 4.02 | 150000 | 2.82 | R-410A | 15.3333
212512528 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.25 | 22.5 | 206000 | 3.89 | 150000 | 2.71 | R-410A | 15.3333
212512529 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.05 | 22.35 | 256000 | 3.85 | 182000 | 2.78 | R-410A | 19.1667
212512530 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.8 | 21.95 | 256000 | 3.8 | 182000 | 2.74 | R-410A | 19.1667
212512537 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.45 | 232000 | 3.91 | 164000 | 2.8 | R-410A | 17.1667
212512539 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 144000 | 11.45 | 21.5 | 162000 | 3.67 | 109000 | 2.55 | R-410A | 12
212924820 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB | AVWT-72FFFSHB |  |  | AVWT-144FFFSHB | Non-Ducted Indoor Units | 144000 | 12.2 | 20 | 162000 | 4.1 | 105000 | 2.45 | R-410A | 12
212924827 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB | AVWT-72FHFSHB |  |  | AVWT-144FHFSHB | Non-Ducted Indoor Units | 144000 | 12.2 | 20 | 162000 | 4.1 | 105000 | 2.45 | R-410A | 12
212928533 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB | AVWT-72FFFSHB |  |  | AVWT-144FFFSHB | Ducted Indoor Units | 144000 | 12.5 | 18.5 | 162000 | 3.72 | 105000 | 2.45 | R-410A | 12
212928534 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB | AVWT-96FFFSHB |  |  | AVWT-192FFFSHB | Ducted Indoor Units | 192000 | 11.5 | 19 | 206000 | 3.6 | 140000 | 2.37 | R-410A | 16
212928535 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB | AVWT-96FFFSHB |  |  | AVWT-192FFFSHB | Non-Ducted Indoor Units | 192000 | 11.8 | 19.5 | 206000 | 3.94 | 140000 | 2.4 | R-410A | 16
212928538 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB | AVWT-72FHFSHB |  |  | AVWT-144FHFSHB | Ducted Indoor Units | 144000 | 12.5 | 18.5 | 162000 | 3.72 | 105000 | 2.45 | R-410A | 12
212928539 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB | AVWT-96FHFSHB |  |  | AVWT-192FHFSHB | Ducted Indoor Units | 192000 | 11.5 | 19 | 206000 | 3.6 | 140000 | 2.37 | R-410A | 16
212928540 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB | AVWT-96FHFSHB |  |  | AVWT-192FHFSHB | Non-Ducted Indoor Units | 192000 | 11.8 | 19.5 | 206000 | 3.94 | 140000 | 2.4 | R-410A | 16
212928543 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FFFSHB | AVWT-72FFFSHB |  |  | AVWT-144FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 144000 | 12.35 | 19.25 | 162000 | 3.91 | 105000 | 2.45 | R-410A | 12
212928544 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FFFSHB | AVWT-96FFFSHB |  |  | AVWT-192FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 192000 | 11.65 | 19.25 | 206000 | 3.77 | 140000 | 2.38 | R-410A | 16
212928546 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-72FHFSHB | AVWT-72FHFSHB |  |  | AVWT-144FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 144000 | 12.35 | 19.25 | 162000 | 3.91 | 105000 | 2.45 | R-410A | 12
212928547 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FHFSHB | AVWT-96FHFSHB |  |  | AVWT-192FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 192000 | 11.65 | 19.25 | 206000 | 3.77 | 140000 | 2.38 | R-410A | 16
213686153 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH | AVWT-120FLFSH |  |  | AVWT-216FLFSH | Ducted Indoor Units | 206000 | 11.1 | 20.7 | 226000 | 3.4 | 150000 | 2.32 | R-410A | 17.1667
213686154 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH | AVWT-120FLFSH |  |  | AVWT-216FLFSH | Non-Ducted Indoor Units | 206000 | 12.4 | 23.2 | 226000 | 3.88 | 150000 | 2.52 | R-410A | 17.1667
213686155 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-96FLFSH | AVWT-120FLFSH |  |  | AVWT-216FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.75 | 21.95 | 226000 | 3.64 | 150000 | 2.42 | R-410A | 17.1667
213686156 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-120FLFSH |  |  | AVWT-240FLFSH | Ducted Indoor Units | 228000 | 11.1 | 20.4 | 252000 | 3.35 | 162000 | 2.32 | R-410A | 19
213686157 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-120FLFSH |  |  | AVWT-240FLFSH | Non-Ducted Indoor Units | 228000 | 12.4 | 22.8 | 252000 | 3.8 | 162000 | 2.59 | R-410A | 19
213686158 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-120FLFSH |  |  | AVWT-240FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 21.6 | 252000 | 3.57 | 162000 | 2.45 | R-410A | 19
213886376 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM096BXVTFH |  |  | AM192BXVTFH1 | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
213886378 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM096BXVTJH |  |  | AM192BXVTJH1 | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
213886379 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM096BXVTJR |  |  | AM192BXVTJR1 | Ducted Indoor Units | 184000 | 12.15 | 22.5 | 206000 | 3.83 | 206000 | 2.27 | R-410A | 15.3333
213886408 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM096BXVTFH |  |  | AM192BXVTFH1 | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
213886410 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM096BXVTJH |  |  | AM192BXVTJH1 | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
213886411 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM096BXVTJR |  |  | AM192BXVTJR1 | Non-Ducted Indoor Units | 184000 | 12.4 | 24.9 | 206000 | 3.76 | 206000 | 2.2 | R-410A | 15.3333
213886412 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM072BXVTFH |  | AM216BXVTFH1 | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
213886414 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM072BXVTJH |  | AM216BXVTJH1 | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
213886415 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM072BXVTJR |  | AM216BXVTJR1 | Non-Ducted Indoor Units | 206000 | 12.3 | 25.9 | 232000 | 3.66 | 232000 | 2.2 | R-410A | 17.1667
213886416 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM096BXVTFH |  | AM240BXVTFH1 | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
213886418 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM096BXVTJH |  | AM240BXVTJH1 | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
213886419 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM096BXVTJR |  | AM240BXVTJR1 | Non-Ducted Indoor Units | 228000 | 12 | 25.3 | 258000 | 3.61 | 258000 | 2.1 | R-410A | 19
213886448 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM096BXVTFH |  |  | AM192BXVTFH1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
213886450 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM096BXVTJH |  |  | AM192BXVTJH1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
213886451 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM096BXVTJR |  |  | AM192BXVTJR1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.27 | 23.7 | 206000 | 3.79 | 206000 | 2.23 | R-410A | 15.3333
213893861 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM072BXVTFH |  | AM216BXVTFH1 | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
213893863 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM072BXVTJH |  | AM216BXVTJH1 | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
213893864 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM072BXVTJR |  | AM216BXVTJR1 | Ducted Indoor Units | 206000 | 12.1 | 22.4 | 232000 | 3.81 | 232000 | 2.23 | R-410A | 17.1667
213893865 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM096BXVTFH |  | AM240BXVTFH1 | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
213893867 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM096BXVTJH |  | AM240BXVTJH1 | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
213893868 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM096BXVTJR |  | AM240BXVTJR1 | Ducted Indoor Units | 228000 | 12.05 | 22.3 | 258000 | 3.8 | 258000 | 2.16 | R-410A | 19
213893869 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM072BXVTFH |  | AM216BXVTFH1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
213893871 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM072BXVTJH |  | AM216BXVTJH1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
213893872 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM072BXVTJR |  | AM216BXVTJR1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.2 | 24.15 | 232000 | 3.73 | 232000 | 2.21 | R-410A | 17.1667
213893873 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM072BXVTFH | AM096BXVTFH |  | AM240BXVTFH1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213893875 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM072BXVTJH | AM096BXVTJH |  | AM240BXVTJH1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
213893876 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM072BXVTJR | AM096BXVTJR |  | AM240BXVTJR1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.02 | 23.8 | 258000 | 3.7 | 258000 | 2.13 | R-410A | 19
200084129 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 21.75 | 256000 | 3.64 | 172000 | 2.43 | R-410A | 19
200084130 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL5-1 |  |  |  | 38VMA240RDL5-1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 21.75 | 256000 | 3.64 | 172000 | 2.43 | R-410A | 19
10515233 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* | RELQ72TATJ* |  |  | RELQ144TATJ* | Non-Ducted Indoor Units | 138000 | 12.9 | 22.5 | 154000 | 3.81 | 131000 | 2.2 | R-410A | 11.5
10515234 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* | RELQ72TAYD* |  |  | RELQ144TAYD* | Non-Ducted Indoor Units | 138000 | 12.9 | 22.5 | 154000 | 3.81 | 131000 | 2.2 | R-410A | 11.5
10515235 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* | RELQ120TATJ* |  |  | RELQ240TATJ* | Non-Ducted Indoor Units | 228000 | 12.3 | 21.1 | 256000 | 3.68 | 218000 | 2.2 | R-410A | 19
10515236 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* | RELQ120TAYD* |  |  | RELQ240TAYD* | Non-Ducted Indoor Units | 228000 | 12.3 | 21.1 | 256000 | 3.68 | 218000 | 2.2 | R-410A | 19
10515243 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* | RELQ72TATJ* |  |  | RELQ144TATJ* | Ducted Indoor Units | 138000 | 12.6 | 18.6 | 154000 | 3.55 | 131000 | 2.2 | R-410A | 11.5
10515244 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* | RELQ72TAYD* |  |  | RELQ144TAYD* | Ducted Indoor Units | 138000 | 12.6 | 18.6 | 154000 | 3.55 | 131000 | 2.2 | R-410A | 11.5
10515245 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* | RELQ120TATJ* |  |  | RELQ240TATJ* | Ducted Indoor Units | 228000 | 11.7 | 18.6 | 256000 | 3.49 | 218000 | 2.13 | R-410A | 19
10515246 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* | RELQ120TAYD* |  |  | RELQ240TAYD* | Ducted Indoor Units | 228000 | 11.7 | 18.6 | 256000 | 3.49 | 218000 | 2.13 | R-410A | 19
10515253 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TATJ* | RELQ72TATJ* |  |  | RELQ144TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.75 | 20.55 | 154000 | 3.68 | 131000 | 2.2 | R-410A | 11.5
10515254 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYD* | RELQ72TAYD* |  |  | RELQ144TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.75 | 20.55 | 154000 | 3.68 | 131000 | 2.2 | R-410A | 11.5
10515255 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TATJ* | RELQ120TATJ* |  |  | RELQ240TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12 | 19.85 | 256000 | 3.58 | 218000 | 2.16 | R-410A | 19
10515256 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYD* | RELQ120TAYD* |  |  | RELQ240TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12 | 19.85 | 256000 | 3.58 | 218000 | 2.16 | R-410A | 19
10515257 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* | RELQ96TATJ* |  |  | RELQ192TATJ* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.1 | 206000 | 3.85 | 176000 | 2.2 | R-410A | 15.3333
10515258 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* | RELQ96TAYD* |  |  | RELQ192TAYD* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.1 | 206000 | 3.85 | 176000 | 2.2 | R-410A | 15.3333
10515259 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* | RELQ96TATJ* |  |  | RELQ192TATJ* | Ducted Indoor Units | 184000 | 12.7 | 19 | 206000 | 3.57 | 176000 | 2.15 | R-410A | 15.3333
10515260 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* | RELQ96TAYD* |  |  | RELQ192TAYD* | Ducted Indoor Units | 184000 | 12.7 | 19 | 206000 | 3.57 | 176000 | 2.15 | R-410A | 15.3333
10515261 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TATJ* | RELQ96TATJ* |  |  | RELQ192TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.6 | 20.55 | 206000 | 3.71 | 176000 | 2.17 | R-410A | 15.3333
10515262 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYD* | RELQ96TAYD* |  |  | RELQ192TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.6 | 20.55 | 206000 | 3.71 | 176000 | 2.17 | R-410A | 15.3333
10267499 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-72WM/B-U(U) |  |  | GMV-144WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 22.75 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
10306442 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) | IOV072H3CDC712(A) |  |  | IOV144H3CDC725(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 23.3 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
10340642 | 1/1/2027 | GREE | HMSV-A-CB | GMV-Y96WM/A-F(U) | GMV-Y96WM/A-F(U) |  |  | GMV-Y192WM/A-F(U) | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
201874092 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P168YSLMU-A | Ducted Indoor Units | 160000 | 12 | 21 | 178000 | 3.5 | 132000 | 2.47 | R-410A | 13.3333
201874093 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  |  | PUHY-P216TSKMU-A | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
201874095 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  |  | PUHY-P216TSLMU-A | Ducted Indoor Units | 206000 | 12.1 | 21 | 232000 | 3.56 | 164000 | 2.36 | R-410A | 17.1667
201874097 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  |  | PUHY-P216YSKMU-A | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
201874099 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  |  | PUHY-P216YSLMU-A | Ducted Indoor Units | 206000 | 12.1 | 21 | 232000 | 3.56 | 164000 | 2.36 | R-410A | 17.1667
201874142 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TLMU-A |  |  |  | PUHY-P144TLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 24.7 | 152000 | 3.88 | 109000 | 2.22 | R-410A | 11.3333
201874143 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YLMU-A |  |  |  | PUHY-P144YLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 24.7 | 152000 | 3.88 | 109000 | 2.22 | R-410A | 11.3333
201874145 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168TLMU-A |  |  |  | PUHY-P168TLMU-A | Non-Ducted Indoor Units | 160000 | 12.5 | 22.2 | 178000 | 3.77 | 132000 | 2.28 | R-410A | 13.3333
201874146 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168YLMU-A |  |  |  | PUHY-P168YLMU-A | Non-Ducted Indoor Units | 160000 | 12.5 | 22.2 | 178000 | 3.77 | 132000 | 2.28 | R-410A | 13.3333
201874156 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P192TSLMU-A | Non-Ducted Indoor Units | 182000 | 13.5 | 24.5 | 204000 | 3.7 | 150000 | 2.17 | R-410A | 15.1667
201874158 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P144TSLMU-A | Non-Ducted Indoor Units | 136000 | 14.6 | 26 | 152000 | 4.1 | 109000 | 2.13 | R-410A | 11.3333
201874159 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P168TSLMU-A | Non-Ducted Indoor Units | 160000 | 14 | 25 | 178000 | 3.9 | 132000 | 2.19 | R-410A | 13.3333
201874160 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P192YSLMU-A | Non-Ducted Indoor Units | 182000 | 13.5 | 24.5 | 204000 | 3.7 | 150000 | 2.17 | R-410A | 15.1667
201874162 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P144YSLMU-A | Non-Ducted Indoor Units | 136000 | 14.6 | 26 | 152000 | 4.1 | 109000 | 2.13 | R-410A | 11.3333
201874163 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P168YSLMU-A | Non-Ducted Indoor Units | 160000 | 14 | 25 | 178000 | 3.9 | 132000 | 2.19 | R-410A | 13.3333
201874167 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  |  | PUHY-P216TSLMU-A | Non-Ducted Indoor Units | 206000 | 13.3 | 24.5 | 232000 | 3.64 | 164000 | 2.09 | R-410A | 17.1667
201874169 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  |  | PUHY-P216YSLMU-A | Non-Ducted Indoor Units | 206000 | 13.3 | 24.5 | 232000 | 3.64 | 164000 | 2.09 | R-410A | 17.1667
201874029 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TKMU-A |  |  |  | PUHY-P144TKMU-A | Ducted Indoor Units | 136000 | 11.6 | 19.3 | 152000 | 3.56 | 109000 | 2.32 | R-410A | 11.3333
201874030 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TLMU-A |  |  |  | PUHY-P144TLMU-A | Ducted Indoor Units | 136000 | 12.5 | 21.2 | 152000 | 3.55 | 109000 | 2.2 | R-410A | 11.3333
201874031 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YKMU-A |  |  |  | PUHY-P144YKMU-A | Ducted Indoor Units | 136000 | 11.6 | 19.3 | 152000 | 3.56 | 108000 | 2.32 | R-410A | 11.3333
201874032 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YLMU-A |  |  |  | PUHY-P144YLMU-A | Ducted Indoor Units | 136000 | 12.5 | 21.2 | 152000 | 3.55 | 109000 | 2.2 | R-410A | 11.3333
201874033 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168TLMU-A |  |  |  | PUHY-P168TLMU-A | Ducted Indoor Units | 160000 | 11.6 | 18.7 | 178000 | 3.47 | 132000 | 2.38 | R-410A | 13.3333
201874034 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168YLMU-A |  |  |  | PUHY-P168YLMU-A | Ducted Indoor Units | 160000 | 11.6 | 18.7 | 178000 | 3.47 | 132000 | 2.38 | R-410A | 13.3333
201874068 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A |  |  | PUHY-P240TSKMU-A | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
201874069 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A |  |  | PUHY-P240TSLMU-A | Ducted Indoor Units | 228000 | 12.1 | 20.8 | 258000 | 3.52 | 182000 | 2.3 | R-410A | 19
201874073 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A |  |  | PUHY-P240YSKMU-A | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
201874074 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A |  |  | PUHY-P240YSLMU-A | Ducted Indoor Units | 228000 | 12.1 | 20.8 | 258000 | 3.52 | 182000 | 2.3 | R-410A | 19
201874078 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P192TSKMU-A | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 204000 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
201874080 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P168TSKMU-A | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
201874081 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P192TSLMU-A | Ducted Indoor Units | 182000 | 12.4 | 21.1 | 204000 | 3.61 | 150000 | 2.33 | R-410A | 15.1667
201874083 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P144TSLMU-A | Ducted Indoor Units | 136000 | 12.6 | 21.3 | 152000 | 3.6 | 109000 | 2.43 | R-410A | 11.3333
201874084 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P168TSLMU-A | Ducted Indoor Units | 160000 | 12 | 21 | 178000 | 3.5 | 132000 | 2.47 | R-410A | 13.3333
201874085 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P192YSKMU-A | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 20400 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
201874087 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P144YSKMU-A | Ducted Indoor Units | 136000 | 12.8 | 19.3 | 152000 | 3.79 | 108000 | 2.56 | R-410A | 11.3333
201874088 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P168YSKMU-A | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
201874089 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P192YSLMU-A | Ducted Indoor Units | 182000 | 12.4 | 21.1 | 204000 | 3.61 | 150000 | 2.33 | R-410A | 15.1667
201902941 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP072C432G |  |  | VEP144C432G | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 22.75 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
201902946 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP096C432G |  |  | VEP168C432G | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.75 | 21.5 | 180000 | 3.46 | 118000 | 2.34 | R-410A | 13.3333
201903106 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G |  |  | VEP192C432G | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 21.5 | 206000 | 3.32 | 134000 | 2.18 | R-410A | 15.3333
201903110 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP120C432G |  |  | VEP216C432G | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 21.5 | 230000 | 3.38 | 150000 | 2.24 | R-410A | 17.1667
201903115 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432G | VEP120C432G |  |  | VEP240C432G | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 20.5 | 256000 | 3.34 | 168000 | 2.17 | R-410A | 19
202516754 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
202516755 | 1/1/2027 | LG | HMSR-A-CB | ARUM144BTE5 |  |  |  | ARUM144BTE5 | Non-Ducted Indoor Units | 138000 | 12.5 | 28.6 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
202516756 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DTE4 |  |  |  | ARUN144DTE4 | Non-Ducted Indoor Units | 138000 | 11.7 | 24.2 | 152000 | 3.6 | 98000 | 2.53 | R-410A | 11.5
202516758 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 |  |  |  | ARUM168BTE5 | Non-Ducted Indoor Units | 160000 | 11.7 | 25.4 | 180000 | 3.57 | 117000 | 2.45 | R-410A | 13.3333
202516760 | 1/1/2027 | LG | HMSV-A-CB | ARUN168DTE4 |  |  |  | ARUN168DTE4 | Non-Ducted Indoor Units | 160000 | 11.1 | 22.1 | 180000 | 3.4 | 117000 | 2.34 | R-410A | 13.3333
202516761 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
202516762 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Non-Ducted Indoor Units | 184000 | 12.4 | 25.9 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
202516764 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 |  |  |  | ARUM216BTE5 | Non-Ducted Indoor Units | 206000 | 11.2 | 24.8 | 230000 | 3.53 | 150000 | 2.66 | R-410A | 17.1667
202516765 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 | ARUN144DTE4 |  |  | ARUN216DTE4 | Ducted Indoor Units | 206000 | 12 | 22.1 | 230000 | 3.66 | 150000 | 2.47 | R-410A | 17.1667
202516766 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 | ARUN144DTE4 |  |  | ARUN216DTE4 | Non-Ducted Indoor Units | 206000 | 12.2 | 25.5 | 230000 | 3.73 | 150000 | 2.58 | R-410A | 17.1667
202516768 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN144DTE4 |  |  | ARUN240DTE4 | Non-Ducted Indoor Units | 228000 | 12.2 | 22 | 256000 | 3.67 | 168000 | 2.61 | R-410A | 19
202517446 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DTE4 |  |  |  | ARUN144DTE4 | Ducted Indoor Units | 138000 | 11.9 | 22.5 | 152000 | 3.49 | 98000 | 2.52 | R-410A | 11.5
202519357 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 | ARUN121DTE4 |  |  | ARUN192DTE4 | Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 3.66 | 134000 | 2.49 | R-410A | 15.3333
202519358 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 | ARUN121DTE4 |  |  | ARUN192DTE4 | Non-Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.62 | 134000 | 2.45 | R-410A | 15.3333
202519359 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN144DTE4 |  |  | ARUN240DTE4 | Ducted Indoor Units | 228000 | 11.6 | 20 | 256000 | 3.56 | 168000 | 2.4 | R-410A | 19
202524545 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Non-Ducted Indoor Units | 138000 | 12.5 | 28.6 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
202524546 | 1/1/2027 | LG | HMSR-A-CB | ARUM144DTE5 |  |  |  | ARUM144DTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
202524547 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 |  |  |  | ARUM168DTE5 | Non-Ducted Indoor Units | 160000 | 11.7 | 25.4 | 180000 | 3.57 | 117000 | 2.45 | R-410A | 13.3333
202524549 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Non-Ducted Indoor Units | 184000 | 12.4 | 25.9 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
202524550 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
202524551 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 |  |  |  | ARUM216DTE5 | Non-Ducted Indoor Units | 206000 | 11.2 | 24.8 | 230000 | 3.53 | 150000 | 2.66 | R-410A | 17.1667
202534252 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DTE4 |  |  |  | ARUB144DTE4 | Non-Ducted Indoor Units | 138000 | 11.7 | 24.2 | 152000 | 3.6 | 98000 | 2.53 | R-410A | 11.5
202534258 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BTE4 |  |  |  | ARUN144BTE4 | Ducted Indoor Units | 138000 | 11.9 | 22.5 | 152000 | 3.49 | 98000 | 2.52 | R-410A | 11.5
202534259 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BTE4 |  |  |  | ARUN144BTE4 | Non-Ducted Indoor Units | 138000 | 11.7 | 24.2 | 152000 | 3.6 | 98000 | 2.53 | R-410A | 11.5
202534260 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DTE4 |  |  |  | ARUB144DTE4 | Ducted Indoor Units | 138000 | 11.9 | 22.5 | 152000 | 3.49 | 98000 | 2.52 | R-410A | 11.5
202534261 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BTE4 |  |  |  | ARUB144BTE4 | Ducted Indoor Units | 138000 | 11.9 | 22.5 | 152000 | 3.49 | 98000 | 2.52 | R-410A | 11.5
202534262 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BTE4 |  |  |  | ARUB144BTE4 | Non-Ducted Indoor Units | 138000 | 11.7 | 24.2 | 152000 | 3.6 | 98000 | 2.53 | R-410A | 11.5
202534264 | 1/1/2027 | LG | HMSV-A-CB | ARUN168BTE4 |  |  |  | ARUN168BTE4 | Non-Ducted Indoor Units | 160000 | 11.1 | 22.1 | 180000 | 3.4 | 117000 | 2.34 | R-410A | 13.3333
202534266 | 1/1/2027 | LG | HMSR-A-CB | ARUB168DTE4 |  |  |  | ARUB168DTE4 | Non-Ducted Indoor Units | 160000 | 11.1 | 22.1 | 180000 | 3.4 | 117000 | 2.34 | R-410A | 13.3333
202534268 | 1/1/2027 | LG | HMSR-A-CB | ARUB168BTE4 |  |  |  | ARUB168BTE4 | Non-Ducted Indoor Units | 160000 | 11.1 | 22.1 | 180000 | 3.4 | 117000 | 2.34 | R-410A | 13.3333
202534269 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 | ARUN121BTE4 |  |  | ARUN192BTE4 | Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 3.66 | 134000 | 2.49 | R-410A | 15.3333
202534270 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 | ARUB121DTE4 |  |  | ARUB192DTE4 | Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 3.66 | 134000 | 2.49 | R-410A | 15.3333
202534271 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 | ARUB121BTE4 |  |  | ARUB192BTE4 | Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 3.66 | 134000 | 2.49 | R-410A | 15.3333
202534272 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 | ARUB121DTE4 |  |  | ARUB192DTE4 | Non-Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.62 | 134000 | 2.45 | R-410A | 15.3333
202534273 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 | ARUB121BTE4 |  |  | ARUB192BTE4 | Non-Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.62 | 134000 | 2.45 | R-410A | 15.3333
202534274 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 | ARUN121BTE4 |  |  | ARUN192BTE4 | Non-Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.62 | 134000 | 2.45 | R-410A | 15.3333
202534275 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 | ARUB144BTE4 |  |  | ARUB216BTE4 | Non-Ducted Indoor Units | 206000 | 12.2 | 25.5 | 230000 | 3.73 | 150000 | 2.58 | R-410A | 17.1667
202534276 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 | ARUB144DTE4 |  |  | ARUB216DTE4 | Non-Ducted Indoor Units | 206000 | 12.2 | 25.5 | 230000 | 3.73 | 150000 | 2.58 | R-410A | 17.1667
202534277 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 | ARUN144BTE4 |  |  | ARUN216BTE4 | Non-Ducted Indoor Units | 206000 | 12.2 | 25.5 | 230000 | 3.73 | 150000 | 2.58 | R-410A | 17.1667
202534278 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN144BTE4 |  |  | ARUN240BTE4 | Non-Ducted Indoor Units | 228000 | 12.2 | 22 | 256000 | 3.67 | 168000 | 2.61 | R-410A | 19
202534279 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 | ARUB144BTE4 |  |  | ARUB240BTE4 | Non-Ducted Indoor Units | 228000 | 12.2 | 22 | 256000 | 3.67 | 168000 | 2.61 | R-410A | 19
202534280 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB144DTE4 |  |  | ARUB240DTE4 | Non-Ducted Indoor Units | 228000 | 12.2 | 22 | 256000 | 3.67 | 168000 | 2.61 | R-410A | 19
202534281 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB144DTE4 |  |  | ARUB240DTE4 | Ducted Indoor Units | 228000 | 11.6 | 20 | 256000 | 3.56 | 168000 | 2.4 | R-410A | 19
202534282 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 | ARUB144BTE4 |  |  | ARUB240BTE4 | Ducted Indoor Units | 228000 | 11.6 | 20 | 256000 | 3.56 | 168000 | 2.4 | R-410A | 19
202534283 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN144BTE4 |  |  | ARUN240BTE4 | Ducted Indoor Units | 228000 | 11.6 | 20 | 256000 | 3.56 | 168000 | 2.4 | R-410A | 19
202517464 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 | ARUB144BTE4 |  |  | ARUB216BTE4 | Ducted Indoor Units | 206000 | 12 | 22.1 | 230000 | 3.66 | 150000 | 2.47 | R-410A | 17.1667
202517465 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 | ARUB144DTE4 |  |  | ARUB216DTE4 | Ducted Indoor Units | 206000 | 12 | 22.1 | 230000 | 3.66 | 150000 | 2.47 | R-410A | 17.1667
202517466 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 | ARUN144BTE4 |  |  | ARUN216BTE4 | Ducted Indoor Units | 206000 | 12 | 22.1 | 230000 | 3.66 | 150000 | 2.47 | R-410A | 17.1667
203297470 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P168TLMU-A |  |  |  | PURY-P168TLMU-A | Non-Ducted Indoor Units | 160000 | 11.2 | 19.3 | 178000 | 3.46 | 119000 | 2.32 | R-410A | 13.3333
203297473 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A | PURY-P72TKMU-A |  |  | PURY-P168TSKMU-A | Ducted Indoor Units | 160000 | 12.1 | 18.5 | 178000 | 3.6 | 132000 | 2.52 | R-410A | 13.3333
203297474 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A | PURY-P72TKMU-A |  |  | PURY-P168TSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 18.2 | 178000 | 3.49 | 132000 | 2.2 | R-410A | 13.3333
203297475 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P72TLMU-A |  |  | PURY-P168TSLMU-A | Ducted Indoor Units | 160000 | 11 | 19 | 178000 | 3.37 | 119000 | 2.21 | R-410A | 13.3333
203297476 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P72TLMU-A |  |  | PURY-P168TSLMU-A | Non-Ducted Indoor Units | 160000 | 12.6 | 23.7 | 178000 | 3.74 | 119000 | 2.34 | R-410A | 13.3333
203297478 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P168YLMU-A |  |  |  | PURY-P168YLMU-A | Non-Ducted Indoor Units | 160000 | 11.2 | 19.3 | 178000 | 3.46 | 119000 | 2.32 | R-410A | 13.3333
203297481 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A | PURY-P72YKMU-A |  |  | PURY-P168YSKMU-A | Ducted Indoor Units | 160000 | 12.1 | 18.5 | 178000 | 3.6 | 132000 | 2.52 | R-410A | 13.3333
203297482 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A | PURY-P72YKMU-A |  |  | PURY-P168YSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 18.2 | 178000 | 3.49 | 132000 | 2.2 | R-410A | 13.3333
203297483 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P72YLMU-A |  |  | PURY-P168YSLMU-A | Ducted Indoor Units | 160000 | 11 | 19 | 178000 | 3.37 | 119000 | 2.21 | R-410A | 13.3333
203297484 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P72YLMU-A |  |  | PURY-P168YSLMU-A | Non-Ducted Indoor Units | 160000 | 12.6 | 23.7 | 178000 | 3.74 | 119000 | 2.34 | R-410A | 13.3333
203297487 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A | PURY-P96TKMU-A |  |  | PURY-P192TSKMU-A | Ducted Indoor Units | 182000 | 11.6 | 18.5 | 204000 | 3.62 | 150000 | 2.52 | R-410A | 15.1667
203297489 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P96TLMU-A |  |  | PURY-P192TSLMU-A | Ducted Indoor Units | 182000 | 11.4 | 22.6 | 204000 | 3.51 | 142000 | 2.19 | R-410A | 15.1667
203297490 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P96TLMU-A |  |  | PURY-P192TSLMU-A | Non-Ducted Indoor Units | 182000 | 12.1 | 23 | 204000 | 3.57 | 142000 | 2.16 | R-410A | 15.1667
203297493 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A | PURY-P96YKMU-A |  |  | PURY-P192YSKMU-A | Ducted Indoor Units | 182000 | 11.6 | 18.5 | 204000 | 3.62 | 150000 | 2.52 | R-410A | 15.1667
203297495 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P96YLMU-A |  |  | PURY-P192YSLMU-A | Ducted Indoor Units | 182000 | 11.4 | 22.6 | 204000 | 3.51 | 142000 | 2.19 | R-410A | 15.1667
203297496 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P96YLMU-A |  |  | PURY-P192YSLMU-A | Non-Ducted Indoor Units | 182000 | 12.1 | 23 | 204000 | 3.57 | 142000 | 2.16 | R-410A | 15.1667
203297501 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TKMU-A | PURY-P96TKMU-A |  |  | PURY-P216TSKMU-A | Ducted Indoor Units | 206000 | 11.4 | 18.1 | 232000 | 3.52 | 164000 | 2.26 | R-410A | 17.1667
203297503 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A | PURY-P96TLMU-A |  |  | PURY-P216TSLMU-A | Ducted Indoor Units | 206000 | 11.7 | 20.8 | 232000 | 3.5 | 158000 | 2.19 | R-410A | 17.1667
203297504 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A | PURY-P96TLMU-A |  |  | PURY-P216TSLMU-A | Non-Ducted Indoor Units | 206000 | 12.4 | 22.2 | 232000 | 3.57 | 158000 | 2.09 | R-410A | 17.1667
203297507 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YKMU-A | PURY-P96YKMU-A |  |  | PURY-P216YSKMU-A | Ducted Indoor Units | 206000 | 11.4 | 18.1 | 232000 | 3.52 | 164000 | 2.26 | R-410A | 17.1667
203297509 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A | PURY-P96YLMU-A |  |  | PURY-P216YSLMU-A | Ducted Indoor Units | 206000 | 11.7 | 20.8 | 232000 | 3.5 | 158000 | 2.19 | R-410A | 17.1667
203297510 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A | PURY-P96YLMU-A |  |  | PURY-P216YSLMU-A | Non-Ducted Indoor Units | 206000 | 12.4 | 22.2 | 232000 | 3.57 | 158000 | 2.09 | R-410A | 17.1667
203297516 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TKMU-A | PURY-P120TKMU-A |  |  | PURY-P240TSKMU-A | Non-Ducted Indoor Units | 228000 | 10.9 | 18.1 | 258000 | 3.4 | 182000 | 2.14 | R-410A | 19
203297517 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A | PURY-P120TLMU-A |  |  | PURY-P240TSLMU-A | Ducted Indoor Units | 228000 | 11.8 | 18.6 | 258000 | 3.43 | 174000 | 2.14 | R-410A | 19
203297520 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YKMU-A | PURY-P120YKMU-A |  |  | PURY-P240YSKMU-A | Non-Ducted Indoor Units | 228000 | 10.9 | 18.1 | 258000 | 3.4 | 182000 | 2.14 | R-410A | 19
203297521 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A | PURY-P120YLMU-A |  |  | PURY-P240YSLMU-A | Ducted Indoor Units | 228000 | 11.8 | 18.6 | 258000 | 3.43 | 174000 | 2.14 | R-410A | 19
203301902 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YKMU-A | PURY-P72YKMU-A |  |  | PURY-P144YSKMU-A | Non-Ducted Indoor Units | 136000 | 14.4 | 19.5 | 152000 | 3.62 | 109000 | 2.28 | R-410A | 11.3333
203301903 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TLMU-A |  |  |  | PURY-P144TLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 23.8 | 152000 | 3.69 | 97000 | 2.16 | R-410A | 11.3333
203301904 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TLMU-A | PURY-P72TLMU-A |  |  | PURY-P144TSLMU-A | Non-Ducted Indoor Units | 136000 | 14.2 | 25.2 | 152000 | 4.03 | 97000 | 2.29 | R-410A | 11.3333
203301906 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YLMU-A |  |  |  | PURY-P144YLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 23.8 | 152000 | 3.69 | 97000 | 2.16 | R-410A | 11.3333
203301907 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YLMU-A | PURY-P72YLMU-A |  |  | PURY-P144YSLMU-A | Non-Ducted Indoor Units | 136000 | 14.2 | 25.2 | 152000 | 4.03 | 97000 | 2.29 | R-410A | 11.3333
203334939 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* |  |  |  | REYQ144XATJ* | Non-Ducted Indoor Units | 138000 | 11.9 | 23.5 | 154000 | 3.75 | 109000 | 2.16 | R-410A | 11.5
203334941 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ96XATJ* |  |  | REYQ192XATJ* | Non-Ducted Indoor Units | 184000 | 13 | 22.6 | 206000 | 3.85 | 150000 | 2.5 | R-410A | 15.3333
203334942 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ120XATJ* |  |  | REYQ216XATJ* | Non-Ducted Indoor Units | 206000 | 12.4 | 23.1 | 232000 | 3.76 | 164000 | 2.34 | R-410A | 17.1667
203334943 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ120XATJ* |  |  | REYQ240XATJ* | Non-Ducted Indoor Units | 228000 | 11.6 | 22.2 | 256000 | 3.68 | 182000 | 2.34 | R-410A | 19
203334956 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* |  |  |  | REYQ144XAYD* | Non-Ducted Indoor Units | 138000 | 11.9 | 23.5 | 154000 | 3.75 | 109000 | 2.16 | R-410A | 11.5
203334958 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ96XAYD* |  |  | REYQ192XAYD* | Non-Ducted Indoor Units | 184000 | 13 | 22.6 | 206000 | 3.85 | 150000 | 2.5 | R-410A | 15.3333
203334959 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ120XAYD* |  |  | REYQ216XAYD* | Non-Ducted Indoor Units | 206000 | 12.4 | 23.1 | 232000 | 3.76 | 164000 | 2.34 | R-410A | 17.1667
203334960 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ120XAYD* |  |  | REYQ240XAYD* | Non-Ducted Indoor Units | 228000 | 11.6 | 22.2 | 256000 | 3.68 | 182000 | 2.34 | R-410A | 19
203334973 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* |  |  |  | REYQ144XAYC* | Non-Ducted Indoor Units | 138000 | 11.9 | 23.5 | 154000 | 3.75 | 109000 | 2.16 | R-410A | 11.5
203334975 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ96XAYC* |  |  | REYQ192XAYC* | Non-Ducted Indoor Units | 184000 | 13 | 22.6 | 206000 | 3.85 | 150000 | 2.5 | R-410A | 15.3333
203334976 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ120XAYC* |  |  | REYQ216XAYC* | Non-Ducted Indoor Units | 206000 | 12.4 | 23.1 | 232000 | 3.76 | 164000 | 2.34 | R-410A | 17.1667
203334977 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ120XAYC* |  |  | REYQ240XAYC* | Non-Ducted Indoor Units | 228000 | 11.6 | 22.2 | 256000 | 3.68 | 182000 | 2.34 | R-410A | 19
203334989 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* |  |  |  | REYQ144XATJ* | Ducted Indoor Units | 138000 | 11.6 | 21.6 | 154000 | 3.42 | 109000 | 2.12 | R-410A | 11.5
203334991 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ96XATJ* |  |  | REYQ192XATJ* | Ducted Indoor Units | 184000 | 13 | 21.4 | 206000 | 3.67 | 150000 | 2.37 | R-410A | 15.3333
203334992 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ120XATJ* |  |  | REYQ216XATJ* | Ducted Indoor Units | 206000 | 12.3 | 21.7 | 232000 | 3.52 | 164000 | 2.2 | R-410A | 17.1667
203334993 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ120XATJ* |  |  | REYQ240XATJ* | Ducted Indoor Units | 228000 | 11.7 | 20 | 256000 | 3.39 | 182000 | 2.16 | R-410A | 19
203335006 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* |  |  |  | REYQ144XAYD* | Ducted Indoor Units | 138000 | 11.6 | 21.6 | 154000 | 3.42 | 109000 | 2.12 | R-410A | 11.5
203335008 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ96XAYD* |  |  | REYQ192XAYD* | Ducted Indoor Units | 184000 | 13 | 21.4 | 206000 | 3.67 | 150000 | 2.37 | R-410A | 15.3333
203335009 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ120XAYD* |  |  | REYQ216XAYD* | Ducted Indoor Units | 206000 | 12.3 | 21.7 | 232000 | 3.52 | 164000 | 2.2 | R-410A | 17.1667
203335010 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ120XAYD* |  |  | REYQ240XAYD* | Ducted Indoor Units | 228000 | 11.7 | 20 | 256000 | 3.39 | 182000 | 2.16 | R-410A | 19
203335023 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* |  |  |  | REYQ144XAYC* | Ducted Indoor Units | 138000 | 11.6 | 21.6 | 154000 | 3.42 | 109000 | 2.12 | R-410A | 11.5
203335025 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ96XAYC* |  |  | REYQ192XAYC* | Ducted Indoor Units | 184000 | 13 | 21.4 | 206000 | 3.67 | 150000 | 2.37 | R-410A | 15.3333
203335026 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ120XAYC* |  |  | REYQ216XAYC* | Ducted Indoor Units | 206000 | 12.3 | 21.7 | 232000 | 3.52 | 164000 | 2.2 | R-410A | 17.1667
203335027 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ120XAYC* |  |  | REYQ240XAYC* | Ducted Indoor Units | 228000 | 11.7 | 20 | 256000 | 3.39 | 182000 | 2.16 | R-410A | 19
203364247 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* |  |  |  | REYQ144XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.55 | 154000 | 3.58 | 109000 | 2.14 | R-410A | 11.5
203364249 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ96XATJ* |  |  | REYQ192XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13 | 22 | 206000 | 3.76 | 150000 | 2.43 | R-410A | 15.3333
203364250 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XATJ* | REYQ120XATJ* |  |  | REYQ216XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.35 | 22.4 | 232000 | 3.64 | 164000 | 2.27 | R-410A | 17.1667
203364251 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ120XATJ* |  |  | REYQ240XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.65 | 21.1 | 256000 | 3.53 | 182000 | 2.25 | R-410A | 19
203364264 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* |  |  |  | REYQ144XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.55 | 154000 | 3.58 | 109000 | 2.14 | R-410A | 11.5
203364266 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ96XAYD* |  |  | REYQ192XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13 | 22 | 206000 | 3.76 | 150000 | 2.43 | R-410A | 15.3333
203364267 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYD* | REYQ120XAYD* |  |  | REYQ216XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.35 | 22.4 | 232000 | 3.64 | 164000 | 2.27 | R-410A | 17.1667
203364268 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ120XAYD* |  |  | REYQ240XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.65 | 21.1 | 256000 | 3.53 | 182000 | 2.25 | R-410A | 19
203364281 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* |  |  |  | REYQ144XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.75 | 22.55 | 154000 | 3.58 | 109000 | 2.14 | R-410A | 11.5
203364283 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ96XAYC* |  |  | REYQ192XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 13 | 22 | 206000 | 3.76 | 150000 | 2.43 | R-410A | 15.3333
203364284 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96XAYC* | REYQ120XAYC* |  |  | REYQ216XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.35 | 22.4 | 232000 | 3.64 | 164000 | 2.27 | R-410A | 17.1667
203364285 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ120XAYC* |  |  | REYQ240XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.65 | 21.1 | 256000 | 3.53 | 182000 | 2.25 | R-410A | 19
204572224 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH |  |  |  | AM144FXVAFH | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
204572239 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH |  |  |  | AM144FXVAJH | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
204572254 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR |  |  |  | AM144FXVAFR | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
204572269 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR |  |  |  | AM144FXVAJR | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
204572284 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH |  |  | AM144KXVTFH | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
204572285 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH |  |  | AM192KXVTFH | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
204572286 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM072KXVTFH |  | AM216KXVTFH | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
204572287 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM096KXVTFH |  | AM240KXVTFH | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
204572292 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH |  |  | AM144KXVTJH | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
204572293 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH |  |  | AM192KXVTJH | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
204572294 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM072KXVTJH |  | AM216KXVTJH | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
204572295 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM096KXVTJH |  | AM240KXVTJH | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
204572300 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR |  |  | AM144KXVTFR | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
204572301 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR |  |  | AM192KXVTFR | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
204572302 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM072KXVTFR |  | AM216KXVTFR | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
204572303 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM096KXVTFR |  | AM240KXVTFR | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
204572308 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR |  |  | AM144KXVTJR | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
204572309 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR |  |  | AM192KXVTJR | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
204572310 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM072KXVTJR |  | AM216KXVTJR | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
204572311 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM096KXVTJR |  | AM240KXVTJR | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
204572314 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216KXVGJH |  |  |  | AM216KXVGJH | Ducted Indoor Units | 206000 | 10.7 | 22.3 | 230000 | 3.62 | 150000 | 2.61 | R-410A | 17.1667
204572317 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216KXVGJR |  |  |  | AM216KXVGJR | Ducted Indoor Units | 206000 | 10.7 | 22.3 | 230000 | 3.62 | 150000 | 2.61 | R-410A | 17.1667
204793027 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP144ME2CA* |  |  |  | MVHP144ME2CA* | Ducted Indoor Units | 138000 | 11.7 | 21.8 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
204793028 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP144ME2CA* |  |  |  | MVHP144ME2CA* | Non-Ducted Indoor Units | 138000 | 11.6 | 22 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
204793029 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR144ME2CA* |  |  |  | MVHR144ME2CA* | Ducted Indoor Units | 138000 | 11 | 20.8 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
204793030 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR144ME2CA* |  |  |  | MVHR144ME2CA* | Non-Ducted Indoor Units | 138000 | 11.4 | 22 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
205000507 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR |  |  | AM168KXVTFR | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
205000512 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAFR |  |  |  | AM168HXVAFR | Non-Ducted Indoor Units | 160000 | 11.6 | 23.8 | 180000 | 3.57 | 118000 | 2.47 | R-410A | 13.3333
205000513 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR |  |  | AM168KXVTFR | Non-Ducted Indoor Units | 160000 | 13.4 | 29.7 | 180000 | 3.74 | 180000 | 2.15 | R-410A | 13.3333
205000527 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH |  |  | AM168KXVTFH | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
205000528 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH |  |  | AM168KXVTJH | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
205000529 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR |  |  | AM168KXVTJR | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
205000542 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAFH |  |  |  | AM168HXVAFH | Non-Ducted Indoor Units | 160000 | 11.6 | 23.8 | 180000 | 3.57 | 118000 | 2.47 | R-410A | 13.3333
205000543 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAJH |  |  |  | AM168HXVAJH | Non-Ducted Indoor Units | 160000 | 11.6 | 23.8 | 180000 | 3.57 | 118000 | 2.47 | R-410A | 13.3333
205000544 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAJR |  |  |  | AM168HXVAJR | Non-Ducted Indoor Units | 160000 | 11.6 | 23.8 | 180000 | 3.57 | 118000 | 2.47 | R-410A | 13.3333
205000545 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH |  |  | AM168KXVTFH | Non-Ducted Indoor Units | 160000 | 13.4 | 29.7 | 180000 | 3.74 | 180000 | 2.15 | R-410A | 13.3333
205000546 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH |  |  | AM168KXVTJH | Non-Ducted Indoor Units | 160000 | 13.4 | 29.7 | 180000 | 3.74 | 180000 | 2.15 | R-410A | 13.3333
205000547 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR |  |  | AM168KXVTJR | Non-Ducted Indoor Units | 160000 | 13.4 | 29.7 | 180000 | 3.74 | 180000 | 2.15 | R-410A | 13.3333
205233057 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* |  |  |  | RXYQ144XATJ* | Non-Ducted Indoor Units | 138000 | 12.1 | 24.8 | 154000 | 3.64 | 96000 | 2.33 | R-410A | 11.5
205233062 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* |  |  |  | RXYQ144XAYD* | Non-Ducted Indoor Units | 138000 | 12.1 | 24.8 | 154000 | 3.64 | 96000 | 2.33 | R-410A | 11.5
205233067 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* |  |  |  | RXYQ144XATJ* | Ducted Indoor Units | 138000 | 11.5 | 22.6 | 154000 | 3.34 | 96000 | 2.2 | R-410A | 11.5
205233072 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* |  |  |  | RXYQ144XAYD* | Ducted Indoor Units | 138000 | 11.5 | 22.6 | 154000 | 3.34 | 96000 | 2.2 | R-410A | 11.5
205234700 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XATJ* | RXYQ120XATJ* |  |  | RXYQ192XATJ* | Non-Ducted Indoor Units | 184000 | 11.1 | 22.2 | 206000 | 3.62 | 134000 | 2.27 | R-410A | 15.3333
205234701 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* | RXYQ120XATJ* |  |  | RXYQ216XATJ* | Non-Ducted Indoor Units | 206000 | 10.7 | 20.5 | 230000 | 3.83 | 158000 | 2.57 | R-410A | 17.1667
205234702 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ120XATJ* |  |  | RXYQ240XATJ* | Non-Ducted Indoor Units | 228000 | 11 | 20.8 | 256000 | 3.63 | 170000 | 2.41 | R-410A | 19
205234770 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYD* | RXYQ120XAYD* |  |  | RXYQ192XAYD* | Non-Ducted Indoor Units | 184000 | 11.1 | 22.2 | 206000 | 3.62 | 134000 | 2.27 | R-410A | 15.3333
205234771 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* | RXYQ120XAYD* |  |  | RXYQ216XAYD* | Non-Ducted Indoor Units | 206000 | 10.7 | 20.5 | 230000 | 3.83 | 158000 | 2.57 | R-410A | 17.1667
205234772 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ120XAYD* |  |  | RXYQ240XAYD* | Non-Ducted Indoor Units | 228000 | 11 | 20.8 | 256000 | 3.63 | 170000 | 2.41 | R-410A | 19
205234783 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYC* |  |  |  | RXYQ144XAYC* | Non-Ducted Indoor Units | 138000 | 11.5 | 22.2 | 154000 | 3.84 | 109000 | 2.2 | R-410A | 11.5
205234785 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ96XAYC* |  |  | RXYQ192XAYC* | Non-Ducted Indoor Units | 184000 | 12.4 | 21.9 | 206000 | 3.91 | 150000 | 2.52 | R-410A | 15.3333
205234786 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ120XAYC* |  |  | RXYQ216XAYC* | Non-Ducted Indoor Units | 206000 | 11.8 | 21.7 | 232000 | 3.84 | 164000 | 2.35 | R-410A | 17.1667
205234787 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* |  |  | RXYQ240XAYC* | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 256000 | 3.77 | 182000 | 2.39 | R-410A | 19
205234792 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XATJ* | RXYQ120XATJ* |  |  | RXYQ192XATJ* | Ducted Indoor Units | 184000 | 11.6 | 21.2 | 206000 | 3.29 | 134000 | 2.23 | R-410A | 15.3333
205234793 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* | RXYQ120XATJ* |  |  | RXYQ216XATJ* | Ducted Indoor Units | 206000 | 10.9 | 21.1 | 230000 | 3.5 | 158000 | 2.46 | R-410A | 17.1667
205234794 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ120XATJ* |  |  | RXYQ240XATJ* | Ducted Indoor Units | 228000 | 11.2 | 20.9 | 256000 | 3.33 | 170000 | 2.34 | R-410A | 19
205234802 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYD* | RXYQ120XAYD* |  |  | RXYQ192XAYD* | Ducted Indoor Units | 184000 | 11.6 | 21.2 | 206000 | 3.29 | 134000 | 2.23 | R-410A | 15.3333
205234803 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* | RXYQ120XAYD* |  |  | RXYQ216XAYD* | Ducted Indoor Units | 206000 | 10.9 | 21.1 | 230000 | 3.5 | 158000 | 2.46 | R-410A | 17.1667
205234804 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ120XAYD* |  |  | RXYQ240XAYD* | Ducted Indoor Units | 228000 | 11.2 | 20.9 | 256000 | 3.33 | 170000 | 2.34 | R-410A | 19
205234817 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* |  |  |  | RXYQ144XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.7 | 154000 | 3.49 | 96000 | 2.26 | R-410A | 11.5
205234822 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* |  |  |  | RXYQ144XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.7 | 154000 | 3.49 | 96000 | 2.26 | R-410A | 11.5
205234831 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYC* |  |  |  | RXYQ144XAYC* | Ducted Indoor Units | 138000 | 10.8 | 18.2 | 154000 | 3.46 | 109000 | 2.14 | R-410A | 11.5
205234833 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ96XAYC* |  |  | RXYQ192XAYC* | Ducted Indoor Units | 184000 | 11.8 | 19.2 | 206000 | 3.72 | 150000 | 2.39 | R-410A | 15.3333
205234834 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ120XAYC* |  |  | RXYQ216XAYC* | Ducted Indoor Units | 206000 | 11.3 | 19.1 | 232000 | 3.58 | 164000 | 2.22 | R-410A | 17.1667
205234835 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* |  |  | RXYQ240XAYC* | Ducted Indoor Units | 228000 | 10.7 | 18.1 | 256000 | 3.46 | 182000 | 2.18 | R-410A | 19
205234840 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XATJ* | RXYQ120XATJ* |  |  | RXYQ192XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21.7 | 206000 | 3.45 | 134000 | 2.25 | R-410A | 15.3333
205234841 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XATJ* | RXYQ120XATJ* |  |  | RXYQ216XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 20.8 | 230000 | 3.66 | 158000 | 2.51 | R-410A | 17.1667
205234842 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ120XATJ* |  |  | RXYQ240XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 20.85 | 256000 | 3.48 | 170000 | 2.37 | R-410A | 19
205234850 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72XAYD* | RXYQ120XAYD* |  |  | RXYQ192XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21.7 | 206000 | 3.45 | 134000 | 2.25 | R-410A | 15.3333
205234851 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYD* | RXYQ120XAYD* |  |  | RXYQ216XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 20.8 | 230000 | 3.66 | 158000 | 2.51 | R-410A | 17.1667
205234852 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ120XAYD* |  |  | RXYQ240XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 20.85 | 256000 | 3.48 | 170000 | 2.37 | R-410A | 19
205234863 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYC* |  |  |  | RXYQ144XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.2 | 154000 | 3.65 | 109000 | 2.17 | R-410A | 11.5
205234865 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ96XAYC* |  |  | RXYQ192XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.1 | 20.55 | 206000 | 3.81 | 150000 | 2.45 | R-410A | 15.3333
205234866 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96XAYC* | RXYQ120XAYC* |  |  | RXYQ216XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.55 | 20.4 | 232000 | 3.71 | 164000 | 2.28 | R-410A | 17.1667
205234867 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* |  |  | RXYQ240XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 19.45 | 256000 | 3.61 | 182000 | 2.28 | R-410A | 19
205281447 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 |  |  |  | ARUM192BTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
205281450 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 |  |  |  | ARUM192DTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
203376873 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168YNU-A |  |  |  | PUHY-P168YNU-A | Ducted Indoor Units | 160000 | 11.2 | 23.4 | 178000 | 3.59 | 132000 | 2.55 | R-410A | 13.3333
203376884 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168TNU-A |  |  |  | PUHY-P168TNU-A | Ducted Indoor Units | 160000 | 11.2 | 23.4 | 178000 | 3.59 | 132000 | 2.55 | R-410A | 13.3333
203376896 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A |  |  |  | PUHY-EP192YNU-A | Ducted Indoor Units | 182000 | 10.7 | 23.1 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.1667
203376908 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A |  |  |  | PUHY-EP192TNU-A | Ducted Indoor Units | 182000 | 10.7 | 23.1 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.1667
203376962 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A |  |  |  | PUHY-EP192YNU-A | Non-Ducted Indoor Units | 182000 | 11.7 | 30 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.1667
203376971 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A |  |  |  | PUHY-EP192TNU-A | Non-Ducted Indoor Units | 182000 | 11.7 | 30 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.1667
203378323 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN40AN |  |  |  | TUHYE1923AN40AN | Ducted Indoor Units | 182000 | 10.7 | 23.1 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.1667
203378324 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN40AN |  |  |  | TUHYE1923AN40AN | Non-Ducted Indoor Units | 182000 | 11.7 | 30 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.1667
203378327 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN40AN |  |  |  | TUHYE1924AN40AN | Ducted Indoor Units | 182000 | 10.7 | 23.1 | 204000 | 3.51 | 144000 | 2.4 | R-410A | 15.1667
203378328 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN40AN |  |  |  | TUHYE1924AN40AN | Non-Ducted Indoor Units | 182000 | 11.7 | 30 | 204000 | 4.04 | 144000 | 2.6 | R-410A | 15.1667
203378391 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1683AN40AN |  |  |  | TUHYP1683AN40AN | Ducted Indoor Units | 160000 | 11.2 | 23.4 | 178000 | 3.59 | 132000 | 2.55 | R-410A | 13.3333
203378392 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1684AN40AN |  |  |  | TUHYP1684AN40AN | Ducted Indoor Units | 160000 | 11.2 | 23.4 | 178000 | 3.59 | 132000 | 2.55 | R-410A | 13.3333
203378434 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168YNU-A |  |  |  | PUHY-P168YNU-A | Non-Ducted Indoor Units | 160000 | 11.7 | 29.8 | 178000 | 4.02 | 132000 | 2.74 | R-410A | 13.3333
203378436 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168TNU-A |  |  |  | PUHY-P168TNU-A | Non-Ducted Indoor Units | 160000 | 11.7 | 29.8 | 178000 | 4.02 | 132000 | 2.74 | R-410A | 13.3333
203378441 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1683AN40AN |  |  |  | TUHYP1683AN40AN | Non-Ducted Indoor Units | 160000 | 11.7 | 29.8 | 178000 | 4.02 | 132000 | 2.74 | R-410A | 13.3333
203378442 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1684AN40AN |  |  |  | TUHYP1684AN40AN | Non-Ducted Indoor Units | 160000 | 11.7 | 29.8 | 178000 | 4.02 | 132000 | 2.74 | R-410A | 13.3333
203381079 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192TNU-A |  |  |  | PUHY-EP192TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 26.55 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.1667
203381081 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP192YNU-A |  |  |  | PUHY-EP192YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 26.55 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.1667
203381123 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168TNU-A |  |  |  | PUHY-P168TNU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.45 | 26.6 | 178000 | 3.8 | 132000 | 2.64 | R-410A | 13.3333
203381124 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P168YNU-A |  |  |  | PUHY-P168YNU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.45 | 26.6 | 178000 | 3.8 | 132000 | 2.64 | R-410A | 13.3333
203381177 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TKMU-A |  |  |  | PURY-P144TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.2 | 19 | 152000 | 3.31 | 109000 | 2.18 | R-410A | 11.3333
203381179 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TLMU-A |  |  |  | PURY-P144TLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.1 | 21.55 | 152000 | 3.52 | 97000 | 2.1 | R-410A | 11.3333
203381181 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72TLMU-A | PURY-P72TLMU-A |  |  | PURY-P144TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.25 | 22.65 | 152000 | 3.79 | 97000 | 2.17 | R-410A | 11.3333
203381182 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YKMU-A |  |  |  | PURY-P144YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.2 | 19 | 152000 | 3.31 | 109000 | 2.18 | R-410A | 11.3333
203381184 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YLMU-A |  |  |  | PURY-P144YLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.1 | 21.55 | 152000 | 3.52 | 97000 | 2.1 | R-410A | 11.3333
203381186 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YKMU-A | PURY-P72YKMU-A |  |  | PURY-P144YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.2 | 18.65 | 152000 | 3.56 | 109000 | 2.33 | R-410A | 11.3333
203381188 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P72YLMU-A | PURY-P72YLMU-A |  |  | PURY-P144YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.25 | 22.65 | 152000 | 3.79 | 97000 | 2.17 | R-410A | 11.3333
203381192 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A | PURY-P72TKMU-A |  |  | PURY-P168TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.5 | 18.35 | 178000 | 3.54 | 132000 | 2.36 | R-410A | 13.3333
203381194 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P72TLMU-A |  |  | PURY-P168TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.8 | 21.35 | 178000 | 3.55 | 119000 | 2.27 | R-410A | 13.3333
203381197 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A | PURY-P72YKMU-A |  |  | PURY-P168YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.5 | 18.35 | 178000 | 3.54 | 132000 | 2.36 | R-410A | 13.3333
203381199 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P72YLMU-A |  |  | PURY-P168YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.8 | 21.35 | 178000 | 3.55 | 119000 | 2.27 | R-410A | 13.3333
203381201 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TKMU-A | PURY-P96TKMU-A |  |  | PURY-P192TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 18 | 204000 | 3.53 | 150000 | 2.34 | R-410A | 15.1667
203381203 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96TLMU-A | PURY-P96TLMU-A |  |  | PURY-P192TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 22.8 | 204000 | 3.54 | 142000 | 2.17 | R-410A | 15.1667
203381205 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YKMU-A | PURY-P96YKMU-A |  |  | PURY-P192YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 18 | 204000 | 3.53 | 150000 | 2.34 | R-410A | 15.1667
203381207 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P96YLMU-A | PURY-P96YLMU-A |  |  | PURY-P192YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 22.8 | 204000 | 3.54 | 142000 | 2.17 | R-410A | 15.1667
203381212 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A | PURY-P96TLMU-A |  |  | PURY-P216TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 21.5 | 232000 | 3.53 | 158000 | 2.14 | R-410A | 17.1667
203381216 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A | PURY-P96YLMU-A |  |  | PURY-P216YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 21.5 | 232000 | 3.53 | 158000 | 2.14 | R-410A | 17.1667
203381221 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120TLMU-A | PURY-P120TLMU-A |  |  | PURY-P240TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.35 | 20.2 | 258000 | 3.52 | 174000 | 2.09 | R-410A | 19
203381225 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P120YLMU-A | PURY-P120YLMU-A |  |  | PURY-P240YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.35 | 20.2 | 258000 | 3.52 | 174000 | 2.09 | R-410A | 19
203381282 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1923AN40AN |  |  |  | TUHYE1923AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 26.55 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.1667
203381284 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1924AN40AN |  |  |  | TUHYE1924AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.2 | 26.55 | 204000 | 3.77 | 144000 | 2.5 | R-410A | 15.1667
203381326 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1683AN40AN |  |  |  | TUHYP1683AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.45 | 26.6 | 178000 | 3.8 | 132000 | 2.64 | R-410A | 13.3333
203381327 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1684AN40AN |  |  |  | TUHYP1684AN40AN | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.45 | 26.6 | 178000 | 3.8 | 132000 | 2.64 | R-410A | 13.3333
204442777 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH |  |  | AM144KXVTFH | Non-Ducted Indoor Units | 138000 | 13.3 | 29.8 | 154000 | 3.71 | 154000 | 2.15 | R-410A | 11.5
204442778 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH |  |  | AM192KXVTFH | Non-Ducted Indoor Units | 184000 | 13.1 | 29.1 | 206000 | 3.78 | 206000 | 2.15 | R-410A | 15.3333
204442779 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM072KXVTFH |  | AM216KXVTFH | Non-Ducted Indoor Units | 206000 | 13.3 | 28.3 | 230000 | 3.81 | 230000 | 2.12 | R-410A | 17.1667
204442780 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM096KXVTFH |  | AM240KXVTFH | Non-Ducted Indoor Units | 228000 | 13.4 | 28.5 | 258000 | 3.77 | 258000 | 2.11 | R-410A | 19
204442785 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH |  |  | AM144KXVTJH | Non-Ducted Indoor Units | 138000 | 13.3 | 29.8 | 154000 | 3.71 | 154000 | 2.15 | R-410A | 11.5
204442786 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH |  |  | AM192KXVTJH | Non-Ducted Indoor Units | 184000 | 13.1 | 29.1 | 206000 | 3.78 | 206000 | 2.15 | R-410A | 15.3333
204442787 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM072KXVTJH |  | AM216KXVTJH | Non-Ducted Indoor Units | 206000 | 13.3 | 28.3 | 230000 | 3.81 | 230000 | 2.12 | R-410A | 17.1667
204442788 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM096KXVTJH |  | AM240KXVTJH | Non-Ducted Indoor Units | 228000 | 13.4 | 28.5 | 258000 | 3.77 | 258000 | 2.11 | R-410A | 19
205749941 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME2CA* | MVHP096ME2CA* |  |  | MVHP168ME2CA* | Ducted Indoor Units | 161000 | 11.4 | 21.6 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
205749942 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME2CA* | MVHR096ME2CA* |  |  | MVHR168ME2CA* | Ducted Indoor Units | 161000 | 11.2 | 20.7 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
205749943 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME2CA* | MVHP096ME2CA* |  |  | MVHP192ME2CA* | Ducted Indoor Units | 184000 | 11.1 | 20.6 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
205749944 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME2CA* | MVHR096ME2CA* |  |  | MVHR192ME2CA* | Ducted Indoor Units | 184000 | 11.2 | 19.7 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
205749945 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME2CA* | MVHP096ME2CA* |  |  | MVHP216ME2CA* | Ducted Indoor Units | 207000 | 10.9 | 20.7 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
205749946 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME2CA* | MVHR096ME2CA* |  |  | MVHR216ME2CA* | Ducted Indoor Units | 207000 | 10.9 | 19.8 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
205749966 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME2CA* | MVHP096ME2CA* |  |  | MVHP168ME2CA* | Non-Ducted Indoor Units | 161000 | 11.6 | 22.6 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
205749967 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME2CA* | MVHR096ME2CA* |  |  | MVHR168ME2CA* | Non-Ducted Indoor Units | 161000 | 11.4 | 22 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
205749968 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME2CA* | MVHP096ME2CA* |  |  | MVHP192ME2CA* | Non-Ducted Indoor Units | 184000 | 11.6 | 21.4 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
205749969 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME2CA* | MVHR096ME2CA* |  |  | MVHR192ME2CA* | Non-Ducted Indoor Units | 184000 | 11.4 | 20.4 | 206000 | 3.4 | 138000 | 2.3 | R-410A | 15.3333
205749970 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME2CA* | MVHP096ME2CA* |  |  | MVHP216ME2CA* | Non-Ducted Indoor Units | 207000 | 11.5 | 20.9 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
205749971 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME2CA* | MVHR096ME2CA* |  |  | MVHR216ME2CA* | Non-Ducted Indoor Units | 207000 | 11.4 | 19.9 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
204442793 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR |  |  | AM144KXVTFR | Non-Ducted Indoor Units | 138000 | 13.3 | 29.8 | 154000 | 3.71 | 154000 | 2.15 | R-410A | 11.5
204442794 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR |  |  | AM192KXVTFR | Non-Ducted Indoor Units | 184000 | 13.1 | 29.1 | 206000 | 3.78 | 206000 | 2.15 | R-410A | 15.3333
204442807 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216KXVGJH |  |  |  | AM216KXVGJH | Non-Ducted Indoor Units | 206000 | 11 | 24.5 | 230000 | 3.82 | 150000 | 2.7 | R-410A | 17.1667
206568895 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP144ME4CA* |  |  |  | MVHP144ME4CA* | Ducted Indoor Units | 138000 | 11.7 | 21.8 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
206568896 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP144ME4CA* |  |  |  | MVHP144ME4CA* | Non-Ducted Indoor Units | 138000 | 11.6 | 22 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
206568897 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR144ME4CA* |  |  |  | MVHR144ME4CA* | Ducted Indoor Units | 138000 | 11 | 20.8 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
206568898 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR144ME4CA* |  |  |  | MVHR144ME4CA* | Non-Ducted Indoor Units | 138000 | 11.4 | 22 | 154000 | 3.5 | 108000 | 2.3 | R-410A | 11.5
206799435 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH |  |  |  | AM144FXVAFH | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
206799436 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR |  |  |  | AM144FXVAFR | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
206799437 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH |  |  |  | AM144FXVAJH | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
206799438 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR |  |  |  | AM144FXVAJR | Ducted Indoor Units | 138000 | 10.8 | 21 | 154000 | 3.44 | 100000 | 2.54 | R-410A | 11.5
206799439 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH |  |  | AM144KXVTFH | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
206799440 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR |  |  | AM144KXVTFR | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
206799441 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH |  |  | AM144KXVTJH | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
206799442 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR |  |  | AM144KXVTJR | Ducted Indoor Units | 138000 | 11.4 | 23 | 154000 | 3.6 | 154000 | 2.3 | R-410A | 11.5
206799447 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH |  |  | AM168KXVTFH | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
206799448 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR |  |  | AM168KXVTFR | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
206799449 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH |  |  | AM168KXVTJH | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
206799450 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR |  |  | AM168KXVTJR | Ducted Indoor Units | 160000 | 11.5 | 22.7 | 180000 | 3.6 | 180000 | 2.25 | R-410A | 13.3333
206799455 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH |  |  | AM192KXVTFH | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
206799456 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR |  |  | AM192KXVTFR | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
206799457 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH |  |  | AM192KXVTJH | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
206799458 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR |  |  | AM192KXVTJR | Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.55 | 206000 | 2.25 | R-410A | 15.3333
206799463 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216KXVGJH |  |  |  | AM216KXVGJH | Ducted Indoor Units | 206000 | 10.7 | 22.3 | 230000 | 3.62 | 150000 | 2.61 | R-410A | 17.1667
206799464 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216KXVGJR |  |  |  | AM216KXVGJR | Ducted Indoor Units | 206000 | 10.7 | 22.3 | 230000 | 3.62 | 150000 | 2.61 | R-410A | 17.1667
206799465 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM072KXVTFH |  | AM216KXVTFH | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
206799466 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM072KXVTFR |  | AM216KXVTFR | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
206799467 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM072KXVTJH |  | AM216KXVTJH | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
206799468 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM072KXVTJR |  | AM216KXVTJR | Ducted Indoor Units | 206000 | 11.3 | 21.4 | 230000 | 3.55 | 230000 | 2.15 | R-410A | 17.1667
206799473 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM072KXVTFH | AM096KXVTFH |  | AM240KXVTFH | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
206799474 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM096KXVTFR |  | AM240KXVTFR | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
206799475 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM072KXVTJH | AM096KXVTJH |  | AM240KXVTJH | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
206799476 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM096KXVTJR |  | AM240KXVTJR | Ducted Indoor Units | 228000 | 11.4 | 21 | 258000 | 3.53 | 258000 | 2.15 | R-410A | 19
207168488 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME4CA* | MVHP096ME4CA* |  |  | MVHP168ME4CA* | Ducted Indoor Units | 161000 | 11.4 | 21.6 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
207168489 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP072ME4CA* | MVHP096ME4CA* |  |  | MVHP168ME4CA* | Non-Ducted Indoor Units | 161000 | 11.6 | 22.6 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
207168490 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME4CA* | MVHR096ME4CA* |  |  | MVHR168ME4CA* | Ducted Indoor Units | 161000 | 11.2 | 20.7 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
207168491 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR072ME4CA* | MVHR096ME4CA* |  |  | MVHR168ME4CA* | Non-Ducted Indoor Units | 161000 | 11.4 | 22 | 180000 | 3.4 | 126000 | 2.3 | R-410A | 13.4167
207168492 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME4CA* | MVHP096ME4CA* |  |  | MVHP192ME4CA* | Ducted Indoor Units | 184000 | 11.1 | 20.6 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
207168493 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP096ME4CA* | MVHP096ME4CA* |  |  | MVHP192ME4CA* | Non-Ducted Indoor Units | 184000 | 11.6 | 21.4 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
207168494 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME4CA* | MVHR096ME4CA* |  |  | MVHR192ME4CA* | Ducted Indoor Units | 184000 | 11.2 | 19.7 | 206000 | 3.3 | 138000 | 2.3 | R-410A | 15.3333
207168495 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR096ME4CA* | MVHR096ME4CA* |  |  | MVHR192ME4CA* | Non-Ducted Indoor Units | 184000 | 11.4 | 20.4 | 206000 | 3.4 | 138000 | 2.3 | R-410A | 15.3333
207168496 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME4CA* | MVHP096ME4CA* |  |  | MVHP216ME4CA* | Ducted Indoor Units | 207000 | 10.9 | 20.7 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
207168497 | 1/1/2027 | HAIER | HMSV-A-CB | MVHP120ME4CA* | MVHP096ME4CA* |  |  | MVHP216ME4CA* | Non-Ducted Indoor Units | 207000 | 11.5 | 20.9 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
207168498 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME4CA* | MVHR096ME4CA* |  |  | MVHR216ME4CA* | Ducted Indoor Units | 207000 | 10.9 | 19.8 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
207168499 | 1/1/2027 | HAIER | HMSR-A-CB | MVHR120ME4CA* | MVHR096ME4CA* |  |  | MVHR216ME4CA* | Non-Ducted Indoor Units | 207000 | 11.4 | 19.9 | 232000 | 3.3 | 156000 | 2.3 | R-410A | 17.25
200084155 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 228000 | 11.2 | 22.4 | 256000 | 3.71 | 172000 | 2.48 | R-410A | 19
200084156 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Non-Ducted Indoor Units | 228000 | 11.2 | 22.4 | 256000 | 3.71 | 172000 | 2.48 | R-410A | 19
200084157 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Ducted Indoor Units | 228000 | 11 | 21.1 | 256000 | 3.57 | 172000 | 2.39 | R-410A | 19
200084158 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Ducted Indoor Units | 228000 | 11 | 21.1 | 256000 | 3.57 | 172000 | 2.39 | R-410A | 19
200084159 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 21.75 | 256000 | 3.64 | 172000 | 2.43 | R-410A | 19
200084160 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA240RDL6-1 |  |  |  | 38VMA240RDL6-1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 21.75 | 256000 | 3.64 | 172000 | 2.43 | R-410A | 19
201847125 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA072H4M-2G |  |  | VPA168H4M-2G | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201847126 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA072H4M-2G |  |  | VPA168H4M-2G | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201847127 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA072H4M-2Y |  |  | VPA168H4M-2Y | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201847128 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA072H4M-2Y |  |  | VPA168H4M-2Y | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201847129 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA096H4M-2G |  |  | VPA192H4M-2G | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201847130 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA096H4M-2G |  |  | VPA192H4M-2G | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201847131 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA096H4M-2Y |  |  | VPA192H4M-2Y | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201847132 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA096H4M-2Y |  |  | VPA192H4M-2Y | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201847133 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G |  |  | VPA216H4M-2G | Non-Ducted Indoor Units | 206000 | 11.4 | 20.4 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
201847134 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G |  |  | VPA216H4M-2G | Ducted Indoor Units | 206000 | 11.1 | 20.9 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
201847135 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y |  |  | VPA216H4M-2Y | Non-Ducted Indoor Units | 206000 | 11.4 | 20.4 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
201847136 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y |  |  | VPA216H4M-2Y | Ducted Indoor Units | 206000 | 11.1 | 20.9 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
201847137 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA120H4M-2G |  |  | VPA240H4M-2G | Non-Ducted Indoor Units | 230000 | 11.2 | 20.1 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
201847138 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA120H4M-2G |  |  | VPA240H4M-2G | Ducted Indoor Units | 230000 | 10.7 | 20.3 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
201847139 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA120H4M-2Y |  |  | VPA240H4M-2Y | Non-Ducted Indoor Units | 230000 | 11.2 | 20.1 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
201847140 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA120H4M-2Y |  |  | VPA240H4M-2Y | Ducted Indoor Units | 230000 | 10.7 | 20.3 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
201847185 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA072H4M-2Y |  |  | VRA168H4M-2Y | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201847186 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA072H4M-2Y |  |  | VRA168H4M-2Y | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201847187 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA072H4M-2G |  |  | VRA168H4M-2G | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201847188 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA072H4M-2G |  |  | VRA168H4M-2G | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201847189 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA096H4M-2Y |  |  | VRA192H4M-2Y | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201847190 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA096H4M-2Y |  |  | VRA192H4M-2Y | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201847191 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA096H4M-2G |  |  | VRA192H4M-2G | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201847192 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA096H4M-2G |  |  | VRA192H4M-2G | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201847193 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y |  |  | VRA216H4M-2Y | Non-Ducted Indoor Units | 206000 | 11.6 | 20.7 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
201847194 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y |  |  | VRA216H4M-2Y | Ducted Indoor Units | 206000 | 11.1 | 21 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
201847195 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G |  |  | VRA216H4M-2G | Non-Ducted Indoor Units | 206000 | 11.6 | 20.7 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
201847196 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G |  |  | VRA216H4M-2G | Ducted Indoor Units | 206000 | 11.1 | 21 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
201847197 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA120H4M-2Y |  |  | VRA240H4M-2Y | Non-Ducted Indoor Units | 230000 | 11.3 | 20.5 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
201847198 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA120H4M-2Y |  |  | VRA240H4M-2Y | Ducted Indoor Units | 230000 | 10.8 | 20.6 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
201847199 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA120H4M-2G |  |  | VRA240H4M-2G | Non-Ducted Indoor Units | 230000 | 11.3 | 20.5 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
201847200 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA120H4M-2G |  |  | VRA240H4M-2G | Ducted Indoor Units | 230000 | 10.8 | 20.6 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
201856724 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DXN1-(A) | MV5-RC72DXN1-(A) |  |  | MV5-RC144DXN1-(A) | Non-Ducted Indoor Units | 138000 | 12 | 22.6 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201856725 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DXN1-(A) | MV5-RC72DXN1-(A) |  |  | MV5-RC144DXN1-(A) | Ducted Indoor Units | 138000 | 11.1 | 20.8 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201856726 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  |  | MV5-RC168DXN1-(A) | Non-Ducted Indoor Units | 160000 | 11.7 | 22.2 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201856727 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  |  | MV5-RC168DXN1-(A) | Ducted Indoor Units | 160000 | 11 | 20.6 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201856728 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) |  |  | MV5-RC192DXN1-(A) | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201856729 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) |  |  | MV5-RC192DXN1-(A) | Ducted Indoor Units | 184000 | 10.9 | 20.6 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201856730 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) |  |  | MV5-RC216DXN1-(A) | Non-Ducted Indoor Units | 206000 | 11.4 | 20.7 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201856731 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) |  |  | MV5-RC216DXN1-(A) | Ducted Indoor Units | 206000 | 10.8 | 20.6 | 224000 | 3.45 | 152000 | 2.23 | R-410A | 17.1667
201856732 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC120DXN1-(A) |  |  | MV5-RC240DXN1-(A) | Non-Ducted Indoor Units | 230000 | 11.3 | 20.1 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201856748 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DZN1-(A) | MV5-RC72DZN1-(A) |  |  | MV5-RC144DZN1-(A) | Non-Ducted Indoor Units | 138000 | 12 | 22.6 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201856749 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC72DZN1-(A) | MV5-RC72DZN1-(A) |  |  | MV5-RC144DZN1-(A) | Ducted Indoor Units | 138000 | 11.1 | 20.8 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201856750 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  |  | MV5-RC168DZN1-(A) | Non-Ducted Indoor Units | 160000 | 11.7 | 22.2 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201856751 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  |  | MV5-RC168DZN1-(A) | Ducted Indoor Units | 160000 | 11 | 20.6 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201856752 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) |  |  | MV5-RC192DZN1-(A) | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201856753 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) |  |  | MV5-RC192DZN1-(A) | Ducted Indoor Units | 184000 | 10.9 | 20.6 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201856754 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) |  |  | MV5-RC216DZN1-(A) | Non-Ducted Indoor Units | 206000 | 11.4 | 20.7 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201856755 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) |  |  | MV5-RC216DZN1-(A) | Ducted Indoor Units | 206000 | 10.8 | 20.6 | 224000 | 3.45 | 152000 | 2.23 | R-410A | 17.1667
201856756 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC120DZN1-(A) |  |  | MV5-RC240DZN1-(A) | Non-Ducted Indoor Units | 230000 | 11.3 | 20.1 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201856772 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DXN1-(A) | MV5-XC72DXN1-(A) |  |  | MV5-XC144DXN1-(A) | Non-Ducted Indoor Units | 138000 | 11.9 | 22.1 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201856773 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DXN1-(A) | MV5-XC72DXN1-(A) |  |  | MV5-XC144DXN1-(A) | Ducted Indoor Units | 138000 | 10.9 | 20.4 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201856774 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  |  | MV5-XC168DXN1-(A) | Non-Ducted Indoor Units | 160000 | 11.5 | 21.7 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201856775 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  |  | MV5-XC168DXN1-(A) | Ducted Indoor Units | 160000 | 10.8 | 20.2 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201856776 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC96DXN1-(A) |  |  | MV5-XC192DXN1-(A) | Non-Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201856777 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC96DXN1-(A) |  |  | MV5-XC192DXN1-(A) | Ducted Indoor Units | 184000 | 10.7 | 20.2 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201856778 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) | MV5-XC96DXN1-(A) |  |  | MV5-XC216DXN1-(A) | Non-Ducted Indoor Units | 206000 | 11.2 | 20.2 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201856780 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) | MV5-XC120DXN1-(A) |  |  | MV5-XC240DXN1-(A) | Non-Ducted Indoor Units | 230000 | 11.1 | 19.7 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201856794 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DZN1-(A) | MV5-XC72DZN1-(A) |  |  | MV5-XC144DZN1-(A) | Non-Ducted Indoor Units | 138000 | 11.9 | 22.1 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201856795 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC72DZN1-(A) | MV5-XC72DZN1-(A) |  |  | MV5-XC144DZN1-(A) | Ducted Indoor Units | 138000 | 10.9 | 20.4 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201856796 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  |  | MV5-XC168DZN1-(A) | Non-Ducted Indoor Units | 160000 | 11.5 | 21.7 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201856797 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  |  | MV5-XC168DZN1-(A) | Ducted Indoor Units | 160000 | 10.8 | 20.2 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201856798 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC96DZN1-(A) |  |  | MV5-XC192DZN1-(A) | Non-Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201856799 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC96DZN1-(A) |  |  | MV5-XC192DZN1-(A) | Ducted Indoor Units | 184000 | 10.7 | 20.2 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201856800 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) | MV5-XC96DZN1-(A) |  |  | MV5-XC216DZN1-(A) | Non-Ducted Indoor Units | 206000 | 11.2 | 20.2 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201856802 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) | MV5-XC120DZN1-(A) |  |  | MV5-XC240DZN1-(A) | Non-Ducted Indoor Units | 230000 | 11.1 | 19.7 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201862860 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2Y | VRA072L4M-2Y |  |  | VRA144L4M-2Y | Non-Ducted Indoor Units | 138000 | 12 | 22.6 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201862861 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2Y | VRA072L4M-2Y |  |  | VRA144L4M-2Y | Ducted Indoor Units | 138000 | 11.1 | 20.8 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201862862 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA072L4M-2Y |  |  | VRA168L4M-2Y | Non-Ducted Indoor Units | 160000 | 11.7 | 22.2 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201862863 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA072L4M-2Y |  |  | VRA168L4M-2Y | Ducted Indoor Units | 160000 | 11 | 20.6 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201862864 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA096L4M-2Y |  |  | VRA192L4M-2Y | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201862865 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA096L4M-2Y |  |  | VRA192L4M-2Y | Ducted Indoor Units | 184000 | 10.9 | 20.6 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201862866 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y |  |  | VRA216L4M-2Y | Non-Ducted Indoor Units | 206000 | 11.4 | 20.7 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201862867 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y |  |  | VRA216L4M-2Y | Ducted Indoor Units | 206000 | 10.8 | 20.6 | 224000 | 3.45 | 152000 | 2.23 | R-410A | 17.1667
201862868 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA120L4M-2Y |  |  | VRA240L4M-2Y | Non-Ducted Indoor Units | 230000 | 11.3 | 20.1 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201862884 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2G | VRA072L4M-2G |  |  | VRA144L4M-2G | Non-Ducted Indoor Units | 138000 | 12 | 22.6 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201862885 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA072L4M-2G | VRA072L4M-2G |  |  | VRA144L4M-2G | Ducted Indoor Units | 138000 | 11.1 | 20.8 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201862886 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA072L4M-2G |  |  | VRA168L4M-2G | Non-Ducted Indoor Units | 160000 | 11.7 | 22.2 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201862887 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA072L4M-2G |  |  | VRA168L4M-2G | Ducted Indoor Units | 160000 | 11 | 20.6 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201862888 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA096L4M-2G |  |  | VRA192L4M-2G | Non-Ducted Indoor Units | 184000 | 11.5 | 21.6 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201862889 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA096L4M-2G |  |  | VRA192L4M-2G | Ducted Indoor Units | 184000 | 10.9 | 20.6 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201862890 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G |  |  | VRA216L4M-2G | Non-Ducted Indoor Units | 206000 | 11.4 | 20.7 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201862891 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G |  |  | VRA216L4M-2G | Ducted Indoor Units | 206000 | 10.8 | 20.6 | 224000 | 3.45 | 152000 | 2.23 | R-410A | 17.1667
201862892 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA120L4M-2G |  |  | VRA240L4M-2G | Non-Ducted Indoor Units | 230000 | 11.3 | 20.1 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201862908 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2Y | VPA072L4M-2Y |  |  | VPA144L4M-2Y | Non-Ducted Indoor Units | 138000 | 11.9 | 22.1 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201862909 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2Y | VPA072L4M-2Y |  |  | VPA144L4M-2Y | Ducted Indoor Units | 138000 | 10.9 | 20.4 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201862910 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA072L4M-2Y |  |  | VPA168L4M-2Y | Non-Ducted Indoor Units | 160000 | 11.5 | 21.7 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201862911 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA072L4M-2Y |  |  | VPA168L4M-2Y | Ducted Indoor Units | 160000 | 10.8 | 20.2 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201862912 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA096L4M-2Y |  |  | VPA192L4M-2Y | Non-Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201862913 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA096L4M-2Y |  |  | VPA192L4M-2Y | Ducted Indoor Units | 184000 | 10.7 | 20.2 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201862914 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y | VPA096L4M-2Y |  |  | VPA216L4M-2Y | Non-Ducted Indoor Units | 206000 | 11.2 | 20.2 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201862916 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y | VPA120L4M-2Y |  |  | VPA240L4M-2Y | Non-Ducted Indoor Units | 230000 | 11.1 | 19.7 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201862930 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2G | VPA072L4M-2G |  |  | VPA144L4M-2G | Non-Ducted Indoor Units | 138000 | 11.9 | 22.1 | 154000 | 3.75 | 108000 | 2.58 | R-410A | 11.5
201862931 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA072L4M-2G | VPA072L4M-2G |  |  | VPA144L4M-2G | Ducted Indoor Units | 138000 | 10.9 | 20.4 | 154000 | 3.62 | 108000 | 2.34 | R-410A | 11.5
201862932 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA072L4M-2G |  |  | VPA168L4M-2G | Non-Ducted Indoor Units | 160000 | 11.5 | 21.7 | 180000 | 3.71 | 126000 | 2.47 | R-410A | 13.3333
201862933 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA072L4M-2G |  |  | VPA168L4M-2G | Ducted Indoor Units | 160000 | 10.8 | 20.2 | 180000 | 3.6 | 126000 | 2.29 | R-410A | 13.3333
201862934 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA096L4M-2G |  |  | VPA192L4M-2G | Non-Ducted Indoor Units | 184000 | 11.3 | 21.1 | 206000 | 3.62 | 144000 | 2.35 | R-410A | 15.3333
201862935 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA096L4M-2G |  |  | VPA192L4M-2G | Ducted Indoor Units | 184000 | 10.7 | 20.2 | 206000 | 3.52 | 144000 | 2.23 | R-410A | 15.3333
201862936 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G | VPA096L4M-2G |  |  | VPA216L4M-2G | Non-Ducted Indoor Units | 206000 | 11.2 | 20.2 | 224000 | 3.58 | 152000 | 2.28 | R-410A | 17.1667
201862938 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G | VPA120L4M-2G |  |  | VPA240L4M-2G | Non-Ducted Indoor Units | 230000 | 11.1 | 19.7 | 240000 | 3.56 | 160000 | 2.28 | R-410A | 19.1667
201863369 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X72DXN1-(A) |  |  | MV5-X168DXN1-(A)* | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201863370 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X72DXN1-(A) |  |  | MV5-X168DXN1-(A)* | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201863371 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X192DXN1-(A)* | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201863372 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X192DXN1-(A)* | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201863375 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X72DZN1-(A) |  |  | MV5-X168DZN1-(A)* | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201863376 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X72DZN1-(A) |  |  | MV5-X168DZN1-(A)* | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201863377 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X192DZN1-(A)* | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201863378 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X192DZN1-(A)* | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201863381 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R72DXN1-(A) |  |  | MV5-R168DXN1-(A)* | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201863382 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R72DXN1-(A) |  |  | MV5-R168DXN1-(A)* | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201863383 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R192DXN1-(A)* | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201863384 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R192DXN1-(A)* | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
201863387 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R72DZN1-(A) |  |  | MV5-R168DZN1-(A)* | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
201863388 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R72DZN1-(A) |  |  | MV5-R168DZN1-(A)* | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
201863389 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R192DZN1-(A)* | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
201863390 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R192DZN1-(A)* | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
10611537 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X72DXN1-(A) |  |  | MV5-X168DXN1-(A) | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
10611538 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X72DXN1-(A) |  |  | MV5-X168DXN1-(A) | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
10611539 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X192DXN1-(A) | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
10611540 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X192DXN1-(A) | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
10611541 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X216DXN1-(A) | Non-Ducted Indoor Units | 206000 | 11.4 | 20.4 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
10611542 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X216DXN1-(A) | Ducted Indoor Units | 206000 | 11.1 | 20.9 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
10611543 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) |  |  | MV5-X240DXN1-(A) | Non-Ducted Indoor Units | 230000 | 11.2 | 20.1 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
10611544 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) |  |  | MV5-X240DXN1-(A) | Ducted Indoor Units | 230000 | 10.7 | 20.3 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
10611551 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X72DZN1-(A) |  |  | MV5-X168DZN1-(A) | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
10611552 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X72DZN1-(A) |  |  | MV5-X168DZN1-(A) | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
10611553 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X192DZN1-(A) | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
10611554 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X192DZN1-(A) | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
10611555 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X216DZN1-(A) | Non-Ducted Indoor Units | 206000 | 11.4 | 20.4 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
10611556 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X216DZN1-(A) | Ducted Indoor Units | 206000 | 11.1 | 20.9 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
10611557 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) |  |  | MV5-X240DZN1-(A) | Non-Ducted Indoor Units | 230000 | 11.2 | 20.1 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
10611558 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) |  |  | MV5-X240DZN1-(A) | Ducted Indoor Units | 230000 | 10.7 | 20.3 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
10611572 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R72DXN1-(A) |  |  | MV5-R168DXN1-(A) | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
10611573 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R72DXN1-(A) |  |  | MV5-R168DXN1-(A) | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
10611574 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R192DXN1-(A) | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
10611575 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R192DXN1-(A) | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
10611576 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R216DXN1-(A) | Non-Ducted Indoor Units | 206000 | 11.6 | 20.7 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
10611577 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R216DXN1-(A) | Ducted Indoor Units | 206000 | 11.1 | 21 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
10611578 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) |  |  | MV5-R240DXN1-(A) | Non-Ducted Indoor Units | 230000 | 11.3 | 20.5 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
10611579 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) |  |  | MV5-R240DXN1-(A) | Ducted Indoor Units | 230000 | 10.8 | 20.6 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
10611596 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R72DZN1-(A) |  |  | MV5-R168DZN1-(A) | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
10611597 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R72DZN1-(A) |  |  | MV5-R168DZN1-(A) | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
10611598 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R192DZN1-(A) | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
10611599 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R192DZN1-(A) | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
10611600 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R216DZN1-(A) | Non-Ducted Indoor Units | 206000 | 11.6 | 20.7 | 224000 | 3.5 | 152000 | 2.25 | R-410A | 17.1667
10611601 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R216DZN1-(A) | Ducted Indoor Units | 206000 | 11.1 | 21 | 224000 | 3.54 | 152000 | 2.25 | R-410A | 17.1667
10611602 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) |  |  | MV5-R240DZN1-(A) | Non-Ducted Indoor Units | 230000 | 11.3 | 20.5 | 240000 | 3.49 | 160000 | 2.25 | R-410A | 19.1667
10611603 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) |  |  | MV5-R240DZN1-(A) | Ducted Indoor Units | 230000 | 10.8 | 20.6 | 240000 | 3.44 | 160000 | 2.25 | R-410A | 19.1667
10611620 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X72DXN1-(A) |  |  | MV5-X168DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.69 | 126000 | 2.42 | R-410A | 13.3333
10611621 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X192DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 22.15 | 206000 | 3.67 | 144000 | 2.35 | R-410A | 15.3333
10611622 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  |  | MV5-X216DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.25 | 20.65 | 224000 | 3.52 | 152000 | 2.25 | R-410A | 17.1667
10611623 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) |  |  | MV5-X240DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.95 | 20.2 | 240000 | 3.46 | 160000 | 2.25 | R-410A | 19.1667
10611635 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X72DZN1-(A) |  |  | MV5-X168DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.69 | 126000 | 2.42 | R-410A | 13.3333
10611636 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X192DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 22.15 | 206000 | 3.67 | 144000 | 2.35 | R-410A | 15.3333
10611637 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  |  | MV5-X216DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.25 | 20.65 | 224000 | 3.52 | 152000 | 2.25 | R-410A | 17.1667
10611638 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) |  |  | MV5-X240DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.95 | 20.2 | 240000 | 3.46 | 160000 | 2.25 | R-410A | 19.1667
10612354 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R72DXN1-(A) |  |  | MV5-R168DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.25 | 22.8 | 180000 | 3.69 | 126000 | 2.42 | R-410A | 13.3333
10612355 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R192DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 22.65 | 206000 | 3.67 | 144000 | 2.35 | R-410A | 15.3333
10612356 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  |  | MV5-R216DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.35 | 20.85 | 224000 | 3.52 | 152000 | 2.25 | R-410A | 17.1667
10612357 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) |  |  | MV5-R240DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.05 | 20.55 | 240000 | 3.46 | 160000 | 2.25 | R-410A | 19.1667
10612366 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R72DZN1-(A) |  |  | MV5-R168DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.25 | 22.8 | 180000 | 3.69 | 126000 | 2.42 | R-410A | 13.3333
10612367 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R192DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 22.65 | 206000 | 3.67 | 144000 | 2.35 | R-410A | 15.3333
10612368 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  |  | MV5-R216DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.35 | 20.85 | 224000 | 3.52 | 152000 | 2.25 | R-410A | 17.1667
10612369 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) |  |  | MV5-R240DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.05 | 20.55 | 240000 | 3.46 | 160000 | 2.25 | R-410A | 19.1667
10612400 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
10612401 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
10612402 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
10612403 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Ducted Indoor Units | 160000 | 10.9 | 19 | 180000 | 3.63 | 132000 | 2.64 | R-410A | 13.3333
10612404 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
10612405 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Ducted Indoor Units | 160000 | 10.9 | 19 | 180000 | 3.63 | 132000 | 2.64 | R-410A | 13.3333
10612406 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Ducted Indoor Units | 184000 | 12.2 | 20.3 | 206000 | 4 | 150000 | 2.88 | R-410A | 15.3333
10612407 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Ducted Indoor Units | 184000 | 12.2 | 20.3 | 206000 | 4 | 150000 | 2.88 | R-410A | 15.3333
10612408 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Ducted Indoor Units | 184000 | 11.9 | 19.9 | 206000 | 3.83 | 150000 | 2.74 | R-410A | 15.3333
10612409 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Ducted Indoor Units | 184000 | 11.9 | 19.9 | 206000 | 3.83 | 150000 | 2.74 | R-410A | 15.3333
10612410 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
10612411 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Ducted Indoor Units | 230000 | 12.1 | 20.6 | 256000 | 3.95 | 182000 | 2.91 | R-410A | 19.1667
10612412 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Ducted Indoor Units | 230000 | 12.1 | 20.6 | 256000 | 3.95 | 182000 | 2.91 | R-410A | 19.1667
10612413 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Ducted Indoor Units | 230000 | 12 | 20.3 | 256000 | 3.9 | 182000 | 2.86 | R-410A | 19.1667
10612414 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Ducted Indoor Units | 230000 | 12 | 20.3 | 256000 | 3.9 | 182000 | 2.86 | R-410A | 19.1667
10612453 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Ducted Indoor Units | 138000 | 11.3 | 20 | 154000 | 3.91 | 109000 | 2.78 | R-410A | 11.5
10612454 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Ducted Indoor Units | 138000 | 11.3 | 20 | 154000 | 3.91 | 109000 | 2.78 | R-410A | 11.5
10612455 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.85 | 22.8 | 154000 | 4.01 | 109000 | 2.75 | R-410A | 11.5
10612456 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.05 | 154000 | 3.63 | 109000 | 2.54 | R-410A | 11.5
10612457 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.05 | 154000 | 3.63 | 109000 | 2.54 | R-410A | 11.5
10612458 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.85 | 22.85 | 154000 | 3.67 | 109000 | 2.59 | R-410A | 11.5
10612459 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 21.4 | 180000 | 3.68 | 132000 | 2.56 | R-410A | 13.3333
10612460 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.95 | 21.4 | 180000 | 3.68 | 132000 | 2.56 | R-410A | 13.3333
10612463 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
10612464 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
10612465 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 4.02 | 150000 | 2.82 | R-410A | 15.3333
10612466 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
10612467 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
10612468 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.25 | 22.5 | 206000 | 3.89 | 150000 | 2.71 | R-410A | 15.3333
10612469 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.85 | 23.25 | 206000 | 3.68 | 150000 | 2.47 | R-410A | 15.3333
10612470 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.85 | 23.25 | 206000 | 3.68 | 150000 | 2.47 | R-410A | 15.3333
10612471 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 22.6 | 206000 | 3.58 | 150000 | 2.42 | R-410A | 15.3333
10612472 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.5 | 22.6 | 206000 | 3.58 | 150000 | 2.42 | R-410A | 15.3333
10612473 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Ducted Indoor Units | 206000 | 12.1 | 20.3 | 232000 | 3.93 | 164000 | 2.86 | R-410A | 17.1667
10612474 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.45 | 232000 | 3.91 | 164000 | 2.8 | R-410A | 17.1667
10612475 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.35 | 232000 | 3.65 | 164000 | 2.45 | R-410A | 17.1667
10612476 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.4 | 22.35 | 232000 | 3.65 | 164000 | 2.45 | R-410A | 17.1667
10612477 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
10612478 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
10612479 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.05 | 22.35 | 256000 | 3.85 | 182000 | 2.78 | R-410A | 19.1667
10612480 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
10612481 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
10612482 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.8 | 21.95 | 256000 | 3.8 | 182000 | 2.74 | R-410A | 19.1667
10612483 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.45 | 22.05 | 256000 | 3.58 | 182000 | 2.5 | R-410A | 19.1667
10612484 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.45 | 22.05 | 256000 | 3.58 | 182000 | 2.5 | R-410A | 19.1667
10612563 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.85 | 22.8 | 154000 | 4.01 | 109000 | 2.75 | R-410A | 11.5
10612564 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Non-Ducted Indoor Units | 138000 | 12.2 | 25.9 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
10612565 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Ducted Indoor Units | 138000 | 11.4 | 20.2 | 154000 | 3.52 | 109000 | 2.48 | R-410A | 11.5
10612566 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Non-Ducted Indoor Units | 138000 | 12.2 | 25.9 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
10612567 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Ducted Indoor Units | 138000 | 11.4 | 20.2 | 154000 | 3.52 | 109000 | 2.48 | R-410A | 11.5
10612568 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Non-Ducted Indoor Units | 138000 | 13.5 | 25.7 | 154000 | 3.77 | 109000 | 2.65 | R-410A | 11.5
10612569 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Ducted Indoor Units | 138000 | 12.2 | 20 | 154000 | 3.57 | 109000 | 2.54 | R-410A | 11.5
10612570 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL |  |  |  | MMY-MAP1686FT6P-UL | Non-Ducted Indoor Units | 160000 | 10.7 | 23.3 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
10612572 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL |  |  |  | MMY-MAP1686FT9P-UL | Non-Ducted Indoor Units | 160000 | 10.7 | 23.3 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
10612574 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 206000 | 4.02 | 150000 | 2.82 | R-410A | 15.3333
10612575 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.25 | 22.5 | 206000 | 3.89 | 150000 | 2.71 | R-410A | 15.3333
10612576 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Non-Ducted Indoor Units | 184000 | 12.2 | 26.1 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
10612577 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Ducted Indoor Units | 184000 | 11.5 | 20.4 | 206000 | 3.67 | 150000 | 2.45 | R-410A | 15.3333
10612578 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Non-Ducted Indoor Units | 184000 | 12.2 | 26.1 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
10612579 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Ducted Indoor Units | 184000 | 11.5 | 20.4 | 206000 | 3.67 | 150000 | 2.45 | R-410A | 15.3333
10612580 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Non-Ducted Indoor Units | 184000 | 11.7 | 25.3 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
10612581 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Ducted Indoor Units | 184000 | 11.3 | 19.9 | 206000 | 3.57 | 150000 | 2.4 | R-410A | 15.3333
10612582 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Non-Ducted Indoor Units | 184000 | 11.7 | 25.3 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
10612583 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Ducted Indoor Units | 184000 | 11.3 | 19.9 | 206000 | 3.57 | 150000 | 2.4 | R-410A | 15.3333
10612584 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Non-Ducted Indoor Units | 206000 | 11.6 | 24.2 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
10612585 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Ducted Indoor Units | 206000 | 11.2 | 20.5 | 232000 | 3.74 | 164000 | 2.44 | R-410A | 17.1667
10612586 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Non-Ducted Indoor Units | 206000 | 11.6 | 24.2 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
10612587 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Ducted Indoor Units | 206000 | 11.2 | 20.5 | 232000 | 3.74 | 164000 | 2.44 | R-410A | 17.1667
10612588 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.05 | 22.35 | 256000 | 3.85 | 182000 | 2.78 | R-410A | 19.1667
10612589 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.8 | 21.95 | 256000 | 3.8 | 182000 | 2.74 | R-410A | 19.1667
10612590 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.3 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
10612591 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Ducted Indoor Units | 230000 | 11.3 | 20.8 | 256000 | 3.56 | 182000 | 2.47 | R-410A | 19.1667
10612592 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.3 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
10612593 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Ducted Indoor Units | 230000 | 11.3 | 20.8 | 256000 | 3.56 | 182000 | 2.47 | R-410A | 19.1667
10612594 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP240S6FT6P-UL | Non-Ducted Indoor Units | 230000 | 10.7 | 22.8 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
10612596 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP240S6FT9P-UL | Non-Ducted Indoor Units | 230000 | 10.7 | 22.8 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
10612663 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
10612664 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Ducted Indoor Units | 206000 | 12.1 | 20.3 | 232000 | 3.93 | 164000 | 2.86 | R-410A | 17.1667
10612707 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.05 | 22.45 | 232000 | 3.91 | 164000 | 2.8 | R-410A | 17.1667
201977973 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  |  | PUHY-P216YSKMU-A | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
201977974 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  |  | PUHY-P216TSKMU-A | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
201978073 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TKMU-A |  |  |  | PUHY-P144TKMU-A | Non-Ducted Indoor Units | 136000 | 11.8 | 20.2 | 152000 | 3.72 | 109000 | 2.22 | R-410A | 11.3333
201978074 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YKMU-A |  |  |  | PUHY-P144YKMU-A | Non-Ducted Indoor Units | 136000 | 11.8 | 20.2 | 152000 | 3.72 | 109000 | 2.22 | R-410A | 11.3333
201978075 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P144YSKMU-A | Non-Ducted Indoor Units | 136000 | 13.2 | 20.3 | 152000 | 3.95 | 109000 | 2.13 | R-410A | 11.3333
201978076 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P168TSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
201978077 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P168YSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
201978078 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P192TSKMU-A | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
201978079 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P192YSKMU-A | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
201992875 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYC* |  |  |  | RXYQ144TAYC* | Non-Ducted Indoor Units | 138000 | 11.5 | 22.2 | 154000 | 3.84 | 109000 | 2.2 | R-410A | 11.5
202016259 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ120TAYC* |  |  | RXYQ216TAYC* | Non-Ducted Indoor Units | 206000 | 11.8 | 21.7 | 232000 | 3.84 | 164000 | 2.35 | R-410A | 17.1667
202016261 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* |  |  | RXYQ240TAYC* | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 256000 | 3.77 | 182000 | 2.39 | R-410A | 19
202016269 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* | RXLQ96TAYC* |  |  | RXLQ192TAYC* | Non-Ducted Indoor Units | 184000 | 12.3 | 22 | 206000 | 3.9 | 176000 | 2.22 | R-410A | 15.3333
202016271 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* | RXLQ120TAYC* |  |  | RXLQ240TAYC* | Non-Ducted Indoor Units | 228000 | 12.1 | 21 | 256000 | 3.77 | 218000 | 2.22 | R-410A | 19
202021854 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ96TAYC* |  |  | RXYQ192TAYC* | Non-Ducted Indoor Units | 184000 | 12.4 | 21.9 | 206000 | 3.91 | 150000 | 2.52 | R-410A | 15.3333
202021855 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* | RXLQ72TAYC* |  |  | RXLQ144TAYC* | Non-Ducted Indoor Units | 138000 | 12.7 | 22.4 | 154000 | 3.86 | 131000 | 2.21 | R-410A | 11.5
202021856 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* | RXLQ96TATJ* |  |  | RXLQ192TATJ* | Non-Ducted Indoor Units | 184000 | 12.3 | 22 | 206000 | 3.9 | 176000 | 2.22 | R-410A | 15.3333
202021857 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* | RXLQ96TAYD* |  |  | RXLQ192TAYD* | Non-Ducted Indoor Units | 184000 | 12.3 | 22 | 206000 | 3.9 | 176000 | 2.22 | R-410A | 15.3333
202021858 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* | RXLQ120TATJ* |  |  | RXLQ240TATJ* | Non-Ducted Indoor Units | 228000 | 12.1 | 21 | 256000 | 3.77 | 218000 | 2.22 | R-410A | 19
202021859 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* | RXLQ120TAYD* |  |  | RXLQ240TAYD* | Non-Ducted Indoor Units | 228000 | 12.1 | 21 | 256000 | 3.77 | 218000 | 2.22 | R-410A | 19
202021860 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* | RXLQ72TATJ* |  |  | RXLQ144TATJ* | Non-Ducted Indoor Units | 138000 | 12.7 | 22.4 | 154000 | 3.86 | 131000 | 2.21 | R-410A | 11.5
202021861 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* | RXLQ72TAYD* |  |  | RXLQ144TAYD* | Non-Ducted Indoor Units | 138000 | 12.7 | 22.4 | 154000 | 3.86 | 131000 | 2.21 | R-410A | 11.5
202021873 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* | RXLQ72TATJ* |  |  | RXLQ144TATJ* | Ducted Indoor Units | 138000 | 12.4 | 18.2 | 154000 | 3.56 | 131000 | 2.21 | R-410A | 11.5
202021874 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* | RXLQ72TAYD* |  |  | RXLQ144TAYD* | Ducted Indoor Units | 138000 | 12.4 | 18.2 | 154000 | 3.56 | 131000 | 2.21 | R-410A | 11.5
202021875 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* | RXLQ72TAYC* |  |  | RXLQ144TAYC* | Ducted Indoor Units | 138000 | 12.4 | 18.2 | 154000 | 3.56 | 131000 | 2.21 | R-410A | 11.5
202021876 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* | RXLQ96TATJ* |  |  | RXLQ192TATJ* | Ducted Indoor Units | 184000 | 12.5 | 18.8 | 206000 | 3.61 | 176000 | 2.16 | R-410A | 15.3333
202021877 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* | RXLQ96TAYD* |  |  | RXLQ192TAYD* | Ducted Indoor Units | 184000 | 12.5 | 18.8 | 206000 | 3.61 | 176000 | 2.16 | R-410A | 15.3333
202021878 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* | RXLQ96TAYC* |  |  | RXLQ192TAYC* | Ducted Indoor Units | 184000 | 12.5 | 18.8 | 206000 | 3.61 | 176000 | 2.16 | R-410A | 15.3333
202021879 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* | RXLQ120TATJ* |  |  | RXLQ240TATJ* | Ducted Indoor Units | 228000 | 11.5 | 18.6 | 256000 | 3.53 | 218000 | 2.13 | R-410A | 19
202021880 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* | RXLQ120TAYD* |  |  | RXLQ240TAYD* | Ducted Indoor Units | 228000 | 11.5 | 18.6 | 256000 | 3.53 | 218000 | 2.13 | R-410A | 19
202021881 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* | RXLQ120TAYC* |  |  | RXLQ240TAYC* | Ducted Indoor Units | 228000 | 11.5 | 18.6 | 256000 | 3.53 | 218000 | 2.13 | R-410A | 19
202021884 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYC* |  |  |  | RXYQ144TAYC* | Ducted Indoor Units | 138000 | 10.8 | 18.2 | 154000 | 3.46 | 109000 | 2.14 | R-410A | 11.5
202021886 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ96TAYC* |  |  | RXYQ192TAYC* | Ducted Indoor Units | 184000 | 11.8 | 19.2 | 206000 | 3.72 | 150000 | 2.39 | R-410A | 15.3333
202021887 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ120TAYC* |  |  | RXYQ216TAYC* | Ducted Indoor Units | 206000 | 11.3 | 19.1 | 232000 | 3.58 | 164000 | 2.22 | R-410A | 17.1667
202021888 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* |  |  | RXYQ240TAYC* | Ducted Indoor Units | 228000 | 10.7 | 18.1 | 256000 | 3.46 | 182000 | 2.18 | R-410A | 19
202022802 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYC* |  |  |  | RXYQ144TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.15 | 20.2 | 154000 | 3.65 | 109000 | 2.17 | R-410A | 11.5
202022804 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ96TAYC* |  |  | RXYQ192TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.1 | 20.55 | 206000 | 3.81 | 150000 | 2.45 | R-410A | 15.3333
202022805 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYC* | RXYQ120TAYC* |  |  | RXYQ216TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.55 | 20.4 | 232000 | 3.71 | 164000 | 2.28 | R-410A | 17.1667
202022806 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* |  |  | RXYQ240TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 19.45 | 256000 | 3.61 | 182000 | 2.28 | R-410A | 19
202022822 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TATJ* | RXLQ72TATJ* |  |  | RXLQ144TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.55 | 20.3 | 154000 | 3.71 | 131000 | 2.21 | R-410A | 11.5
202022823 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYD* | RXLQ72TAYD* |  |  | RXLQ144TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.55 | 20.3 | 154000 | 3.71 | 131000 | 2.21 | R-410A | 11.5
202022824 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ72TAYC* | RXLQ72TAYC* |  |  | RXLQ144TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.55 | 20.3 | 154000 | 3.71 | 131000 | 2.21 | R-410A | 11.5
202022825 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TATJ* | RXLQ96TATJ* |  |  | RXLQ192TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.4 | 20.4 | 206000 | 3.75 | 176000 | 2.19 | R-410A | 15.3333
202022826 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYD* | RXLQ96TAYD* |  |  | RXLQ192TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.4 | 20.4 | 206000 | 3.75 | 176000 | 2.19 | R-410A | 15.3333
202022827 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ96TAYC* | RXLQ96TAYC* |  |  | RXLQ192TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.4 | 20.4 | 206000 | 3.75 | 176000 | 2.19 | R-410A | 15.3333
202022828 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TATJ* | RXLQ120TATJ* |  |  | RXLQ240TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.8 | 19.8 | 256000 | 3.65 | 218000 | 2.17 | R-410A | 19
202022829 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYD* | RXLQ120TAYD* |  |  | RXLQ240TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.8 | 19.8 | 256000 | 3.65 | 218000 | 2.17 | R-410A | 19
202022830 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXLQ120TAYC* | RXLQ120TAYC* |  |  | RXLQ240TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.8 | 19.8 | 256000 | 3.65 | 218000 | 2.17 | R-410A | 19
202095830 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA072H4M-2Y |  |  | VPA168H4M-2Y | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
202095831 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA072H4M-2Y |  |  | VPA168H4M-2Y | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
202095832 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA072H4M-2G |  |  | VPA168H4M-2G | Non-Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
202095833 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA072H4M-2G |  |  | VPA168H4M-2G | Ducted Indoor Units | 160000 | 12.2 | 22.4 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
202095834 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA072H4M-2Y |  |  | VRA168H4M-2Y | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
202095835 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA072H4M-2Y |  |  | VRA168H4M-2Y | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
202095836 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA072H4M-2G |  |  | VRA168H4M-2G | Non-Ducted Indoor Units | 160000 | 12.3 | 22.7 | 180000 | 3.74 | 126000 | 2.5 | R-410A | 13.3333
202095837 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA072H4M-2G |  |  | VRA168H4M-2G | Ducted Indoor Units | 160000 | 12.2 | 22.9 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13.3333
202095838 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA096H4M-2Y |  |  | VPA192H4M-2Y | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
202095839 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2Y | VPA096H4M-2Y |  |  | VPA192H4M-2Y | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
202095840 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA096H4M-2G |  |  | VPA192H4M-2G | Non-Ducted Indoor Units | 184000 | 11.9 | 21.9 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
202095841 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096H4M-2G | VPA096H4M-2G |  |  | VPA192H4M-2G | Ducted Indoor Units | 184000 | 11.5 | 22.4 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
202095842 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA096H4M-2Y |  |  | VRA192H4M-2Y | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
202095843 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2Y | VRA096H4M-2Y |  |  | VRA192H4M-2Y | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
202095844 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA096H4M-2G |  |  | VRA192H4M-2G | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.74 | 144000 | 2.4 | R-410A | 15.3333
202095845 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096H4M-2G | VRA096H4M-2G |  |  | VRA192H4M-2G | Ducted Indoor Units | 184000 | 11.5 | 22.9 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 15.3333
202606778 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S |  |  | TVAHP144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
202606779 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S |  |  | HVAHP144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
202606780 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S |  |  | YVAHP144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
202606781 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S |  |  | TVAHP144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
202606782 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S |  |  | HVAHP144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
202606783 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S |  |  | YVAHP144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
202606784 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S |  |  | TVAHR144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
202606785 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S |  |  | HVAHR144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
202606786 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S |  |  | YVAHR144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
202606787 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S |  |  | TVAHR144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
202606788 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S |  |  | HVAHR144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
202606789 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S |  |  | YVAHR144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
202606796 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S |  |  | TVAHP168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
202606797 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S |  |  | HVAHP168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
202606798 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S |  |  | YVAHP168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
202606799 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S |  |  | TVAHP168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
202606800 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S |  |  | HVAHP168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
202606801 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S |  |  | YVAHP168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
202606802 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S |  |  | TVAHR168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
202606803 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S |  |  | HVAHR168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
202606804 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S |  |  | YVAHR168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
202606805 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S |  |  | TVAHR168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
202606806 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S |  |  | HVAHR168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
202606807 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S |  |  | YVAHR168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
202606814 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S |  |  | TVAHP192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
202606815 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S |  |  | HVAHP192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
202606816 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S |  |  | YVAHP192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
202606820 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S |  |  | TVAHR192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
202606821 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S |  |  | HVAHR192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
202606822 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S |  |  | YVAHR192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
202606832 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
202606833 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
202606834 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
202606835 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
202606836 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
202606837 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
202606838 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
202606839 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
202606840 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
202606841 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
202606842 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
202606843 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
202606844 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
202606845 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
202606846 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
202606847 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
202606848 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
202606849 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
202606850 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
202606851 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
202606852 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
202606853 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
202606854 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
202606855 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
202607401 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607402 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607403 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607404 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607405 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607406 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607407 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607408 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607409 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607410 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607411 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607412 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
202607413 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607414 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607415 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607416 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607417 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607418 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607419 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607420 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607421 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607422 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607423 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607424 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
202607425 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S |  |  |  | TVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607426 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S |  |  |  | HVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607427 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S |  |  |  | YVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607428 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S |  |  |  | TVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607429 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S |  |  |  | HVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607430 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S |  |  |  | YVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607431 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S |  |  |  | TVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607432 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S |  |  |  | HVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607433 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S |  |  |  | YVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607434 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S |  |  |  | TVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607435 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S |  |  |  | HVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607436 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S |  |  |  | YVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
202607475 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S |  |  | TVAHP144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
202607476 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S |  |  | HVAHP144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
202607477 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S |  |  | YVAHP144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
202607478 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S |  |  | TVAHP144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
202607479 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S |  |  | HVAHP144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
202607480 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S |  |  | YVAHP144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
202607481 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S |  |  | TVAHR144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
202607482 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S |  |  | HVAHR144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
202607483 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S |  |  | YVAHR144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
202607484 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S |  |  | TVAHR144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
202607485 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S |  |  | HVAHR144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
202607486 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S |  |  | YVAHR144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
202607493 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607494 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607495 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607496 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607497 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607498 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607499 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607500 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607501 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607502 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607503 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607504 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
202607505 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S |  |  | TVAHP168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
202607506 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S |  |  | HVAHP168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
202607507 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S |  |  | YVAHP168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
202607508 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S |  |  | TVAHP168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
202607509 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S |  |  | HVAHP168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
202607510 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S |  |  | YVAHP168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
202607511 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S |  |  | TVAHR168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
202607512 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S |  |  | HVAHR168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
202607513 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S |  |  | YVAHR168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
202607514 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S |  |  | TVAHR168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
202607515 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S |  |  | HVAHR168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
202607516 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S |  |  | YVAHR168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
202607517 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP072B31CW |  |  | TVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607518 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP072B31CW |  |  | HVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607519 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP072B31CW |  |  | YVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607520 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP072B41CW |  |  | TVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607521 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP072B41CW |  |  | HVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607522 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP072B41CW |  |  | YVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
202607523 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607524 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607525 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607526 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607527 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607528 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607529 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607530 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607531 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607532 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607533 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607534 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
202607565 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607566 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607567 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607568 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607569 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607570 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607571 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607572 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607573 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607574 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607575 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607576 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
202607577 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607578 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607579 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607580 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607581 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607582 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607583 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607584 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607585 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607586 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607587 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607588 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
202607622 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S | TVAHP120B32S |  |  | TVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607623 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S | HVAHP120B32S |  |  | HVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607624 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S | YVAHP120B32S |  |  | YVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607625 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S | TVAHP120B42S |  |  | TVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607626 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S | HVAHP120B42S |  |  | HVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607627 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S | YVAHP120B42S |  |  | YVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607628 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S | TVAHR120B32S |  |  | TVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607629 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S | HVAHR120B32S |  |  | HVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607630 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S | YVAHR120B32S |  |  | YVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607631 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S | TVAHR120B42S |  |  | TVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607632 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S | HVAHR120B42S |  |  | HVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202607633 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S | YVAHR120B42S |  |  | YVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
202608010 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608011 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608012 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608013 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608014 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608015 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608016 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608017 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608018 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608019 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608020 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608021 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
202608040 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608041 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608042 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608043 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608044 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608045 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608046 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608047 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608048 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608049 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608050 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608051 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
202608070 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S |  |  |  | TVAHP192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608071 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S |  |  |  | HVAHP192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608072 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S |  |  |  | YVAHP192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608073 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S |  |  |  | TVAHP192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608074 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S |  |  |  | HVAHP192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608075 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S |  |  |  | YVAHP192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608076 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S |  |  |  | TVAHR192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608077 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S |  |  |  | HVAHR192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608078 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S |  |  |  | YVAHR192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608079 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S |  |  |  | TVAHR192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608080 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S |  |  |  | HVAHR192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608081 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S |  |  |  | YVAHR192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
202608094 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608095 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608096 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608097 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608098 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608099 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608100 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608101 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608102 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608103 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608104 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608105 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
202608124 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S | TVAHP120B32S |  |  | TVAHP240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608125 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S | HVAHP120B32S |  |  | HVAHP240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608126 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S | YVAHP120B32S |  |  | YVAHP240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608127 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S | TVAHP120B42S |  |  | TVAHP240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608128 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S | HVAHP120B42S |  |  | HVAHP240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608129 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S | YVAHP120B42S |  |  | YVAHP240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608130 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S | TVAHR120B32S |  |  | TVAHR240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608131 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S | HVAHR120B32S |  |  | HVAHR240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608132 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S | YVAHR120B32S |  |  | YVAHR240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608133 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S | TVAHR120B42S |  |  | TVAHR240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608134 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S | HVAHR120B42S |  |  | HVAHR240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
202608135 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S | YVAHR120B42S |  |  | YVAHR240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
203906663 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906664 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906665 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906666 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906667 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906668 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906669 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906670 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906671 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906672 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906673 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906674 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
203906675 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906676 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906677 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906678 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906679 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906680 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906681 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906682 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906684 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906685 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906686 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906687 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
203906688 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S |  |  |  | TVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906689 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S |  |  |  | HVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906690 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S |  |  |  | YVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906691 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S |  |  |  | TVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906692 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S |  |  |  | HVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906693 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S |  |  |  | YVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906694 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S |  |  |  | TVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906695 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S |  |  |  | HVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906696 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S |  |  |  | YVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906697 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S |  |  |  | TVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906698 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S |  |  |  | HVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906699 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S |  |  |  | YVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
203906732 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906733 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906734 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906735 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906736 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906737 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906738 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906740 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906741 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906742 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906743 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906744 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
203906745 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP072B31CW |  |  | TVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203906746 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP072B31CW |  |  | HVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203906747 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP072B31CW |  |  | YVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203906748 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP072B41CW |  |  | TVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203906749 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP072B41CW |  |  | HVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203906750 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP072B41CW |  |  | YVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203906751 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906752 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906754 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906755 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906756 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906757 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906758 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906759 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906760 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906761 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906762 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906763 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
203906770 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906771 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906773 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906774 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906775 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906776 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906777 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906778 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906779 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906780 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906781 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906782 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
203906783 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906784 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906785 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906786 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906787 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906788 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906789 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906790 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906792 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906793 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906794 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906795 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
203906808 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S | TVAHP120B32S |  |  | TVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906809 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S | HVAHP120B32S |  |  | HVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906810 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S | YVAHP120B32S |  |  | YVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906811 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S | TVAHP120B42S |  |  | TVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906812 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S | HVAHP120B42S |  |  | HVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906813 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S | YVAHP120B42S |  |  | YVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906814 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S | TVAHR120B32S |  |  | TVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906815 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S | HVAHR120B32S |  |  | HVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906817 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S | YVAHR120B32S |  |  | YVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906818 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S | TVAHR120B42S |  |  | TVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906819 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S | HVAHR120B42S |  |  | HVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203906820 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S | YVAHR120B42S |  |  | YVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
203993992 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B31CW | TVAHP072B31CW |  |  | TVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203993994 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP072B31CW |  |  | HVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203993996 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP072B31CW |  |  | YVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203993999 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B41CW | TVAHP072B41CW |  |  | TVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203994001 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP072B41CW |  |  | HVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
203994003 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP072B41CW |  |  | YVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
204268354 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S |  |  |  | TVAHR144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268356 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B52S |  |  |  | TVAHR168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204268360 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR072B52S |  |  | TVAHR216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268362 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B52S | TVAHR120B52S |  |  | TVAHR240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204268379 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S |  |  |  | HVAHR144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268380 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S |  |  |  | HVAHR168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204268382 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR072B52S |  |  | HVAHR216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268383 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B52S | HVAHR120B52S |  |  | HVAHR240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204268395 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S |  |  |  | YVAHR144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268396 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S |  |  |  | YVAHR168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204268398 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR072B52S |  |  | YVAHR216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268399 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B52S | YVAHR120B52S |  |  | YVAHR240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204268411 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S |  |  |  | TVAHR144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268412 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B52S |  |  |  | TVAHR168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204268413 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B52S |  |  |  | TVAHR192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268414 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR072B52S |  |  | TVAHR216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204268427 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S |  |  |  | HVAHR144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268428 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S |  |  |  | HVAHR168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204268429 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B52S |  |  |  | HVAHR192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268430 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR072B52S |  |  | HVAHR216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204268445 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S |  |  |  | YVAHR144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268447 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S |  |  |  | YVAHR168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204268449 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B52S |  |  |  | YVAHR192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268451 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR072B52S |  |  | YVAHR216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204268474 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S |  |  |  | TVAHP144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268476 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B52S |  |  |  | TVAHP168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204268478 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP072B52S |  |  | TVAHP216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268480 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B52S | TVAHP120B52S |  |  | TVAHP240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204268502 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S |  |  |  | HVAHP144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268504 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S |  |  |  | HVAHP168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204268509 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP072B52S |  |  | HVAHP216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268511 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B52S | HVAHP120B52S |  |  | HVAHP240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204268535 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S |  |  |  | YVAHP144B52S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
204268536 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S |  |  |  | YVAHP168B52S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
204268540 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP072B52S |  |  | YVAHP216B52S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
204268542 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B52S | YVAHP120B52S |  |  | YVAHP240B52S | Non-Ducted Indoor Units | 228000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19
204268561 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S |  |  |  | TVAHP144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268563 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B52S |  |  |  | TVAHP168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204268565 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B52S |  |  |  | TVAHP192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268567 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP072B52S |  |  | TVAHP216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204268583 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S |  |  |  | HVAHP144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268584 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S |  |  |  | HVAHP168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204268585 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B52S |  |  |  | HVAHP192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268586 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP072B52S |  |  | HVAHP216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204268599 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S |  |  |  | YVAHP144B52S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
204268600 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S |  |  |  | YVAHP168B52S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
204268601 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B52S |  |  |  | YVAHP192B52S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
204268602 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP072B52S |  |  | YVAHP216B52S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
204269027 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S |  |  |  | TVAHR144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204269028 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B52S |  |  |  | TVAHR168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269029 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B52S |  |  |  | TVAHR192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204269030 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR072B52S |  |  | TVAHR216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204269031 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B52S | TVAHR120B52S |  |  | TVAHR240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204269043 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S |  |  |  | HVAHR144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204269044 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S |  |  |  | HVAHR168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269045 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B52S |  |  |  | HVAHR192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204269046 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR072B52S |  |  | HVAHR216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204269047 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B52S | HVAHR120B52S |  |  | HVAHR240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204269059 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S |  |  |  | YVAHR144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204269060 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S |  |  |  | YVAHR168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269061 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B52S |  |  |  | YVAHR192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204269062 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR072B52S |  |  | YVAHR216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204269063 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B52S | YVAHR120B52S |  |  | YVAHR240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204269075 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S |  |  |  | TVAHP144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204269076 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B52S |  |  |  | TVAHP168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269077 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B52S |  |  |  | TVAHP192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204269078 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP072B52S |  |  | TVAHP216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204269079 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B52S | TVAHP120B52S |  |  | TVAHP240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204269091 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S |  |  |  | HVAHP144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204269092 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S |  |  |  | HVAHP168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269093 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B52S |  |  |  | HVAHP192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204269094 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP072B52S |  |  | HVAHP216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204269095 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B52S | HVAHP120B52S |  |  | HVAHP240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204269107 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S |  |  |  | YVAHP144B52S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
204269108 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S |  |  |  | YVAHP168B52S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
204269109 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B52S |  |  |  | YVAHP192B52S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
204269110 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP072B52S |  |  | YVAHP216B52S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
204269111 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B52S | YVAHP120B52S |  |  | YVAHP240B52S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19
204442715 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH |  |  |  | AM144FXVAFH | Non-Ducted Indoor Units | 138000 | 11.5 | 23.9 | 154000 | 3.81 | 100000 | 2.55 | R-410A | 11.5
204442716 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192HXVAFH |  |  |  | AM192HXVAFH | Non-Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.61 | 134000 | 2.53 | R-410A | 15.3333
204442718 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM168HXVAFH |  |  | AM240JXVAFH | Non-Ducted Indoor Units | 228000 | 10.8 | 23 | 258000 | 3.65 | 168000 | 2.5 | R-410A | 19
204442730 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH |  |  |  | AM144FXVAJH | Non-Ducted Indoor Units | 138000 | 11.5 | 23.9 | 154000 | 3.81 | 100000 | 2.55 | R-410A | 11.5
204442731 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192HXVAJH |  |  |  | AM192HXVAJH | Non-Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.61 | 134000 | 2.53 | R-410A | 15.3333
204442733 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM168HXVAJH |  |  | AM240JXVAJH | Non-Ducted Indoor Units | 228000 | 10.8 | 23 | 258000 | 3.65 | 168000 | 2.5 | R-410A | 19
204442746 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR |  |  |  | AM144FXVAFR | Non-Ducted Indoor Units | 138000 | 11.5 | 23.9 | 154000 | 3.81 | 100000 | 2.55 | R-410A | 11.5
9956559 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y | VEP072C432Y |  |  | VEP140C432Y | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 23.3 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
9550138 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Non-Ducted Indoor Units | 138000 | 13.9 | 26.4 | 154000 | 3.77 | 109000 | 2.65 | R-410A | 11.5
9550161 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Ducted Indoor Units | 138000 | 13 | 22.6 | 154000 | 3.65 | 109000 | 2.6 | R-410A | 11.5
9680960 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0726FT2P-UL | MMY-MAP0726FT2P-UL |  |  | MMY-AP1446FT2P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.45 | 24.5 | 154000 | 3.71 | 109000 | 2.62 | R-410A | 11.5
9133487 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC120KHP/220V | TVRF-OC120KHP/220V |  |  | TVRF-OC240KHP/220V | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 21.7 | 256000 | 3.34 | 168000 | 2.17 | R-410A | 19
10267474 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-96WM/B-U(U) |  |  | GMV-168WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.75 | 21.5 | 180000 | 3.46 | 118000 | 2.34 | R-410A | 13.3333
10267477 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  |  | GMV-192WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 21.5 | 206000 | 3.32 | 134000 | 2.18 | R-410A | 15.3333
10267480 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) |  |  | GMV-216WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 21.5 | 230000 | 3.38 | 150000 | 2.24 | R-410A | 17.1667
10267483 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  |  | GMV-240WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.7 | 20.5 | 256000 | 3.34 | 168000 | 2.17 | R-410A | 19
10306471 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H6CDC712(A) | IOV072H6CDC712(A) |  |  | IOV144H6CDC725(A) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 22.75 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
10323537 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10323538 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10323540 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10323541 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S | TVAHR120B32S |  |  | TVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10323553 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10323554 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10323556 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10323557 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S | HVAHR120B32S |  |  | HVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10323569 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10323570 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10323572 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10323573 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S | YVAHR120B32S |  |  | YVAHR240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10323585 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10323586 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10323588 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10323589 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S | TVAHR120B42S |  |  | TVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10323601 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10323602 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10323604 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10323605 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S | HVAHR120B42S |  |  | HVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10323617 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10323618 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10323620 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10323621 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S | YVAHR120B42S |  |  | YVAHR240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10323633 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10323634 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10323635 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S |  |  |  | TVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10323636 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10323649 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10323650 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10323651 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S |  |  |  | HVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10323652 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10323665 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10323666 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10323667 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S |  |  |  | YVAHR192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10323668 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10323681 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10323682 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10323683 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S |  |  |  | TVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10323684 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10323697 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10323698 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10323699 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S |  |  |  | HVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10323700 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10323713 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10323714 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10323715 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S |  |  |  | YVAHR192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10323716 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10323731 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S |  |  |  | TVAHR144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10323732 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S |  |  |  | TVAHR168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10323733 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S |  |  |  | TVAHR192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10323734 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR072B42S |  |  | TVAHR216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10323735 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B42S | TVAHR120B42S |  |  | TVAHR240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10323747 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S |  |  |  | HVAHR144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10323748 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S |  |  |  | HVAHR168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10323749 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S |  |  |  | HVAHR192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10323750 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR072B42S |  |  | HVAHR216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10323751 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B42S | HVAHR120B42S |  |  | HVAHR240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10323763 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S |  |  |  | YVAHR144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10323764 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S |  |  |  | YVAHR168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10323765 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S |  |  |  | YVAHR192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10323766 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR072B42S |  |  | YVAHR216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10323767 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B42S | YVAHR120B42S |  |  | YVAHR240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10323780 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S |  |  |  | TVAHR144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10323781 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S |  |  |  | TVAHR168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10323782 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S |  |  |  | TVAHR192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10323783 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR072B32S |  |  | TVAHR216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10323784 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B32S | TVAHR120B32S |  |  | TVAHR240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10323796 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S |  |  |  | HVAHR144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10323797 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S |  |  |  | HVAHR168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10323798 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S |  |  |  | HVAHR192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10323799 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR072B32S |  |  | HVAHR216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10323800 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B32S | HVAHR120B32S |  |  | HVAHR240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10323812 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S |  |  |  | YVAHR144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10323813 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S |  |  |  | YVAHR168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10323814 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S |  |  |  | YVAHR192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10323815 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR072B32S |  |  | YVAHR216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10323816 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B32S | YVAHR120B32S |  |  | YVAHR240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10103105 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* | RELQ72TAYC* |  |  | RELQ144TAYC* | Non-Ducted Indoor Units | 138000 | 12.9 | 22.5 | 154000 | 3.81 | 131000 | 2.2 | R-410A | 11.5
10103106 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* | RELQ96TAYC* |  |  | RELQ192TAYC* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.1 | 206000 | 3.85 | 176000 | 2.2 | R-410A | 15.3333
10103107 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* | RELQ120TAYC* |  |  | RELQ240TAYC* | Non-Ducted Indoor Units | 228000 | 12.3 | 21.1 | 256000 | 3.68 | 218000 | 2.2 | R-410A | 19
10103111 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* |  |  |  | REYQ144TAYC* | Non-Ducted Indoor Units | 138000 | 11.8 | 22.5 | 154000 | 3.75 | 109000 | 2.16 | R-410A | 11.5
10103113 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ96TAYC* |  |  | REYQ192TAYC* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.2 | 206000 | 3.85 | 150000 | 2.5 | R-410A | 15.3333
10103114 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ120TAYC* |  |  | REYQ216TAYC* | Non-Ducted Indoor Units | 206000 | 12.2 | 22 | 232000 | 3.76 | 164000 | 2.34 | R-410A | 17.1667
10103115 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ120TAYC* |  |  | REYQ240TAYC* | Non-Ducted Indoor Units | 228000 | 11.6 | 21.1 | 256000 | 3.68 | 182000 | 2.34 | R-410A | 19
10103126 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* | RELQ72TAYC* |  |  | RELQ144TAYC* | Ducted Indoor Units | 138000 | 12.6 | 18.6 | 154000 | 3.55 | 131000 | 2.2 | R-410A | 11.5
10103127 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* | RELQ96TAYC* |  |  | RELQ192TAYC* | Ducted Indoor Units | 184000 | 12.7 | 19 | 206000 | 3.57 | 176000 | 2.15 | R-410A | 15.3333
10103128 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* | RELQ120TAYC* |  |  | RELQ240TAYC* | Ducted Indoor Units | 228000 | 11.7 | 18.6 | 256000 | 3.49 | 218000 | 2.13 | R-410A | 19
10103132 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ72TAYC* | RELQ72TAYC* |  |  | RELQ144TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.75 | 20.55 | 154000 | 3.68 | 131000 | 2.2 | R-410A | 11.5
10103133 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ96TAYC* | RELQ96TAYC* |  |  | RELQ192TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.6 | 20.55 | 206000 | 3.71 | 176000 | 2.17 | R-410A | 15.3333
10103134 | 1/1/2027 | DAIKIN | HMSR-A-CB | RELQ120TAYC* | RELQ120TAYC* |  |  | RELQ240TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12 | 19.85 | 256000 | 3.58 | 218000 | 2.16 | R-410A | 19
10103138 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* |  |  |  | REYQ144TAYC* | Ducted Indoor Units | 138000 | 11.3 | 18.6 | 154000 | 3.42 | 109000 | 2.12 | R-410A | 11.5
10103140 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ96TAYC* |  |  | REYQ192TAYC* | Ducted Indoor Units | 184000 | 12.6 | 19.7 | 206000 | 3.67 | 150000 | 2.37 | R-410A | 15.3333
10103141 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ120TAYC* |  |  | REYQ216TAYC* | Ducted Indoor Units | 206000 | 11.6 | 19.6 | 232000 | 3.52 | 164000 | 2.2 | R-410A | 17.1667
10103142 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ120TAYC* |  |  | REYQ240TAYC* | Ducted Indoor Units | 228000 | 11.4 | 18.6 | 256000 | 3.39 | 182000 | 2.16 | R-410A | 19
10103152 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* |  |  |  | REYQ144TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.55 | 20.55 | 154000 | 3.58 | 109000 | 2.14 | R-410A | 11.5
10103154 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ96TAYC* |  |  | REYQ192TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.55 | 20.95 | 206000 | 3.76 | 150000 | 2.43 | R-410A | 15.3333
10103155 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYC* | REYQ120TAYC* |  |  | REYQ216TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.9 | 20.8 | 232000 | 3.64 | 164000 | 2.27 | R-410A | 17.1667
10103156 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ120TAYC* |  |  | REYQ240TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.5 | 19.85 | 256000 | 3.53 | 182000 | 2.25 | R-410A | 19
10206679 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10206680 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10206682 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10206683 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S | TVAHP120B32S |  |  | TVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10206693 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10206694 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10206696 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10206697 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S | HVAHP120B32S |  |  | HVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10206707 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10206708 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10206710 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10206711 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S | YVAHP120B32S |  |  | YVAHP240B32S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10206721 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10206722 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10206724 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10206725 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S | TVAHP120B42S |  |  | TVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10206735 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10206736 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10206738 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10206739 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S | HVAHP120B42S |  |  | HVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10206749 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Non-Ducted Indoor Units | 138000 | 10.9 | 23.9 | 154000 | 3.42 | 110000 | 2.12 | R-410A | 11.5
10206750 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Non-Ducted Indoor Units | 160000 | 11.6 | 23.4 | 180000 | 3.65 | 124000 | 2.16 | R-410A | 13.3333
10206752 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Non-Ducted Indoor Units | 206000 | 10.9 | 20.9 | 232000 | 3.82 | 164000 | 2.32 | R-410A | 17.1667
10206753 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S | YVAHP120B42S |  |  | YVAHP240B42S | Non-Ducted Indoor Units | 230000 | 11.1 | 20.8 | 258000 | 3.67 | 178000 | 2.35 | R-410A | 19.1667
10206763 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10206764 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10206765 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S |  |  |  | TVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10206766 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10206777 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10206778 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10206779 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S |  |  |  | HVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10206780 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10206791 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10206792 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10206793 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S |  |  |  | YVAHP192B32S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10206794 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10206805 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10206806 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10206807 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S |  |  |  | TVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10206808 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10206819 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10206820 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10206821 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S |  |  |  | HVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10206822 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10206833 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Ducted Indoor Units | 138000 | 11.2 | 21.2 | 154000 | 3.4 | 110000 | 2.15 | R-410A | 11.5
10206834 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Ducted Indoor Units | 160000 | 11.8 | 21.4 | 180000 | 3.56 | 124000 | 2.4 | R-410A | 13.3333
10206835 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S |  |  |  | YVAHP192B42S | Ducted Indoor Units | 184000 | 11.1 | 20.8 | 206000 | 3.38 | 140000 | 2.15 | R-410A | 15.3333
10206836 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Ducted Indoor Units | 206000 | 11.2 | 20.7 | 232000 | 3.51 | 164000 | 2.29 | R-410A | 17.1667
10207513 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S |  |  |  | TVAHP144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10207514 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S |  |  |  | TVAHP168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10207515 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S |  |  |  | TVAHP192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10207516 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP072B32S |  |  | TVAHP216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10207517 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B32S | TVAHP120B32S |  |  | TVAHP240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10207527 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S |  |  |  | HVAHP144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10207528 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S |  |  |  | HVAHP168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10207529 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S |  |  |  | HVAHP192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10207530 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP072B32S |  |  | HVAHP216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10207531 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B32S | HVAHP120B32S |  |  | HVAHP240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10207541 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S |  |  |  | YVAHP144B32S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10207542 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S |  |  |  | YVAHP168B32S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10207543 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S |  |  |  | YVAHP192B32S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10207544 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP072B32S |  |  | YVAHP216B32S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10207545 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B32S | YVAHP120B32S |  |  | YVAHP240B32S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10207555 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S |  |  |  | TVAHP144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10207556 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S |  |  |  | TVAHP168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10207557 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S |  |  |  | TVAHP192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10207558 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP072B42S |  |  | TVAHP216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10207559 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B42S | TVAHP120B42S |  |  | TVAHP240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10207569 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S |  |  |  | HVAHP144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10207570 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S |  |  |  | HVAHP168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10207571 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S |  |  |  | HVAHP192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10207572 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP072B42S |  |  | HVAHP216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10207573 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B42S | HVAHP120B42S |  |  | HVAHP240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10207583 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S |  |  |  | YVAHP144B42S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.05 | 22.55 | 154000 | 3.41 | 110000 | 2.13 | R-410A | 11.5
10207584 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S |  |  |  | YVAHP168B42S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.7 | 22.4 | 180000 | 3.6 | 124000 | 2.28 | R-410A | 13.3333
10207585 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S |  |  |  | YVAHP192B42S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.85 | 21.1 | 206000 | 3.35 | 140000 | 2.1 | R-410A | 15.3333
10207586 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP072B42S |  |  | YVAHP216B42S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.05 | 20.8 | 232000 | 3.66 | 164000 | 2.3 | R-410A | 17.1667
10207587 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B42S | YVAHP120B42S |  |  | YVAHP240B42S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.85 | 20.9 | 258000 | 3.59 | 178000 | 2.31 | R-410A | 19.1667
10208207 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DZN1 |  |  |  | MV5-2R241DZN1 | Ducted Indoor Units | 228000 | 11 | 21.1 | 256000 | 3.57 | 172000 | 2.39 | R-410A | 19
10208212 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DZN1 |  |  |  | MV5-2R241DZN1 | Non-Ducted Indoor Units | 228000 | 11.2 | 22.4 | 256000 | 3.71 | 172000 | 2.48 | R-410A | 19
10208472 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DXN1 |  |  |  | MV5-2R241DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 21.75 | 256000 | 3.64 | 172000 | 2.43 | R-410A | 19
10208477 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R241DZN1 |  |  |  | MV5-2R241DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 21.75 | 256000 | 3.64 | 172000 | 2.43 | R-410A | 19
9363453 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 12 | 22 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
9363454 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 12.25 | 22 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
9363455 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 12.5 | 22 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
9363456 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 12 | 22 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
9363457 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 12.25 | 22 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
9363458 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 12.5 | 22 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
9363460 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 11.6 | 22 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
9363461 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 11.95 | 21.75 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
9363462 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 12.3 | 21.5 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
9363463 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 11.6 | 22 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
9363464 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 11.95 | 21.75 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
9363465 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 12.3 | 21.5 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
9363466 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA216HDS5-1 | Ducted Indoor Units | 196000 | 11.3 | 21.3 | 224000 | 3.54 | 152000 | 2.3 | R-410A | 16.3333
9363468 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA216HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 196000 | 11.5 | 20.9 | 224000 | 3.58 | 152000 | 2.35 | R-410A | 16.3333
9363469 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA216HDS5-1 | Non-Ducted Indoor Units | 196000 | 11.7 | 20.5 | 224000 | 3.62 | 152000 | 2.4 | R-410A | 16.3333
9363470 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA216HDS6-1 | Ducted Indoor Units | 196000 | 11.3 | 21.3 | 224000 | 3.54 | 152000 | 2.3 | R-410A | 16.3333
9363471 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA216HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 196000 | 11.5 | 20.9 | 224000 | 3.58 | 152000 | 2.35 | R-410A | 16.3333
9363472 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA216HDS6-1 | Non-Ducted Indoor Units | 196000 | 11.7 | 20.5 | 224000 | 3.62 | 152000 | 2.4 | R-410A | 16.3333
9363473 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA240HDS5-1 | Ducted Indoor Units | 214000 | 11 | 20.6 | 240000 | 3.47 | 160000 | 2.3 | R-410A | 17.8333
9363475 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA240HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 10.85 | 20.3 | 240000 | 3.5 | 160000 | 2.32 | R-410A | 17.8333
9363476 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA240HDS5-1 | Non-Ducted Indoor Units | 214000 | 10.7 | 20 | 240000 | 3.54 | 160000 | 2.35 | R-410A | 17.8333
9363477 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA240HDS6-1 | Ducted Indoor Units | 214000 | 11 | 20.6 | 240000 | 3.47 | 160000 | 2.3 | R-410A | 17.8333
9363478 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA240HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 10.85 | 20.3 | 240000 | 3.5 | 160000 | 2.32 | R-410A | 17.8333
9363479 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA240HDS6-1 | Non-Ducted Indoor Units | 214000 | 10.7 | 20 | 240000 | 3.54 | 160000 | 2.35 | R-410A | 17.8333
9989457 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TATJ* | REYQ120TATJ* |  |  | REYQ192TATJ* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 200000 | 3.85 | 146000 | 2.38 | R-410A | 15.3333
9989759 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ120TATJ* |  |  | REYQ216TATJ* | Non-Ducted Indoor Units | 206000 | 12.5 | 23 | 226000 | 3.74 | 160000 | 2.32 | R-410A | 17.1667
9989782 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYD* | REYQ120TAYD* |  |  | REYQ192TAYD* | Non-Ducted Indoor Units | 184000 | 12.5 | 22.9 | 200000 | 3.85 | 146000 | 2.38 | R-410A | 15.3333
9989783 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ120TAYD* |  |  | REYQ216TAYD* | Non-Ducted Indoor Units | 206000 | 12.5 | 23 | 226000 | 3.74 | 160000 | 2.32 | R-410A | 17.1667
9989794 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TATJ* | REYQ120TATJ* |  |  | REYQ192TATJ* | Ducted Indoor Units | 184000 | 12.3 | 21.1 | 200000 | 3.67 | 146000 | 2.26 | R-410A | 15.3333
9989795 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYD* | REYQ120TAYD* |  |  | REYQ192TAYD* | Ducted Indoor Units | 184000 | 12.3 | 21.1 | 200000 | 3.67 | 146000 | 2.26 | R-410A | 15.3333
9989796 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ120TATJ* |  |  | REYQ216TATJ* | Ducted Indoor Units | 206000 | 12.2 | 20.8 | 226000 | 3.66 | 160000 | 2.18 | R-410A | 17.1667
9989797 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ120TAYD* |  |  | REYQ216TAYD* | Ducted Indoor Units | 206000 | 12.2 | 20.8 | 226000 | 3.66 | 160000 | 2.18 | R-410A | 17.1667
9989799 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ144TATJ* |  |  | REYQ240TATJ* | Non-Ducted Indoor Units | 228000 | 11.9 | 21.9 | 250000 | 3.68 | 178000 | 2.24 | R-410A | 19
9989809 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ144TAYD* |  |  | REYQ240TAYD* | Non-Ducted Indoor Units | 228000 | 11.9 | 21.9 | 250000 | 3.68 | 178000 | 2.24 | R-410A | 19
9989819 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ144TATJ* |  |  | REYQ240TATJ* | Ducted Indoor Units | 228000 | 11.6 | 19.8 | 250000 | 3.51 | 178000 | 2.09 | R-410A | 19
9989820 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ144TAYD* |  |  | REYQ240TAYD* | Ducted Indoor Units | 228000 | 11.6 | 19.8 | 250000 | 3.51 | 178000 | 2.09 | R-410A | 19
9989849 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TATJ* | REYQ120TATJ* |  |  | REYQ192TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.4 | 22 | 200000 | 3.76 | 146000 | 2.32 | R-410A | 15.3333
9989850 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TAYD* | REYQ120TAYD* |  |  | REYQ192TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.4 | 22 | 200000 | 3.76 | 146000 | 2.32 | R-410A | 15.3333
9989851 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ120TATJ* |  |  | REYQ216TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.35 | 21.9 | 226000 | 3.7 | 160000 | 2.25 | R-410A | 17.1667
9989852 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ120TAYD* |  |  | REYQ216TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.35 | 21.9 | 226000 | 3.7 | 160000 | 2.25 | R-410A | 17.1667
9989853 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TATJ* | REYQ144TATJ* |  |  | REYQ240TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 20.85 | 250000 | 3.59 | 178000 | 2.16 | R-410A | 19
9989854 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TAYD* | REYQ144TAYD* |  |  | REYQ240TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.75 | 20.85 | 250000 | 3.59 | 178000 | 2.16 | R-410A | 19
9990032 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* |  |  |  | RXYQ144TATJ* | Non-Ducted Indoor Units | 138000 | 12.1 | 24.8 | 154000 | 3.64 | 96000 | 2.33 | R-410A | 11.5
9990034 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TATJ* | RXYQ120TATJ* |  |  | RXYQ192TATJ* | Non-Ducted Indoor Units | 184000 | 11.1 | 22.2 | 206000 | 3.62 | 134000 | 2.27 | R-410A | 15.3333
9990035 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* | RXYQ120TATJ* |  |  | RXYQ216TATJ* | Non-Ducted Indoor Units | 206000 | 10.7 | 20.5 | 230000 | 3.83 | 158000 | 2.57 | R-410A | 17.1667
9990036 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* |  |  | RXYQ240TATJ* | Non-Ducted Indoor Units | 228000 | 11 | 20.8 | 256000 | 3.63 | 170000 | 2.41 | R-410A | 19
9990049 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* |  |  |  | RXYQ144TAYD* | Non-Ducted Indoor Units | 138000 | 12.1 | 24.8 | 154000 | 3.64 | 96000 | 2.33 | R-410A | 11.5
9990051 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYD* | RXYQ120TAYD* |  |  | RXYQ192TAYD* | Non-Ducted Indoor Units | 184000 | 11.1 | 22.2 | 206000 | 3.62 | 134000 | 2.27 | R-410A | 15.3333
9990052 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* | RXYQ120TAYD* |  |  | RXYQ216TAYD* | Non-Ducted Indoor Units | 206000 | 10.7 | 20.5 | 230000 | 3.83 | 158000 | 2.57 | R-410A | 17.1667
9990053 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ120TAYD* |  |  | RXYQ240TAYD* | Non-Ducted Indoor Units | 228000 | 11 | 20.8 | 256000 | 3.63 | 170000 | 2.41 | R-410A | 19
9990063 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* |  |  |  | RXYQ144TATJ* | Ducted Indoor Units | 138000 | 11.5 | 22.6 | 154000 | 3.34 | 96000 | 2.2 | R-410A | 11.5
9990064 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* |  |  |  | RXYQ144TAYD* | Ducted Indoor Units | 138000 | 11.5 | 22.6 | 154000 | 3.34 | 96000 | 2.2 | R-410A | 11.5
9990067 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TATJ* | RXYQ120TATJ* |  |  | RXYQ192TATJ* | Ducted Indoor Units | 184000 | 11.6 | 21.2 | 206000 | 3.29 | 134000 | 2.23 | R-410A | 15.3333
9990068 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYD* | RXYQ120TAYD* |  |  | RXYQ192TAYD* | Ducted Indoor Units | 184000 | 11.6 | 21.2 | 206000 | 3.29 | 134000 | 2.23 | R-410A | 15.3333
9990069 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* | RXYQ120TATJ* |  |  | RXYQ216TATJ* | Ducted Indoor Units | 206000 | 10.9 | 21.1 | 230000 | 3.5 | 158000 | 2.46 | R-410A | 17.1667
9990070 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* | RXYQ120TAYD* |  |  | RXYQ216TAYD* | Ducted Indoor Units | 206000 | 10.9 | 21.1 | 230000 | 3.5 | 158000 | 2.46 | R-410A | 17.1667
9990071 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* |  |  | RXYQ240TATJ* | Ducted Indoor Units | 228000 | 11.2 | 20.9 | 256000 | 3.33 | 170000 | 2.34 | R-410A | 19
9990072 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ120TAYD* |  |  | RXYQ240TAYD* | Ducted Indoor Units | 228000 | 11.2 | 20.9 | 256000 | 3.33 | 170000 | 2.34 | R-410A | 19
9990093 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* |  |  |  | RXYQ144TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.7 | 154000 | 3.49 | 96000 | 2.26 | R-410A | 11.5
9990094 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* |  |  |  | RXYQ144TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.8 | 23.7 | 154000 | 3.49 | 96000 | 2.26 | R-410A | 11.5
9990097 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TATJ* | RXYQ120TATJ* |  |  | RXYQ192TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21.7 | 206000 | 3.45 | 134000 | 2.25 | R-410A | 15.3333
9990098 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TAYD* | RXYQ120TAYD* |  |  | RXYQ192TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.35 | 21.7 | 206000 | 3.45 | 134000 | 2.25 | R-410A | 15.3333
9990099 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TATJ* | RXYQ120TATJ* |  |  | RXYQ216TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 20.8 | 230000 | 3.66 | 158000 | 2.51 | R-410A | 17.1667
9990100 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TAYD* | RXYQ120TAYD* |  |  | RXYQ216TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.8 | 20.8 | 230000 | 3.66 | 158000 | 2.51 | R-410A | 17.1667
9990101 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* |  |  | RXYQ240TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 20.85 | 256000 | 3.48 | 170000 | 2.37 | R-410A | 19
9990102 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* |  |  | RXYQ240TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 20.85 | 256000 | 3.48 | 170000 | 2.37 | R-410A | 19
9990302 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 | AOUA72RLBV1 |  |  | AOUA144RLBVG1 | Ducted Indoor Units | 138000 | 11.4 | 20.4 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
9990303 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA72RLBV1 |  |  | AOUA168RLBVG1 | Ducted Indoor Units | 160000 | 11 | 20 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
9990304 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA72RLBV1 |  |  | AOUA192RLBVG1 | Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.57 | 142000 | 2.36 | R-410A | 15.3333
9990305 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA96RLBV1 |  |  | AOUA216RLBVG1 | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
9990306 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA120RLBV1 |  |  | AOUA240RLBVG1 | Ducted Indoor Units | 228000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
9990309 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV1 | AOUA72RLBV1 |  |  | AOUA144RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 21.3 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
9990310 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA72RLBV1 |  |  | AOUA168RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.1 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
9990311 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA72RLBV1 |  |  | AOUA192RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 22.4 | 206000 | 3.66 | 142000 | 2.42 | R-410A | 15.3333
9990312 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA96RLBV1 |  |  | AOUA216RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
9990313 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLBV1 | AOUA120RLBV1 |  |  | AOUA240RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
9302730 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Ducted Indoor Units | 156000 | 12 | 22 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
9302731 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 12.25 | 22 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
9302732 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA072HDS5-1 |  |  | 38VMA168HDS5-1 | Non-Ducted Indoor Units | 156000 | 12.5 | 22 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
9302733 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Ducted Indoor Units | 156000 | 12 | 22 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
9302734 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 12.25 | 22 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
9302735 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA072HDS6-1 |  |  | 38VMA168HDS6-1 | Non-Ducted Indoor Units | 156000 | 12.5 | 22 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
9302736 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Ducted Indoor Units | 176000 | 11.6 | 22 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
9302737 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 11.95 | 21.75 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
9302738 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA192HDS5-1 | Non-Ducted Indoor Units | 176000 | 12.3 | 21.5 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
9302739 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Ducted Indoor Units | 176000 | 11.6 | 22 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
9302740 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 11.95 | 21.75 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
9302741 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA192HDS6-1 | Non-Ducted Indoor Units | 176000 | 12.3 | 21.5 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
9302742 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA216HDS5-1 | Ducted Indoor Units | 196000 | 11.3 | 21.3 | 224000 | 3.54 | 152000 | 2.3 | R-410A | 16.3333
9302743 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA216HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 196000 | 11.5 | 20.9 | 224000 | 3.58 | 152000 | 2.35 | R-410A | 16.3333
9302744 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  |  | 38VMA216HDS5-1 | Non-Ducted Indoor Units | 196000 | 11.7 | 20.5 | 224000 | 3.62 | 152000 | 2.4 | R-410A | 16.3333
9302745 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA216HDS6-1 | Ducted Indoor Units | 196000 | 11.3 | 21.3 | 224000 | 3.54 | 152000 | 2.3 | R-410A | 16.3333
9302746 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA216HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 196000 | 11.5 | 20.9 | 224000 | 3.58 | 152000 | 2.35 | R-410A | 16.3333
9302747 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  |  | 38VMA216HDS6-1 | Non-Ducted Indoor Units | 196000 | 11.7 | 20.5 | 224000 | 3.62 | 152000 | 2.4 | R-410A | 16.3333
9302748 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA240HDS5-1 | Ducted Indoor Units | 214000 | 11 | 20.6 | 240000 | 3.47 | 160000 | 2.3 | R-410A | 17.8333
9302749 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA240HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 10.85 | 20.3 | 240000 | 3.5 | 160000 | 2.32 | R-410A | 17.8333
9302750 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA240HDS5-1 | Non-Ducted Indoor Units | 214000 | 10.7 | 20 | 240000 | 3.54 | 160000 | 2.35 | R-410A | 17.8333
9302751 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA240HDS6-1 | Ducted Indoor Units | 214000 | 11 | 20.6 | 240000 | 3.47 | 160000 | 2.3 | R-410A | 17.8333
9302752 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA240HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 10.85 | 20.3 | 240000 | 3.5 | 160000 | 2.32 | R-410A | 17.8333
9302753 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA240HDS6-1 | Non-Ducted Indoor Units | 214000 | 10.7 | 20 | 240000 | 3.54 | 160000 | 2.35 | R-410A | 17.8333
9133446 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V | TVRF-OC96KHP/220V |  |  | TVRF-OC192KHP/220V | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.95 | 22.15 | 206000 | 3.32 | 134000 | 2.18 | R-410A | 15.3333
9133436 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/220V | TVRF-OC72KHP/220V |  |  | TVRF-OC144KHP/220V | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
9133438 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC72KHP/220V | TVRF-OC72KHP/220V |  |  | TVRF-OC144KHP/220V | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 21.6 | 154000 | 3.5 | 100000 | 2.3 | R-410A | 11.5
9088668 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712 | IOV072H3CDC712 |  |  | IOV144H3CDC724 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 23.3 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
8657018 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144ZKMU-A |  |  |  | PUHY-P144ZKMU-A | Non-Ducted Indoor Units | 136000 | 13.1 | 23.9 | 152000 | 3.73 | 109000 | 2.22 | R-410A | 11.3333
8657020 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P72ZKMU-A |  |  | PUHY-P168ZSKMU-A | Non-Ducted Indoor Units | 160000 | 13.3 | 24.8 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
8657022 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P72ZKMU-A |  |  | PUHY-P192ZSKMU-A | Non-Ducted Indoor Units | 182000 | 13.2 | 23.7 | 204000 | 3.68 | 150000 | 2.17 | R-410A | 15.1667
8657024 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P96ZKMU-A |  |  | PUHY-P216ZSKMU-A | Non-Ducted Indoor Units | 206000 | 12.7 | 23.2 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
9122308 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H72DZN1 |  |  | MV5-H168DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 12.25 | 22 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
9122309 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H96DZN1 |  |  | MV5-H196DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 11.95 | 21.75 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
9122310 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 |  |  | MV5-H216DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 196000 | 11.5 | 20.9 | 224000 | 3.58 | 152000 | 2.35 | R-410A | 16.3333
9122311 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 |  |  | MV5-H240DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 10.85 | 20.3 | 240000 | 3.5 | 160000 | 2.32 | R-410A | 17.8333
9122950 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Non-Ducted Indoor Units | 138000 | 12.5 | 26.6 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
9122951 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL |  |  |  | MMY-MAP1686FT6P-UL | Non-Ducted Indoor Units | 160000 | 11 | 24 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
9122952 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Non-Ducted Indoor Units | 184000 | 12.5 | 26.9 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
9122953 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Non-Ducted Indoor Units | 184000 | 12 | 26 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
9122954 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Non-Ducted Indoor Units | 206000 | 11.9 | 24.9 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
9122955 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Non-Ducted Indoor Units | 230000 | 11.9 | 24 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
9122956 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP240S6FT6P-UL | Non-Ducted Indoor Units | 230000 | 11 | 23.5 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
9122977 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Ducted Indoor Units | 138000 | 12 | 23 | 154000 | 3.6 | 109000 | 2.54 | R-410A | 11.5
9122978 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Non-Ducted Indoor Units | 138000 | 12.5 | 26.6 | 154000 | 3.75 | 109000 | 2.6 | R-410A | 11.5
9122979 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Ducted Indoor Units | 138000 | 12 | 23 | 154000 | 3.6 | 109000 | 2.54 | R-410A | 11.5
9122980 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL |  |  |  | MMY-MAP1686FT6P-UL | Ducted Indoor Units | 160000 | 11 | 22 | 180000 | 3.3 | 132000 | 2.4 | R-410A | 13.3333
9122981 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL |  |  |  | MMY-MAP1686FT9P-UL | Non-Ducted Indoor Units | 160000 | 11 | 24 | 180000 | 3.44 | 132000 | 2.4 | R-410A | 13.3333
9122982 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL |  |  |  | MMY-MAP1686FT9P-UL | Ducted Indoor Units | 160000 | 11 | 22 | 180000 | 3.3 | 132000 | 2.4 | R-410A | 13.3333
9122983 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Ducted Indoor Units | 184000 | 12.2 | 24 | 206000 | 3.75 | 150000 | 2.5 | R-410A | 15.3333
9122984 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Non-Ducted Indoor Units | 184000 | 12.5 | 26.9 | 206000 | 3.7 | 150000 | 2.5 | R-410A | 15.3333
9122985 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Ducted Indoor Units | 184000 | 12.2 | 24 | 206000 | 3.75 | 150000 | 2.5 | R-410A | 15.3333
9122986 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Ducted Indoor Units | 184000 | 12 | 23.5 | 206000 | 3.65 | 150000 | 2.45 | R-410A | 15.3333
9122987 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Non-Ducted Indoor Units | 184000 | 12 | 26 | 206000 | 3.6 | 150000 | 2.45 | R-410A | 15.3333
9122988 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Ducted Indoor Units | 184000 | 12 | 23.5 | 206000 | 3.65 | 150000 | 2.45 | R-410A | 15.3333
9122989 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Ducted Indoor Units | 206000 | 11.8 | 23.5 | 232000 | 3.8 | 164000 | 2.48 | R-410A | 17.1667
9122990 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Non-Ducted Indoor Units | 206000 | 11.9 | 24.9 | 232000 | 3.57 | 164000 | 2.46 | R-410A | 17.1667
9122991 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Ducted Indoor Units | 206000 | 11.8 | 23.5 | 232000 | 3.8 | 164000 | 2.48 | R-410A | 17.1667
9122992 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Ducted Indoor Units | 230000 | 11.9 | 23 | 256000 | 3.6 | 182000 | 2.5 | R-410A | 19.1667
9122993 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Non-Ducted Indoor Units | 230000 | 11.9 | 24 | 256000 | 3.6 | 182000 | 2.53 | R-410A | 19.1667
9122994 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Ducted Indoor Units | 230000 | 11.9 | 23 | 256000 | 3.6 | 182000 | 2.5 | R-410A | 19.1667
9122995 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP240S6FT6P-UL | Ducted Indoor Units | 230000 | 11 | 22.5 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
9122996 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP240S6FT9P-UL | Non-Ducted Indoor Units | 230000 | 11 | 23.5 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
9122997 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP240S6FT9P-UL | Ducted Indoor Units | 230000 | 11 | 22.5 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
9123037 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL |  |  |  | MMY-MAP1446FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.25 | 24.8 | 154000 | 3.67 | 109000 | 2.57 | R-410A | 11.5
9123038 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL |  |  |  | MMY-MAP1446FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.25 | 24.8 | 154000 | 3.67 | 109000 | 2.57 | R-410A | 11.5
9123039 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL |  |  |  | MMY-MAP1686FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 23 | 180000 | 3.37 | 132000 | 2.4 | R-410A | 13.3333
9123040 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL |  |  |  | MMY-MAP1686FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 23 | 180000 | 3.37 | 132000 | 2.4 | R-410A | 13.3333
9123041 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP1926FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.35 | 25.45 | 206000 | 3.72 | 150000 | 2.5 | R-410A | 15.3333
9123042 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0966FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP1926FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.35 | 25.45 | 206000 | 3.72 | 150000 | 2.5 | R-410A | 15.3333
9123043 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0726FT6P-UL |  |  | MMY-AP192S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12 | 24.75 | 206000 | 3.62 | 150000 | 2.45 | R-410A | 15.3333
9123044 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0726FT9P-UL |  |  | MMY-AP192S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12 | 24.75 | 206000 | 3.62 | 150000 | 2.45 | R-410A | 15.3333
9123045 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2166FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.85 | 24.2 | 232000 | 3.68 | 164000 | 2.47 | R-410A | 17.1667
9123046 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2166FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.85 | 24.2 | 232000 | 3.68 | 164000 | 2.47 | R-410A | 17.1667
9123047 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP0966FT6P-UL |  |  | MMY-AP2406FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.9 | 23.5 | 256000 | 3.6 | 182000 | 2.51 | R-410A | 19.1667
9123048 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP0966FT9P-UL |  |  | MMY-AP2406FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.9 | 23.5 | 256000 | 3.6 | 182000 | 2.51 | R-410A | 19.1667
9123049 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP240S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 23 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
9123050 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP240S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11 | 23 | 256000 | 3.5 | 182000 | 2.38 | R-410A | 19.1667
9121962 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H72DXN1 |  |  | MV5-H168DXN1 | Non-Ducted Indoor Units | 156000 | 12.5 | 22 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
9121963 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H72DXN1 |  |  | MV5-H168DXN1 | Ducted Indoor Units | 156000 | 12 | 22 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
9121964 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H96DXN1 |  |  | MV5-H196DXN1 | Non-Ducted Indoor Units | 176000 | 12.3 | 21.5 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
9121965 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H96DXN1 |  |  | MV5-H196DXN1 | Ducted Indoor Units | 176000 | 11.6 | 22 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
9121966 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 |  |  | MV5-H216DXN1 | Non-Ducted Indoor Units | 196000 | 11.7 | 20.5 | 224000 | 3.62 | 152000 | 2.4 | R-410A | 16.3333
9121967 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 |  |  | MV5-H216DXN1 | Ducted Indoor Units | 196000 | 11.3 | 21.3 | 224000 | 3.54 | 152000 | 2.3 | R-410A | 16.3333
9121968 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 |  |  | MV5-H240DXN1 | Non-Ducted Indoor Units | 214000 | 10.7 | 20 | 240000 | 3.54 | 160000 | 2.35 | R-410A | 17.8333
9121969 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 |  |  | MV5-H240DXN1 | Ducted Indoor Units | 214000 | 11 | 20.6 | 240000 | 3.47 | 160000 | 2.3 | R-410A | 17.8333
9121983 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H72DZN1 |  |  | MV5-H168DZN1 | Non-Ducted Indoor Units | 156000 | 12.5 | 22 | 180000 | 3.8 | 126000 | 2.55 | R-410A | 13
9121984 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H72DZN1 |  |  | MV5-H168DZN1 | Ducted Indoor Units | 156000 | 12 | 22 | 180000 | 3.64 | 126000 | 2.35 | R-410A | 13
9121985 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H96DZN1 |  |  | MV5-H196DZN1 | Non-Ducted Indoor Units | 176000 | 12.3 | 21.5 | 206000 | 3.75 | 144000 | 2.45 | R-410A | 14.6667
9121986 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DZN1 | MV5-H96DZN1 |  |  | MV5-H196DZN1 | Ducted Indoor Units | 176000 | 11.6 | 22 | 206000 | 3.6 | 144000 | 2.3 | R-410A | 14.6667
9121987 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 |  |  | MV5-H216DZN1 | Non-Ducted Indoor Units | 196000 | 11.7 | 20.5 | 224000 | 3.62 | 152000 | 2.4 | R-410A | 16.3333
9121988 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 |  |  | MV5-H216DZN1 | Ducted Indoor Units | 196000 | 11.3 | 21.3 | 224000 | 3.54 | 152000 | 2.3 | R-410A | 16.3333
9121989 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 |  |  | MV5-H240DZN1 | Non-Ducted Indoor Units | 214000 | 10.7 | 20 | 240000 | 3.54 | 160000 | 2.35 | R-410A | 17.8333
9121990 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 |  |  | MV5-H240DZN1 | Ducted Indoor Units | 214000 | 11 | 20.6 | 240000 | 3.47 | 160000 | 2.3 | R-410A | 17.8333
9122292 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H72DXN1 |  |  | MV5-H168DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 12.25 | 22 | 180000 | 3.72 | 126000 | 2.45 | R-410A | 13
9122293 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H96DXN1 | MV5-H96DXN1 |  |  | MV5-H196DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 176000 | 11.95 | 21.75 | 206000 | 3.67 | 144000 | 2.37 | R-410A | 14.6667
9122294 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 |  |  | MV5-H216DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 196000 | 11.5 | 20.9 | 224000 | 3.58 | 152000 | 2.35 | R-410A | 16.3333
9122295 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 |  |  | MV5-H240DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 214000 | 10.85 | 20.3 | 240000 | 3.5 | 160000 | 2.32 | R-410A | 17.8333
9045754 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP072B31CW |  |  | TVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
9045756 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP072B41CW |  |  | TVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
9045778 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP072B31CW |  |  | HVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
9045780 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP072B41CW |  |  | HVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
9045802 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP072B31CW |  |  | YVAHP168B31CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
9045804 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP072B41CW |  |  | YVAHP168B41CW | Non-Ducted Indoor Units | 160000 | 10.8 | 18.5 | 178000 | 3.77 | 150000 | 2.2 | R-410A | 13.3333
9060358 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP240*31S | Ducted Indoor Units | 228000 | 11.9 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19
9060360 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP240*41S | Ducted Indoor Units | 228000 | 11.3 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19
9060361 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP240*41S | Non-Ducted Indoor Units | 228000 | 10.9 | 19.8 | 258000 | 3.68 | 182000 | 2.32 | R-410A | 19
9060362 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR240*31S | Ducted Indoor Units | 228000 | 11.9 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19
9060364 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR240*41S | Ducted Indoor Units | 228000 | 11.3 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19
9060365 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR240*41S | Non-Ducted Indoor Units | 228000 | 10.9 | 19.8 | 258000 | 3.68 | 182000 | 2.32 | R-410A | 19
9060374 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP240*31S | Ducted Indoor Units | 228000 | 11.9 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19
9060376 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP240*41S | Ducted Indoor Units | 228000 | 11.3 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19
9060377 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP240*41S | Non-Ducted Indoor Units | 228000 | 10.9 | 19.8 | 258000 | 3.68 | 182000 | 2.32 | R-410A | 19
9060378 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR240*31S | Ducted Indoor Units | 228000 | 11.9 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19
9060380 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR240*41S | Ducted Indoor Units | 228000 | 11.3 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19
9060381 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR240*41S | Non-Ducted Indoor Units | 228000 | 10.9 | 19.8 | 258000 | 3.68 | 182000 | 2.32 | R-410A | 19
9060390 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP240*31S | Ducted Indoor Units | 228000 | 11.9 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19
9060392 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP240*41S | Ducted Indoor Units | 228000 | 11.3 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19
9060393 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP240*41S | Non-Ducted Indoor Units | 228000 | 10.9 | 19.8 | 258000 | 3.68 | 182000 | 2.32 | R-410A | 19
9060394 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR240*31S | Ducted Indoor Units | 228000 | 11.9 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19
9060396 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR240*41S | Ducted Indoor Units | 228000 | 11.3 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19
9060397 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR240*41S | Non-Ducted Indoor Units | 228000 | 10.9 | 19.8 | 258000 | 3.68 | 182000 | 2.32 | R-410A | 19
9060406 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP240*31S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.25 | 20.35 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19
9060407 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP240*41S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19
9060408 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR240*31S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.25 | 20.4 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19
9060409 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR240*41S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19
9060414 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP240*31S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.25 | 20.35 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19
9060415 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP240*41S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19
9060416 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR240*31S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.25 | 20.4 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19
9060417 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR240*41S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19
9060422 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP240*31S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.25 | 20.35 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19
9060423 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP240*41S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19
9060424 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR240*31S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.25 | 20.4 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19
9060425 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR240*41S | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.1 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19
9085402 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
9085403 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Ducted Indoor Units | 138000 | 11.6 | 22.1 | 154000 | 4 | 109000 | 2.85 | R-410A | 11.5
9085404 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
9085405 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Ducted Indoor Units | 160000 | 11.2 | 21 | 180000 | 3.7 | 132000 | 2.7 | R-410A | 13.3333
9085406 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
9085407 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Ducted Indoor Units | 184000 | 12.7 | 23 | 206000 | 4.1 | 150000 | 2.95 | R-410A | 15.3333
9085408 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
9085409 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Ducted Indoor Units | 184000 | 12.3 | 22.6 | 206000 | 3.92 | 150000 | 2.8 | R-410A | 15.3333
9085410 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
9085411 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Ducted Indoor Units | 206000 | 12.5 | 22.5 | 232000 | 4 | 164000 | 2.92 | R-410A | 17.1667
9085412 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
9085413 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Ducted Indoor Units | 230000 | 12.4 | 22.2 | 256000 | 4 | 182000 | 2.95 | R-410A | 19.1667
9085414 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
9085415 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Ducted Indoor Units | 230000 | 12.3 | 21.8 | 256000 | 3.95 | 182000 | 2.9 | R-410A | 19.1667
9085441 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL |  |  |  | MMY-MAP1446HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12 | 23.85 | 154000 | 4.06 | 109000 | 2.79 | R-410A | 11.5
9085442 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL |  |  |  | MMY-MAP1686HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 22.4 | 180000 | 3.72 | 132000 | 2.59 | R-410A | 13.3333
9085443 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0966HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP1926HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.75 | 24.25 | 206000 | 4.07 | 150000 | 2.85 | R-410A | 15.3333
9085444 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0726HT9P-UL |  |  | MMY-AP192S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.45 | 23.85 | 206000 | 3.93 | 150000 | 2.74 | R-410A | 15.3333
9085445 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2166HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.25 | 23.55 | 232000 | 3.95 | 164000 | 2.83 | R-410A | 17.1667
9085446 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP0966HT9P-UL |  |  | MMY-AP2406HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.2 | 23.15 | 256000 | 3.87 | 182000 | 2.8 | R-410A | 19.1667
9085447 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP240S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.95 | 22.7 | 256000 | 3.82 | 182000 | 2.76 | R-410A | 19.1667
8578650 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R144DZN1-(A) |  |  |  | MV5-R144DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 10.8 | 19.5 | 150000 | 3.37 | 102000 | 2.25 | R-410A | 11.3333
8578651 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X144DZN1-(A) |  |  |  | MV5-X144DZN1-(A) | Non-Ducted Indoor Units | 136000 | 10.9 | 19.5 | 150000 | 3.4 | 102000 | 2.28 | R-410A | 11.3333
8656998 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144ZKMU-A |  |  |  | PURY-P144ZKMU-A | Non-Ducted Indoor Units | 136000 | 12.8 | 21.9 | 152000 | 3.57 | 97000 | 2.13 | R-410A | 11.3333
8657000 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96ZKMU-A | PURY-P72ZKMU-A |  |  | PURY-P168ZSKMU-A | Non-Ducted Indoor Units | 160000 | 12.4 | 21 | 178000 | 3.6 | 119000 | 2.13 | R-410A | 13.3333
8657002 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96ZKMU-A | PURY-P96ZKMU-A |  |  | PURY-P192ZSKMU-A | Non-Ducted Indoor Units | 182000 | 11.8 | 21.2 | 204000 | 3.48 | 142000 | 2.1 | R-410A | 15.1667
8989554 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Non-Ducted Indoor Units | 138000 | 12.4 | 25.6 | 154000 | 4.12 | 109000 | 2.73 | R-410A | 11.5
8989555 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Non-Ducted Indoor Units | 160000 | 11 | 23.8 | 180000 | 3.74 | 132000 | 2.48 | R-410A | 13.3333
8989556 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0966HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.8 | 25.5 | 206000 | 4.05 | 150000 | 2.76 | R-410A | 15.3333
8989557 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Non-Ducted Indoor Units | 184000 | 12.6 | 25.1 | 206000 | 3.95 | 150000 | 2.68 | R-410A | 15.3333
8989558 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Non-Ducted Indoor Units | 206000 | 12 | 24.6 | 232000 | 3.9 | 164000 | 2.75 | R-410A | 17.1667
8989559 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Non-Ducted Indoor Units | 230000 | 12 | 24.1 | 256000 | 3.75 | 182000 | 2.66 | R-410A | 19.1667
8989569 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Ducted Indoor Units | 138000 | 11.6 | 22.1 | 154000 | 4 | 109000 | 2.85 | R-410A | 11.5
8989570 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Ducted Indoor Units | 160000 | 11.2 | 21 | 180000 | 3.7 | 132000 | 2.7 | R-410A | 13.3333
8989571 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0966HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Ducted Indoor Units | 184000 | 12.7 | 23 | 206000 | 4.1 | 150000 | 2.95 | R-410A | 15.3333
8989572 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Ducted Indoor Units | 184000 | 12.3 | 22.6 | 206000 | 3.92 | 150000 | 2.8 | R-410A | 15.3333
8989573 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Ducted Indoor Units | 206000 | 12.5 | 22.5 | 232000 | 4 | 164000 | 2.92 | R-410A | 17.1667
8989574 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Ducted Indoor Units | 230000 | 12.4 | 22.2 | 256000 | 4 | 182000 | 2.95 | R-410A | 19.1667
8989575 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Non-Ducted Indoor Units | 230000 | 11.6 | 23.6 | 256000 | 3.7 | 182000 | 2.62 | R-410A | 19.1667
8989610 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL |  |  |  | MMY-MAP1446HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12 | 23.85 | 154000 | 4.06 | 109000 | 2.79 | R-410A | 11.5
8989611 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL |  |  |  | MMY-MAP1686HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.1 | 22.4 | 180000 | 3.72 | 132000 | 2.59 | R-410A | 13.3333
8989612 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP0966HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP1926HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.75 | 24.25 | 206000 | 4.07 | 150000 | 2.85 | R-410A | 15.3333
8989613 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP0726HT6P-UL |  |  | MMY-AP192S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.45 | 23.85 | 206000 | 3.93 | 150000 | 2.74 | R-410A | 15.3333
8989614 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP2166HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.25 | 23.55 | 232000 | 3.95 | 164000 | 2.83 | R-410A | 17.1667
8989615 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP0966HT6P-UL |  |  | MMY-AP2406HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 12.2 | 23.15 | 256000 | 3.87 | 182000 | 2.8 | R-410A | 19.1667
8989616 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Ducted Indoor Units | 230000 | 12.3 | 21.8 | 256000 | 3.95 | 182000 | 2.9 | R-410A | 19.1667
8989622 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP240S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.95 | 22.7 | 256000 | 3.82 | 182000 | 2.76 | R-410A | 19.1667
8578653 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X144DZN1-(A) |  |  |  | MV5-X144DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 10.75 | 19.5 | 150000 | 3.4 | 102000 | 2.28 | R-410A | 11.3333
8577925 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R144DXN1-(A) |  |  |  | MV5-R144DXN1-(A) | Non-Ducted Indoor Units | 136000 | 11 | 19.5 | 150000 | 3.4 | 102000 | 2.25 | R-410A | 11.3333
8578410 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R144DXN1-(A) |  |  |  | MV5-R144DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 10.8 | 19.5 | 150000 | 3.37 | 102000 | 2.25 | R-410A | 11.3333
8578615 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X144DXN1-(A) |  |  |  | MV5-X144DXN1-(A) | Non-Ducted Indoor Units | 136000 | 10.9 | 19.5 | 150000 | 3.4 | 102000 | 2.28 | R-410A | 11.3333
8578639 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X144DXN1-(A) |  |  |  | MV5-X144DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 10.75 | 19.5 | 150000 | 3.37 | 102000 | 2.28 | R-410A | 11.3333
7041885 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU |  |  |  | RXYQ144TTJU | Ducted Indoor Units | 138000 | 11.5 | 21 | 154000 | 3.72 | 96000 | 2.2 | R-410A | 11.5
7041886 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN |  |  |  | RXYQ144TYDN | Ducted Indoor Units | 138000 | 11.5 | 21 | 154000 | 3.72 | 96000 | 2.2 | R-410A | 11.5
7041887 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU |  |  |  | RXYQ144TTJU | Non-Ducted Indoor Units | 138000 | 12.3 | 24.1 | 154000 | 4.1 | 96000 | 2.33 | R-410A | 11.5
7041888 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN |  |  |  | RXYQ144TYDN | Non-Ducted Indoor Units | 138000 | 12.3 | 24.1 | 154000 | 4.1 | 96000 | 2.33 | R-410A | 11.5
7041893 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TTJU | RXYQ120TTJU |  |  | RXYQ192TTJU | Ducted Indoor Units | 184000 | 12.3 | 20.7 | 206000 | 3.6 | 134000 | 2.4 | R-410A | 15.3333
7041894 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TYDN | RXYQ120TYDN |  |  | RXYQ192TYDN | Ducted Indoor Units | 184000 | 12.3 | 20.7 | 206000 | 3.6 | 134000 | 2.4 | R-410A | 15.3333
7041895 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TTJU | RXYQ120TTJU |  |  | RXYQ192TTJU | Non-Ducted Indoor Units | 184000 | 11.9 | 22.2 | 206000 | 3.8 | 134000 | 2.27 | R-410A | 15.3333
7041896 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TYDN | RXYQ120TYDN |  |  | RXYQ192TYDN | Non-Ducted Indoor Units | 184000 | 11.9 | 22.2 | 206000 | 3.8 | 134000 | 2.27 | R-410A | 15.3333
7041913 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU | RXYQ120TTJU |  |  | RXYQ216TTJU | Ducted Indoor Units | 206000 | 11.7 | 20 | 230000 | 3.65 | 158000 | 2.48 | R-410A | 17.1667
7041914 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN | RXYQ120TYDN |  |  | RXYQ216TYDN | Ducted Indoor Units | 206000 | 11.7 | 20 | 230000 | 3.65 | 158000 | 2.48 | R-410A | 17.1667
7041915 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU | RXYQ120TTJU |  |  | RXYQ216TTJU | Non-Ducted Indoor Units | 206000 | 11.6 | 20.5 | 230000 | 3.83 | 158000 | 2.62 | R-410A | 17.1667
7041916 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN | RXYQ120TYDN |  |  | RXYQ216TYDN | Non-Ducted Indoor Units | 206000 | 11.6 | 20.5 | 230000 | 3.83 | 158000 | 2.62 | R-410A | 17.1667
7042715 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU |  |  |  | RXYQ144TTJU | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.9 | 22.55 | 154000 | 3.91 | 96000 | 2.26 | R-410A | 11.5
7042716 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN |  |  |  | RXYQ144TYDN | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.9 | 22.55 | 154000 | 3.91 | 96000 | 2.26 | R-410A | 11.5
7042719 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TTJU | RXYQ120TTJU |  |  | RXYQ192TTJU | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.1 | 21.45 | 206000 | 3.7 | 134000 | 2.33 | R-410A | 15.3333
7042720 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ72TYDN | RXYQ120TYDN |  |  | RXYQ192TYDN | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 12.1 | 21.45 | 206000 | 3.7 | 134000 | 2.33 | R-410A | 15.3333
7042721 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU | RXYQ120TTJU |  |  | RXYQ216TTJU | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.25 | 230000 | 3.74 | 158000 | 2.55 | R-410A | 17.1667
7042722 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN | RXYQ120TYDN |  |  | RXYQ216TYDN | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 20.25 | 230000 | 3.74 | 158000 | 2.55 | R-410A | 17.1667
7064754 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ120TTJU |  |  | RXYQ240TTJU | Ducted Indoor Units | 228000 | 11.6 | 18.4 | 256000 | 3.55 | 172000 | 2.43 | R-410A | 19
7064755 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ120TYDN |  |  | RXYQ240TYDN | Ducted Indoor Units | 228000 | 11.6 | 18.4 | 256000 | 3.55 | 172000 | 2.43 | R-410A | 19
7064756 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ120TTJU |  |  | RXYQ240TTJU | Non-Ducted Indoor Units | 228000 | 11.5 | 20.8 | 256000 | 3.63 | 172000 | 2.62 | R-410A | 19
7064757 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ120TYDN |  |  | RXYQ240TYDN | Non-Ducted Indoor Units | 228000 | 11.5 | 20.8 | 256000 | 3.63 | 172000 | 2.62 | R-410A | 19
7064759 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ120TTJU |  |  | RXYQ240TTJU | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.55 | 19.6 | 256000 | 3.59 | 172000 | 2.52 | R-410A | 19
7064760 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ120TYDN |  |  | RXYQ240TYDN | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.55 | 19.6 | 256000 | 3.59 | 172000 | 2.52 | R-410A | 19
7159062 | 1/1/2027 | PANASONIC | HMSV-A-CB | U-144ME2U9 |  |  |  | U-144ME2U9 | Non-Ducted Indoor Units | 138000 | 10.9 | 23.4 | 154000 | 3.41 | 100000 | 2.45 | R-410A | 11.5
7159374 | 1/1/2027 | PANASONIC | HMSV-A-CB | U-96ME2U9 | U-96ME2U9 |  |  | WU-192ME2U9 | Non-Ducted Indoor Units | 184000 | 11.9 | 22.4 | 206000 | 3.25 | 134000 | 2.39 | R-410A | 15.3333
7490342 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TKMU-U |  |  |  | PUHY-P144TKMU-U | Non-Ducted Indoor Units | 136000 | 11.8 | 20.2 | 152000 | 3.72 | 109000 | 2.22 | R-410A | 11.3333
7490343 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TKMU-U |  |  |  | PUHY-P144TKMU-U | Ducted Indoor Units | 136000 | 11.6 | 19.3 | 152000 | 3.56 | 109000 | 2.32 | R-410A | 11.3333
7490344 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YKMU-U |  |  |  | PUHY-P144YKMU-U | Non-Ducted Indoor Units | 136000 | 11.8 | 20.2 | 152000 | 3.72 | 109000 | 2.22 | R-410A | 11.3333
7490345 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YKMU-U |  |  |  | PUHY-P144YKMU-U | Ducted Indoor Units | 136000 | 11.6 | 19.3 | 152000 | 3.56 | 108000 | 2.32 | R-410A | 11.3333
7490347 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-U | PUHY-P72YKMU-U |  |  | PUHY-P144YSKMU-U | Non-Ducted Indoor Units | 136000 | 13.2 | 20.3 | 152000 | 3.95 | 109000 | 2.13 | R-410A | 11.3333
7490349 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-U | PUHY-P72YKMU-U |  |  | PUHY-P144YSKMU-U | Ducted Indoor Units | 136000 | 12.8 | 19.3 | 152000 | 3.79 | 108000 | 2.56 | R-410A | 11.3333
7490351 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-U | PUHY-P72TKMU-U |  |  | PUHY-P168TSKMU-U | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
7490353 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-U | PUHY-P72TKMU-U |  |  | PUHY-P168TSKMU-U | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
7490355 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-U | PUHY-P72YKMU-U |  |  | PUHY-P168YSKMU-U | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
7490356 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-U | PUHY-P72YKMU-U |  |  | PUHY-P168YSKMU-U | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
7490358 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P72TKMU-U |  |  | PUHY-P192TSKMU-U | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
7490360 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P72TKMU-U |  |  | PUHY-P192TSKMU-U | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 204000 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
7490362 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P72YKMU-U |  |  | PUHY-P192YSKMU-U | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
7490363 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P72YKMU-U |  |  | PUHY-P192YSKMU-U | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 20400 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
7490365 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P96TKMU-U |  |  | PUHY-P216TSKMU-U | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
7490367 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P96TKMU-U |  |  | PUHY-P216TSKMU-U | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
7490369 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P96YKMU-U |  |  | PUHY-P216YSKMU-U | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
7490370 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P96YKMU-U |  |  | PUHY-P216YSKMU-U | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
7490374 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P120TKMU-U |  |  | PUHY-P240TSKMU-U | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
7490377 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P120YKMU-U |  |  | PUHY-P240YSKMU-U | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
7490430 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-U |  |  |  | PURY-P144TKMU-U | Ducted Indoor Units | 136000 | 11.7 | 18 | 152000 | 3.41 | 109000 | 2.32 | R-410A | 11.3333
7490432 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-U |  |  |  | PURY-P144YKMU-U | Ducted Indoor Units | 136000 | 11.7 | 18 | 152000 | 3.41 | 109000 | 2.32 | R-410A | 11.3333
7490434 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-U | PURY-P72YKMU-U |  |  | PURY-P144YSKMU-U | Ducted Indoor Units | 136000 | 12 | 18.8 | 152000 | 3.54 | 109000 | 2.41 | R-410A | 11.3333
7490435 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-U | PURY-P72YKMU-U |  |  | PURY-P144YSKMU-U | Non-Ducted Indoor Units | 136000 | 14.4 | 20.6 | 152000 | 3.65 | 109000 | 2.3 | R-410A | 11.3333
7490436 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-U | PURY-P72TKMU-U |  |  | PURY-P168TSKMU-U | Ducted Indoor Units | 160000 | 12.1 | 19.4 | 178000 | 3.63 | 132000 | 2.54 | R-410A | 13.3333
7490437 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-U | PURY-P72TKMU-U |  |  | PURY-P168TSKMU-U | Non-Ducted Indoor Units | 160000 | 12.9 | 19.1 | 178000 | 3.52 | 132000 | 2.22 | R-410A | 13.3333
7490438 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-U | PURY-P72YKMU-U |  |  | PURY-P168YSKMU-U | Ducted Indoor Units | 160000 | 12.1 | 19.4 | 178000 | 3.63 | 132000 | 2.54 | R-410A | 13.3333
7490439 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-U | PURY-P72YKMU-U |  |  | PURY-P168YSKMU-U | Non-Ducted Indoor Units | 160000 | 12.9 | 19.1 | 178000 | 3.52 | 132000 | 2.22 | R-410A | 13.3333
7490440 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-U | PURY-P96TKMU-U |  |  | PURY-P192TSKMU-U | Ducted Indoor Units | 182000 | 11.6 | 19.3 | 204000 | 3.64 | 150000 | 2.54 | R-410A | 15.1667
7490441 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-U | PURY-P96TKMU-U |  |  | PURY-P192TSKMU-U | Non-Ducted Indoor Units | 182000 | 11.9 | 18.2 | 204000 | 3.47 | 150000 | 2.18 | R-410A | 15.1667
7490442 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-U | PURY-P96YKMU-U |  |  | PURY-P192YSKMU-U | Ducted Indoor Units | 182000 | 11.6 | 19.3 | 204000 | 3.64 | 150000 | 2.54 | R-410A | 15.1667
7490444 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-U | PURY-P96YKMU-U |  |  | PURY-P192YSKMU-U | Non-Ducted Indoor Units | 182000 | 11.9 | 18.2 | 204000 | 3.47 | 150000 | 2.18 | R-410A | 15.1667
7490445 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-U | PURY-P96TKMU-U |  |  | PURY-P216TSKMU-U | Ducted Indoor Units | 206000 | 11.4 | 18.7 | 232000 | 3.54 | 164000 | 2.27 | R-410A | 17.1667
7490446 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-U | PURY-P96TKMU-U |  |  | PURY-P216TSKMU-U | Non-Ducted Indoor Units | 206000 | 11.3 | 18.3 | 232000 | 3.43 | 164000 | 2.16 | R-410A | 17.1667
7490447 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-U | PURY-P96YKMU-U |  |  | PURY-P216YSKMU-U | Ducted Indoor Units | 206000 | 11.4 | 18.7 | 232000 | 3.54 | 164000 | 2.27 | R-410A | 17.1667
7490448 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-U | PURY-P96YKMU-U |  |  | PURY-P216YSKMU-U | Non-Ducted Indoor Units | 206000 | 11.3 | 18.3 | 232000 | 3.43 | 164000 | 2.16 | R-410A | 17.1667
7490451 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-U | PURY-P120TKMU-U |  |  | PURY-P240TSKMU-U | Non-Ducted Indoor Units | 228000 | 10.9 | 18.5 | 258000 | 3.42 | 182000 | 2.15 | R-410A | 19
7490453 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-U | PURY-P120YKMU-U |  |  | PURY-P240YSKMU-U | Non-Ducted Indoor Units | 228000 | 10.9 | 18.5 | 258000 | 3.42 | 182000 | 2.15 | R-410A | 19
7505345 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ144PBTJ |  |  |  | REYQ144PBTJ | Non-Ducted Indoor Units | 138000 | 11.2 | 18.9 | 154000 | 3.6 | 104000 | 2.55 | R-410A | 11.5
7505347 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD |  |  | REYQ144PBYD | Non-Ducted Indoor Units | 138000 | 13.8 | 22.5 | 154000 | 3.8 | 104000 | 2.55 | R-410A | 11.5
7505348 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD |  |  | REYQ144PBYD | Ducted Indoor Units | 138000 | 13.7 | 20 | 154000 | 3.6 | 104000 | 2.4 | R-410A | 11.5
7505349 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ |  |  | REYQ168PBTJ | Non-Ducted Indoor Units | 160000 | 12 | 20.3 | 180000 | 3.7 | 122000 | 2.5 | R-410A | 13.3333
7505350 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ |  |  | REYQ168PBTJ | Ducted Indoor Units | 160000 | 11.5 | 19.4 | 180000 | 3.5 | 122000 | 2.35 | R-410A | 13.3333
7505351 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD |  |  | REYQ168PBYD | Non-Ducted Indoor Units | 160000 | 12 | 20.3 | 180000 | 3.7 | 122000 | 2.5 | R-410A | 13.3333
7505352 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD |  |  | REYQ168PBYD | Ducted Indoor Units | 160000 | 11.5 | 19.4 | 180000 | 3.5 | 122000 | 2.35 | R-410A | 13.3333
7505353 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBTJ | REMQ96PBTJ |  |  | REYQ192PBTJ | Non-Ducted Indoor Units | 184000 | 11.2 | 18.7 | 206000 | 3.4 | 138000 | 2.5 | R-410A | 15.3333
7505354 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBYD | REMQ96PBYD |  |  | REYQ192PBYD | Non-Ducted Indoor Units | 184000 | 11.2 | 18.7 | 206000 | 3.4 | 138000 | 2.5 | R-410A | 15.3333
7505410 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD |  |  | REYQ144PBYD | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.75 | 21.25 | 154000 | 3.7 | 104000 | 2.47 | R-410A | 11.5
7505411 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ |  |  | REYQ168PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.75 | 19.85 | 180000 | 3.6 | 122000 | 2.42 | R-410A | 13.3333
7505412 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD |  |  | REYQ168PBYD | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.75 | 19.85 | 180000 | 3.6 | 122000 | 2.42 | R-410A | 13.3333
7628554 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TTJU |  |  |  | REYQ168TTJU | Non-Ducted Indoor Units | 156000 | 11.7 | 22 | 176000 | 3.77 | 128000 | 2.32 | R-410A | 13
7628557 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TYDN |  |  |  | REYQ168TYDN | Non-Ducted Indoor Units | 156000 | 11.7 | 22 | 176000 | 3.77 | 128000 | 2.32 | R-410A | 13
7628559 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TTJU | REYQ120TTJU |  |  | REYQ192TTJU | Non-Ducted Indoor Units | 180000 | 12.5 | 22.9 | 200000 | 3.84 | 146000 | 2.55 | R-410A | 15
7628561 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TYDN | REYQ120TYDN |  |  | REYQ192TYDN | Non-Ducted Indoor Units | 180000 | 12.5 | 22.9 | 200000 | 3.84 | 146000 | 2.55 | R-410A | 15
7628563 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TTJU | REYQ120TTJU |  |  | REYQ216TTJU | Non-Ducted Indoor Units | 200000 | 12.5 | 22.9 | 226000 | 3.73 | 160000 | 2.45 | R-410A | 16.6667
7628566 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TYDN | REYQ120TYDN |  |  | REYQ216TYDN | Non-Ducted Indoor Units | 200000 | 12.5 | 22.9 | 226000 | 3.73 | 160000 | 2.45 | R-410A | 16.6667
7628567 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ120TTJU |  |  | REYQ240TTJU | Non-Ducted Indoor Units | 222000 | 12.2 | 21.9 | 250000 | 3.67 | 178000 | 2.48 | R-410A | 18.5
7628570 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ120TYDN |  |  | REYQ240TYDN | Non-Ducted Indoor Units | 222000 | 12.2 | 21.9 | 250000 | 3.67 | 178000 | 2.48 | R-410A | 18.5
7628626 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TTJU |  |  |  | REYQ168TTJU | Ducted Indoor Units | 156000 | 11.3 | 20.8 | 176000 | 3.33 | 128000 | 2.15 | R-410A | 13
7628627 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TYDN |  |  |  | REYQ168TYDN | Ducted Indoor Units | 156000 | 11.3 | 20.8 | 176000 | 3.33 | 128000 | 2.15 | R-410A | 13
7628630 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TTJU | REYQ120TTJU |  |  | REYQ192TTJU | Ducted Indoor Units | 180000 | 12.6 | 21.1 | 200000 | 3.67 | 146000 | 2.38 | R-410A | 15
7628632 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TYDN | REYQ120TYDN |  |  | REYQ192TYDN | Ducted Indoor Units | 180000 | 12.6 | 21.1 | 200000 | 3.67 | 146000 | 2.38 | R-410A | 15
7628634 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TTJU | REYQ120TTJU |  |  | REYQ216TTJU | Ducted Indoor Units | 200000 | 12.4 | 20.8 | 226000 | 3.67 | 160000 | 2.28 | R-410A | 16.6667
7628636 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TYDN | REYQ120TYDN |  |  | REYQ216TYDN | Ducted Indoor Units | 200000 | 12.4 | 20.8 | 226000 | 3.67 | 160000 | 2.28 | R-410A | 16.6667
7628639 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ120TTJU |  |  | REYQ240TTJU | Ducted Indoor Units | 222000 | 11.6 | 19.8 | 250000 | 3.55 | 178000 | 2.31 | R-410A | 18.5
7628640 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ120TYDN |  |  | REYQ240TYDN | Ducted Indoor Units | 222000 | 11.6 | 19.8 | 250000 | 3.55 | 178000 | 2.31 | R-410A | 18.5
7629591 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TTJU |  |  |  | REYQ168TTJU | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 11.5 | 21.4 | 176000 | 3.55 | 128000 | 2.23 | R-410A | 13
7629594 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TYDN |  |  |  | REYQ168TYDN | Mixed Ducted and Non-Ducted Indoor Units | 156000 | 11.5 | 21.4 | 176000 | 3.55 | 128000 | 2.23 | R-410A | 13
7629595 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TTJU | REYQ120TTJU |  |  | REYQ192TTJU | Mixed Ducted and Non-Ducted Indoor Units | 180000 | 12.55 | 22 | 200000 | 3.75 | 146000 | 2.46 | R-410A | 15
7629598 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ72TYDN | REYQ120TYDN |  |  | REYQ192TYDN | Mixed Ducted and Non-Ducted Indoor Units | 180000 | 12.55 | 22 | 200000 | 3.75 | 146000 | 2.46 | R-410A | 15
7629601 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TTJU | REYQ120TTJU |  |  | REYQ216TTJU | Mixed Ducted and Non-Ducted Indoor Units | 200000 | 12.45 | 21.85 | 226000 | 3.7 | 160000 | 2.36 | R-410A | 16.6667
7629603 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ96TYDN | REYQ120TYDN |  |  | REYQ216TYDN | Mixed Ducted and Non-Ducted Indoor Units | 200000 | 12.45 | 21.85 | 226000 | 3.7 | 160000 | 2.36 | R-410A | 16.6667
7629606 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ120TTJU |  |  | REYQ240TTJU | Mixed Ducted and Non-Ducted Indoor Units | 222000 | 11.9 | 20.85 | 250000 | 3.61 | 178000 | 2.39 | R-410A | 18.5
7629608 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ120TYDN |  |  | REYQ240TYDN | Mixed Ducted and Non-Ducted Indoor Units | 222000 | 11.9 | 20.85 | 250000 | 3.61 | 178000 | 2.39 | R-410A | 18.5
7849631 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) | GMV-72WM/B-F(U) |  |  | GMV-144WM/B-F(U) | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 10.7 | 23.3 | 154000 | 3.47 | 100000 | 2.32 | R-410A | 11.5
7850825 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV | AOUA72TLCV |  |  | AOUA144TLCVG | Ducted Indoor Units | 138000 | 11.4 | 20.4 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850827 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA72TLCV |  |  | AOUA168TLCVG | Ducted Indoor Units | 160000 | 11 | 20 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850829 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA72TLCV |  |  | AOUA192TLCVG | Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.57 | 142000 | 2.36 | R-410A | 15.3333
7850831 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA96TLCV |  |  | AOUA216TLCVG | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850833 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA120TLCV |  |  | AOUA240TLCVG | Ducted Indoor Units | 228000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7850845 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV | AOUA72RLCV |  |  | AOUA144RLCVG | Ducted Indoor Units | 138000 | 11.4 | 20.4 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850847 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA72RLCV |  |  | AOUA168RLCVG | Ducted Indoor Units | 160000 | 11 | 20 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850849 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA72RLCV |  |  | AOUA192RLCVG | Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.57 | 142000 | 2.36 | R-410A | 15.3333
7850851 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA96RLCV |  |  | AOUA216RLCVG | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850853 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA120RLCV |  |  | AOUA240RLCVG | Ducted Indoor Units | 228000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7850861 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLCV | AOUA72TLCV |  |  | AOUA144TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 21.3 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850862 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA72TLCV |  |  | AOUA168TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.1 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850863 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA72TLCV |  |  | AOUA192TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 22.4 | 206000 | 3.66 | 142000 | 2.42 | R-410A | 15.3333
7850864 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA96TLCV |  |  | AOUA216TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850865 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLCV | AOUA120TLCV |  |  | AOUA240TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7850871 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLCV | AOUA72RLCV |  |  | AOUA144RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 21.3 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
7850872 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA72RLCV |  |  | AOUA168RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.1 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
7850873 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA72RLCV |  |  | AOUA192RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 22.4 | 206000 | 3.66 | 142000 | 2.42 | R-410A | 15.3333
7850874 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA96RLCV |  |  | AOUA216RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
7850875 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA120RLCV | AOUA120RLCV |  |  | AOUA240RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
7987132 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S |  |  | TVAHP144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
7987133 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S |  |  | TVAHP144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
7987134 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S |  |  | TVAHP168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
7987135 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S |  |  | TVAHP168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
7987137 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S |  |  | TVAHP192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
7987139 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
7987141 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
7987152 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S |  |  | TVAHR144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
7987153 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S |  |  | TVAHR144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
7987154 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S |  |  | TVAHR168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
7987155 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S |  |  | TVAHR168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
7987157 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S |  |  | TVAHR192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
7987159 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
7987161 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
7987178 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S |  |  | TVAHP144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
7987179 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S |  |  | TVAHP144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
7987180 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S |  |  | TVAHP168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
7987181 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S |  |  | TVAHP168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
7987185 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
7987187 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
7987198 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S |  |  | TVAHR144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
7987199 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S |  |  | TVAHR144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
7987200 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S |  |  | TVAHR168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
7987201 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S |  |  | TVAHR168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
7987205 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
7987207 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
7987224 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S |  |  | HVAHP144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
7987225 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S |  |  | HVAHP144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
7987226 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S |  |  | HVAHP168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
7987227 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S |  |  | HVAHP168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
7987229 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S |  |  | HVAHP192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
7987231 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
7987233 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
7987244 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S |  |  | HVAHR144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
7987245 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S |  |  | HVAHR144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
7987246 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S |  |  | HVAHR168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
7987247 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S |  |  | HVAHR168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
7987249 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S |  |  | HVAHR192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
7987251 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
7987253 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
7987270 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S |  |  | HVAHP144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
7987271 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S |  |  | HVAHP144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
7987272 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S |  |  | HVAHP168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
7987273 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S |  |  | HVAHP168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
7987277 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
7987279 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
7987290 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S |  |  | HVAHR144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
7987291 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S |  |  | HVAHR144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
7987292 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S |  |  | HVAHR168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
7987293 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S |  |  | HVAHR168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
7987297 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
7987299 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
7987316 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S |  |  | YVAHP144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
7987317 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S |  |  | YVAHP144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
7987318 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S |  |  | YVAHP168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
7987319 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S |  |  | YVAHP168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
7987321 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S |  |  | YVAHP192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
7987323 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
7987325 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.4 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
7987336 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S |  |  | YVAHR144B31S | Non-Ducted Indoor Units | 138000 | 14.4 | 24.2 | 154000 | 4.11 | 109000 | 2.78 | R-410A | 11.5
7987337 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S |  |  | YVAHR144B31S | Ducted Indoor Units | 138000 | 12.3 | 19.7 | 154000 | 3.55 | 109000 | 2.65 | R-410A | 11.5
7987338 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S |  |  | YVAHR168B31S | Non-Ducted Indoor Units | 160000 | 11.4 | 19.7 | 178000 | 3.69 | 129000 | 2.27 | R-410A | 13.3333
7987339 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S |  |  | YVAHR168B31S | Ducted Indoor Units | 160000 | 11.6 | 19.6 | 178000 | 3.68 | 129000 | 2.44 | R-410A | 13.3333
7987341 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S |  |  | YVAHR192B31S | Ducted Indoor Units | 184000 | 10.9 | 19.3 | 204000 | 3.61 | 150000 | 2.47 | R-410A | 15.3333
7987343 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR216B31S | Ducted Indoor Units | 206000 | 11.8 | 20.1 | 232000 | 3.62 | 164000 | 2.39 | R-410A | 17.1667
7987345 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR240B31S | Ducted Indoor Units | 230000 | 11.8 | 20.5 | 258000 | 3.72 | 182000 | 2.55 | R-410A | 19.1667
7987362 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S |  |  | YVAHP144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
7987363 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S |  |  | YVAHP144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
7987364 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S |  |  | YVAHP168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
7987365 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S |  |  | YVAHP168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
7987369 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
7987371 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
7987382 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S |  |  | YVAHR144B41S | Non-Ducted Indoor Units | 138000 | 13.6 | 23.8 | 154000 | 4.04 | 109000 | 2.58 | R-410A | 11.5
7987383 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S |  |  | YVAHR144B41S | Ducted Indoor Units | 138000 | 11.7 | 19.4 | 154000 | 3.48 | 109000 | 2.52 | R-410A | 11.5
7987384 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S |  |  | YVAHR168B41S | Non-Ducted Indoor Units | 160000 | 10.8 | 19.4 | 178000 | 3.51 | 129000 | 2.16 | R-410A | 13.3333
7987385 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S |  |  | YVAHR168B41S | Ducted Indoor Units | 160000 | 11 | 19.3 | 178000 | 3.5 | 129000 | 2.32 | R-410A | 13.3333
7987389 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR216B41S | Ducted Indoor Units | 206000 | 11.3 | 20.1 | 232000 | 3.44 | 164000 | 2.31 | R-410A | 17.1667
7987391 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR240B41S | Ducted Indoor Units | 230000 | 11.2 | 20 | 258000 | 3.6 | 182000 | 2.47 | R-410A | 19.1667
7990693 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S |  |  | TVAHP144B31S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.35 | 21.95 | 154000 | 3.83 | 109000 | 2.71 | R-410A | 11.5
7990694 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S |  |  | TVAHP168B31S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.5 | 19.65 | 178000 | 3.68 | 129000 | 2.35 | R-410A | 13.3333
7990695 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S |  |  | TVAHP192B31S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.75 | 19.2 | 204000 | 3.62 | 150000 | 2.4 | R-410A | 15.3333
7990697 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP216B31S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.2 | 19.65 | 232000 | 3.55 | 164000 | 2.36 | R-410A | 17.1667
7990698 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP240B31S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.2 | 20.35 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19.1667
7990707 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S |  |  | TVAHR144B31S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.35 | 21.95 | 154000 | 3.83 | 109000 | 2.71 | R-410A | 11.5
7990708 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S |  |  | TVAHR168B31S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.5 | 19.65 | 178000 | 3.68 | 129000 | 2.35 | R-410A | 13.3333
7990709 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S |  |  | TVAHR192B31S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.75 | 19.2 | 204000 | 3.62 | 150000 | 2.4 | R-410A | 15.3333
7990710 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR216B31S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.2 | 19.65 | 232000 | 3.55 | 164000 | 2.36 | R-410A | 17.1667
7990711 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR240B31S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.2 | 20.4 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19.1667
7990720 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S |  |  | TVAHP144B41S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.65 | 21.6 | 154000 | 3.76 | 109000 | 2.55 | R-410A | 11.5
7990721 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S |  |  | TVAHP168B41S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.9 | 19.35 | 178000 | 3.5 | 129000 | 2.24 | R-410A | 13.3333
7990723 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP072B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP216B41S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.45 | 232000 | 3.38 | 164000 | 2.27 | R-410A | 17.1667
7990724 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP240B41S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19.1667
7990734 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S |  |  | TVAHR144B41S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.65 | 21.6 | 154000 | 3.76 | 109000 | 2.55 | R-410A | 11.5
7990735 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S |  |  | TVAHR168B41S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.9 | 19.35 | 178000 | 3.5 | 129000 | 2.24 | R-410A | 13.3333
7990737 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR072B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR216B41S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.45 | 232000 | 3.38 | 164000 | 2.27 | R-410A | 17.1667
7990738 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR240B41S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.8 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19.1667
7990747 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S |  |  | HVAHP144B31S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.35 | 21.95 | 154000 | 3.83 | 109000 | 2.71 | R-410A | 11.5
7990748 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S |  |  | HVAHP168B31S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.5 | 19.65 | 178000 | 3.68 | 129000 | 2.35 | R-410A | 13.3333
7990749 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S |  |  | HVAHP192B31S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.75 | 19.2 | 204000 | 3.62 | 150000 | 2.4 | R-410A | 15.3333
7990750 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP216B31S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.2 | 19.65 | 232000 | 3.55 | 164000 | 2.36 | R-410A | 17.1667
7990751 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP240B31S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.2 | 20.35 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19.1667
7990760 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S |  |  | HVAHR144B31S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.35 | 21.95 | 154000 | 3.83 | 109000 | 2.71 | R-410A | 11.5
7990761 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S |  |  | HVAHR168B31S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.5 | 19.65 | 178000 | 3.68 | 129000 | 2.35 | R-410A | 13.3333
7990762 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S |  |  | HVAHR192B31S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.75 | 19.2 | 204000 | 3.62 | 150000 | 2.4 | R-410A | 15.3333
7990764 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR216B31S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.2 | 19.65 | 232000 | 3.55 | 164000 | 2.36 | R-410A | 17.1667
7990765 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR240B31S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.2 | 20.4 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19.1667
7990774 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S |  |  | HVAHP144B41S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.65 | 21.6 | 154000 | 3.76 | 109000 | 2.55 | R-410A | 11.5
7990775 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S |  |  | HVAHP168B41S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.9 | 19.35 | 178000 | 3.5 | 129000 | 2.24 | R-410A | 13.3333
7990777 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP072B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP216B41S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.45 | 232000 | 3.38 | 164000 | 2.27 | R-410A | 17.1667
7990778 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP240B41S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19.1667
7990787 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S |  |  | HVAHR144B41S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.65 | 21.6 | 154000 | 3.76 | 109000 | 2.55 | R-410A | 11.5
7990788 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S |  |  | HVAHR168B41S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.9 | 19.35 | 178000 | 3.5 | 129000 | 2.24 | R-410A | 13.3333
7990790 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR072B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR216B41S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.45 | 232000 | 3.38 | 164000 | 2.27 | R-410A | 17.1667
7990791 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR240B41S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.8 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19.1667
7990801 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S |  |  | YVAHP144B31S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.35 | 21.95 | 154000 | 3.83 | 109000 | 2.71 | R-410A | 11.5
7990802 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S |  |  | YVAHP168B31S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.5 | 19.65 | 178000 | 3.68 | 129000 | 2.35 | R-410A | 13.3333
7990803 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S |  |  | YVAHP192B31S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.75 | 19.2 | 204000 | 3.62 | 150000 | 2.4 | R-410A | 15.3333
7990804 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP216B31S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.2 | 19.65 | 232000 | 3.55 | 164000 | 2.36 | R-410A | 17.1667
7990805 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP240B31S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.2 | 20.35 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19.1667
7990814 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S |  |  | YVAHR144B31S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.35 | 21.95 | 154000 | 3.83 | 109000 | 2.71 | R-410A | 11.5
7990815 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S |  |  | YVAHR168B31S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.5 | 19.65 | 178000 | 3.68 | 129000 | 2.35 | R-410A | 13.3333
7990816 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S |  |  | YVAHR192B31S | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 10.75 | 19.2 | 204000 | 3.62 | 150000 | 2.4 | R-410A | 15.3333
7990817 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR216B31S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.2 | 19.65 | 232000 | 3.55 | 164000 | 2.36 | R-410A | 17.1667
7990818 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR240B31S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 11.2 | 20.4 | 258000 | 3.76 | 182000 | 2.48 | R-410A | 19.1667
7990827 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S |  |  | YVAHP144B41S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.65 | 21.6 | 154000 | 3.76 | 109000 | 2.55 | R-410A | 11.5
7990828 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S |  |  | YVAHP168B41S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.9 | 19.35 | 178000 | 3.5 | 129000 | 2.24 | R-410A | 13.3333
7990830 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP072B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP216B41S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.45 | 232000 | 3.38 | 164000 | 2.27 | R-410A | 17.1667
7990831 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP240B41S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.9 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19.1667
7990840 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S |  |  | YVAHR144B41S | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.65 | 21.6 | 154000 | 3.76 | 109000 | 2.55 | R-410A | 11.5
7990841 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S |  |  | YVAHR168B41S | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 10.9 | 19.35 | 178000 | 3.5 | 129000 | 2.24 | R-410A | 13.3333
7990843 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR072B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR216B41S | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 19.45 | 232000 | 3.38 | 164000 | 2.27 | R-410A | 17.1667
7990844 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR240B41S | Mixed Ducted and Non-Ducted Indoor Units | 230000 | 10.8 | 19.9 | 258000 | 3.64 | 182000 | 2.39 | R-410A | 19.1667
8033331 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-* | PUHY-P72YKMU-* |  |  | PUHY-P144YSKMU-* | Non-Ducted Indoor Units | 136000 | 13.2 | 20.3 | 152000 | 3.95 | 109000 | 2.13 | R-410A | 11.3333
8033332 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-* | PUHY-P72YKMU-* |  |  | PUHY-P144YSKMU-* | Ducted Indoor Units | 136000 | 12.8 | 19.3 | 152000 | 3.79 | 108000 | 2.56 | R-410A | 11.3333
8033333 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-* | PUHY-P72TKMU-* |  |  | PUHY-P168TSKMU-* | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
8033334 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-* | PUHY-P72TKMU-* |  |  | PUHY-P168TSKMU-* | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
8033335 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-* | PUHY-P72YKMU-* |  |  | PUHY-P168YSKMU-* | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
8033336 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-* | PUHY-P72YKMU-* |  |  | PUHY-P168YSKMU-* | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
8033337 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P72TKMU-* |  |  | PUHY-P192TSKMU-* | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
8033338 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P72TKMU-* |  |  | PUHY-P192TSKMU-* | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 204000 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
8033339 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P72YKMU-* |  |  | PUHY-P192YSKMU-* | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
8033340 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P72YKMU-* |  |  | PUHY-P192YSKMU-* | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 20400 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
8033341 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P96TKMU-* |  |  | PUHY-P216TSKMU-* | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
8033342 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P96TKMU-* |  |  | PUHY-P216TSKMU-* | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
8033343 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P96YKMU-* |  |  | PUHY-P216YSKMU-* | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
8033344 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P96YKMU-* |  |  | PUHY-P216YSKMU-* | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
8033346 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P120TKMU-* |  |  | PUHY-P240TSKMU-* | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
8033348 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P120YKMU-* |  |  | PUHY-P240YSKMU-* | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
8033369 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-* | PURY-P72YKMU-* |  |  | PURY-P144YSKMU-* | Ducted Indoor Units | 136000 | 12 | 18.8 | 152000 | 3.54 | 109000 | 2.41 | R-410A | 11.3333
8033370 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-* | PURY-P72YKMU-* |  |  | PURY-P144YSKMU-* | Non-Ducted Indoor Units | 136000 | 14.4 | 20.6 | 152000 | 3.62 | 109000 | 2.28 | R-410A | 11.3333
8033371 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-* | PURY-P72TKMU-* |  |  | PURY-P168TSKMU-* | Ducted Indoor Units | 160000 | 12.1 | 19.4 | 178000 | 3.63 | 132000 | 2.54 | R-410A | 13.3333
8033372 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-* | PURY-P72TKMU-* |  |  | PURY-P168TSKMU-* | Non-Ducted Indoor Units | 160000 | 12.9 | 19.1 | 178000 | 3.49 | 132000 | 2.2 | R-410A | 13.3333
8033373 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-* | PURY-P72YKMU-* |  |  | PURY-P168YSKMU-* | Ducted Indoor Units | 160000 | 12.1 | 19.4 | 178000 | 3.63 | 132000 | 2.54 | R-410A | 13.3333
8033374 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-* | PURY-P72YKMU-* |  |  | PURY-P168YSKMU-* | Non-Ducted Indoor Units | 160000 | 12.9 | 19.1 | 178000 | 3.49 | 132000 | 2.2 | R-410A | 13.3333
8033375 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-* | PURY-P96TKMU-* |  |  | PURY-P192TSKMU-* | Ducted Indoor Units | 182000 | 11.6 | 19.3 | 204000 | 3.64 | 150000 | 2.54 | R-410A | 15.1667
8033376 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-* | PURY-P96TKMU-* |  |  | PURY-P192TSKMU-* | Non-Ducted Indoor Units | 182000 | 11.9 | 18.2 | 204000 | 3.45 | 150000 | 2.17 | R-410A | 15.1667
8033377 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-* | PURY-P96YKMU-* |  |  | PURY-P192YSKMU-* | Ducted Indoor Units | 182000 | 11.6 | 19.3 | 204000 | 3.64 | 150000 | 2.54 | R-410A | 15.1667
8033378 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-* | PURY-P96YKMU-* |  |  | PURY-P192YSKMU-* | Non-Ducted Indoor Units | 182000 | 11.9 | 18.2 | 204000 | 3.45 | 150000 | 2.17 | R-410A | 15.1667
8033379 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-* | PURY-P96TKMU-* |  |  | PURY-P216TSKMU-* | Ducted Indoor Units | 206000 | 11.4 | 18.7 | 232000 | 3.54 | 164000 | 2.27 | R-410A | 17.1667
8033380 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-* | PURY-P96TKMU-* |  |  | PURY-P216TSKMU-* | Non-Ducted Indoor Units | 206000 | 11.3 | 18.3 | 232000 | 3.41 | 164000 | 2.15 | R-410A | 17.1667
8033381 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-* | PURY-P96YKMU-* |  |  | PURY-P216YSKMU-* | Ducted Indoor Units | 206000 | 11.4 | 18.7 | 232000 | 3.54 | 164000 | 2.27 | R-410A | 17.1667
8033382 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-* | PURY-P96YKMU-* |  |  | PURY-P216YSKMU-* | Non-Ducted Indoor Units | 206000 | 11.3 | 18.3 | 232000 | 3.41 | 164000 | 2.15 | R-410A | 17.1667
8033384 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-* | PURY-P120TKMU-* |  |  | PURY-P240TSKMU-* | Non-Ducted Indoor Units | 228000 | 10.9 | 18.5 | 258000 | 3.4 | 182000 | 2.14 | R-410A | 19
8033386 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-* | PURY-P120YKMU-* |  |  | PURY-P240YSKMU-* | Non-Ducted Indoor Units | 228000 | 10.9 | 18.5 | 258000 | 3.4 | 182000 | 2.14 | R-410A | 19
8175484 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YLMU-A |  |  |  | PUHY-P144YLMU-A | Ducted Indoor Units | 136000 | 12.5 | 21.2 | 152000 | 3.55 | 109000 | 2.2 | R-410A | 11.3333
8175485 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YLMU-A |  |  |  | PUHY-P144YLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 24.7 | 152000 | 3.88 | 109000 | 2.22 | R-410A | 11.3333
8175486 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P144YSLMU-A | Ducted Indoor Units | 136000 | 12.6 | 21.3 | 152000 | 3.6 | 109000 | 2.43 | R-410A | 11.3333
8175487 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P144YSLMU-A | Non-Ducted Indoor Units | 136000 | 14.6 | 26 | 152000 | 4.1 | 109000 | 2.13 | R-410A | 11.3333
8175488 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P168YLMU-A |  |  |  | PUHY-P168YLMU-A | Ducted Indoor Units | 160000 | 11.6 | 18.7 | 178000 | 3.47 | 132000 | 2.38 | R-410A | 13.3333
8175489 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P168YLMU-A |  |  |  | PUHY-P168YLMU-A | Non-Ducted Indoor Units | 160000 | 12.5 | 22.2 | 178000 | 3.77 | 132000 | 2.28 | R-410A | 13.3333
8175490 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P168YSLMU-A | Ducted Indoor Units | 160000 | 12 | 21 | 178000 | 3.5 | 132000 | 2.47 | R-410A | 13.3333
8175491 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P168YSLMU-A | Non-Ducted Indoor Units | 160000 | 14 | 25 | 178000 | 3.9 | 132000 | 2.19 | R-410A | 13.3333
8175492 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P192YSLMU-A | Ducted Indoor Units | 182000 | 12.4 | 21.1 | 204000 | 3.61 | 150000 | 2.33 | R-410A | 15.1667
8175493 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P192YSLMU-A | Non-Ducted Indoor Units | 182000 | 13.5 | 24.5 | 204000 | 3.7 | 150000 | 2.17 | R-410A | 15.1667
8175494 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  |  | PUHY-P216YSLMU-A | Ducted Indoor Units | 206000 | 12.1 | 21 | 232000 | 3.56 | 164000 | 2.36 | R-410A | 17.1667
8175495 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  |  | PUHY-P216YSLMU-A | Non-Ducted Indoor Units | 206000 | 13.3 | 24.5 | 232000 | 3.64 | 164000 | 2.09 | R-410A | 17.1667
8175496 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A |  |  | PUHY-P240YSLMU-A | Ducted Indoor Units | 228000 | 12.1 | 20.8 | 258000 | 3.52 | 182000 | 2.3 | R-410A | 19
8175514 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TLMU-A |  |  |  | PUHY-P144TLMU-A | Ducted Indoor Units | 136000 | 12.5 | 21.2 | 152000 | 3.55 | 109000 | 2.2 | R-410A | 11.3333
8175515 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TLMU-A |  |  |  | PUHY-P144TLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 24.7 | 152000 | 3.88 | 109000 | 2.22 | R-410A | 11.3333
8175516 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P144TSLMU-A | Ducted Indoor Units | 136000 | 12.6 | 21.3 | 152000 | 3.6 | 109000 | 2.43 | R-410A | 11.3333
8175517 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P144TSLMU-A | Non-Ducted Indoor Units | 136000 | 14.6 | 26 | 152000 | 4.1 | 109000 | 2.13 | R-410A | 11.3333
8175518 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P168TLMU-A |  |  |  | PUHY-P168TLMU-A | Ducted Indoor Units | 160000 | 11.6 | 18.7 | 178000 | 3.47 | 132000 | 2.38 | R-410A | 13.3333
8175519 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P168TLMU-A |  |  |  | PUHY-P168TLMU-A | Non-Ducted Indoor Units | 160000 | 12.5 | 22.2 | 178000 | 3.77 | 132000 | 2.28 | R-410A | 13.3333
8175520 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P168TSLMU-A | Ducted Indoor Units | 160000 | 12 | 21 | 178000 | 3.5 | 132000 | 2.47 | R-410A | 13.3333
8175521 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P168TSLMU-A | Non-Ducted Indoor Units | 160000 | 14 | 25 | 178000 | 3.9 | 132000 | 2.19 | R-410A | 13.3333
8175522 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P192TSLMU-A | Ducted Indoor Units | 182000 | 12.4 | 21.1 | 204000 | 3.61 | 150000 | 2.33 | R-410A | 15.1667
8175523 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  |  | PUHY-P192TSLMU-A | Non-Ducted Indoor Units | 182000 | 13.5 | 24.5 | 204000 | 3.7 | 150000 | 2.17 | R-410A | 15.1667
8175524 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  |  | PUHY-P216TSLMU-A | Ducted Indoor Units | 206000 | 12.1 | 21 | 232000 | 3.56 | 164000 | 2.36 | R-410A | 17.1667
8175525 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  |  | PUHY-P216TSLMU-A | Non-Ducted Indoor Units | 206000 | 13.3 | 24.5 | 232000 | 3.64 | 164000 | 2.09 | R-410A | 17.1667
8175526 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A |  |  | PUHY-P240TSLMU-A | Ducted Indoor Units | 228000 | 12.1 | 20.8 | 258000 | 3.52 | 182000 | 2.3 | R-410A | 19
8175897 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YLMU-A |  |  |  | PURY-P144YLMU-A | Ducted Indoor Units | 136000 | 12.2 | 19.7 | 152000 | 3.38 | 97000 | 2.07 | R-410A | 11.3333
8175898 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YLMU-A |  |  |  | PURY-P144YLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 23.8 | 152000 | 3.69 | 97000 | 2.16 | R-410A | 11.3333
8175899 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YLMU-A | PURY-P72YLMU-A |  |  | PURY-P144YSLMU-A | Ducted Indoor Units | 136000 | 12.3 | 21.2 | 152000 | 3.58 | 97000 | 2.08 | R-410A | 11.3333
8175900 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YLMU-A | PURY-P72YLMU-A |  |  | PURY-P144YSLMU-A | Non-Ducted Indoor Units | 136000 | 14.2 | 25.2 | 152000 | 4.03 | 97000 | 2.29 | R-410A | 11.3333
8175902 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P168YLMU-A |  |  |  | PURY-P168YLMU-A | Non-Ducted Indoor Units | 160000 | 11.2 | 19.3 | 178000 | 3.46 | 119000 | 2.32 | R-410A | 13.3333
8175903 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A | PURY-P72YLMU-A |  |  | PURY-P168YSLMU-A | Ducted Indoor Units | 160000 | 11 | 19.9 | 178000 | 3.39 | 119000 | 2.23 | R-410A | 13.3333
8175904 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A | PURY-P72YLMU-A |  |  | PURY-P168YSLMU-A | Non-Ducted Indoor Units | 160000 | 12.6 | 23.7 | 178000 | 3.74 | 119000 | 2.34 | R-410A | 13.3333
8175905 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A | PURY-P96YLMU-A |  |  | PURY-P192YSLMU-A | Ducted Indoor Units | 182000 | 11.4 | 23.5 | 204000 | 3.53 | 142000 | 2.21 | R-410A | 15.1667
8175906 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YLMU-A | PURY-P96YLMU-A |  |  | PURY-P192YSLMU-A | Non-Ducted Indoor Units | 182000 | 12.1 | 23 | 204000 | 3.57 | 142000 | 2.16 | R-410A | 15.1667
8175907 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A | PURY-P96YLMU-A |  |  | PURY-P216YSLMU-A | Ducted Indoor Units | 206000 | 11.7 | 21.5 | 232000 | 3.52 | 158000 | 2.2 | R-410A | 17.1667
8175908 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A | PURY-P96YLMU-A |  |  | PURY-P216YSLMU-A | Non-Ducted Indoor Units | 206000 | 12.4 | 22.2 | 232000 | 3.57 | 158000 | 2.09 | R-410A | 17.1667
8175909 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YLMU-A | PURY-P120YLMU-A |  |  | PURY-P240YSLMU-A | Ducted Indoor Units | 228000 | 11.8 | 19 | 258000 | 3.45 | 174000 | 2.15 | R-410A | 19
8175925 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TLMU-A |  |  |  | PURY-P144TLMU-A | Ducted Indoor Units | 136000 | 12.2 | 19.7 | 152000 | 3.38 | 97000 | 2.07 | R-410A | 11.3333
8175926 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TLMU-A |  |  |  | PURY-P144TLMU-A | Non-Ducted Indoor Units | 136000 | 14 | 23.8 | 152000 | 3.69 | 97000 | 2.16 | R-410A | 11.3333
8175927 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TLMU-A | PURY-P72TLMU-A |  |  | PURY-P144TSLMU-A | Ducted Indoor Units | 136000 | 12.3 | 21.2 | 152000 | 3.58 | 97000 | 2.08 | R-410A | 11.3333
8175928 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72TLMU-A | PURY-P72TLMU-A |  |  | PURY-P144TSLMU-A | Non-Ducted Indoor Units | 136000 | 14.2 | 25.2 | 152000 | 4.03 | 97000 | 2.29 | R-410A | 11.3333
8175930 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P168TLMU-A |  |  |  | PURY-P168TLMU-A | Non-Ducted Indoor Units | 160000 | 11.2 | 19.3 | 178000 | 3.46 | 119000 | 2.32 | R-410A | 13.3333
8175931 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A | PURY-P72TLMU-A |  |  | PURY-P168TSLMU-A | Ducted Indoor Units | 160000 | 11 | 19.9 | 178000 | 3.39 | 119000 | 2.23 | R-410A | 13.3333
8175932 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A | PURY-P72TLMU-A |  |  | PURY-P168TSLMU-A | Non-Ducted Indoor Units | 160000 | 12.6 | 23.7 | 178000 | 3.74 | 119000 | 2.34 | R-410A | 13.3333
8175933 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A | PURY-P96TLMU-A |  |  | PURY-P192TSLMU-A | Ducted Indoor Units | 182000 | 11.4 | 23.5 | 204000 | 3.53 | 142000 | 2.21 | R-410A | 15.1667
8175934 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TLMU-A | PURY-P96TLMU-A |  |  | PURY-P192TSLMU-A | Non-Ducted Indoor Units | 182000 | 12.1 | 23 | 204000 | 3.57 | 142000 | 2.16 | R-410A | 15.1667
8175935 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A | PURY-P96TLMU-A |  |  | PURY-P216TSLMU-A | Ducted Indoor Units | 206000 | 11.7 | 21.5 | 232000 | 3.52 | 158000 | 2.2 | R-410A | 17.1667
8175936 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A | PURY-P96TLMU-A |  |  | PURY-P216TSLMU-A | Non-Ducted Indoor Units | 206000 | 12.4 | 22.2 | 232000 | 3.57 | 158000 | 2.09 | R-410A | 17.1667
8175937 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TLMU-A | PURY-P120TLMU-A |  |  | PURY-P240TSLMU-A | Ducted Indoor Units | 228000 | 11.8 | 19 | 258000 | 3.45 | 174000 | 2.15 | R-410A | 19
4677066 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ144PBTJ |  |  |  | RXYQ144PBTJ | Non-Ducted Indoor Units | 138000 | 11.3 | 20.5 | 154000 | 3.6 | 100000 | 2.55 | R-410A | 11.5
4677068 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ144PBTJ |  |  |  | RXYQ144PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.3 | 19.05 | 154000 | 3.5 | 100000 | 2.5 | R-410A | 11.5
4677069 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ96PBTJ |  |  | RXYQ168PBTJ | Non-Ducted Indoor Units | 160000 | 12.4 | 22 | 180000 | 3.95 | 118000 | 2.65 | R-410A | 13.3333
4677070 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ96PBTJ |  |  | RXYQ168PBTJ | Ducted Indoor Units | 160000 | 12.1 | 20.2 | 180000 | 3.7 | 118000 | 2.45 | R-410A | 13.3333
4677071 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ96PBTJ |  |  | RXYQ168PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.25 | 21.1 | 180000 | 3.82 | 118000 | 2.55 | R-410A | 13.3333
4677072 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ120PBTJ |  |  | RXYQ192PBTJ | Non-Ducted Indoor Units | 184000 | 11.7 | 19.9 | 206000 | 3.7 | 134000 | 2.55 | R-410A | 15.3333
4677073 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ120PBTJ |  |  | RXYQ192PBTJ | Ducted Indoor Units | 184000 | 11.8 | 19.1 | 206000 | 3.55 | 134000 | 2.45 | R-410A | 15.3333
4677074 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ120PBTJ |  |  | RXYQ192PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.75 | 19.5 | 206000 | 3.62 | 134000 | 2.5 | R-410A | 15.3333
4677075 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBTJ | RXYQ120PBTJ |  |  | RXYQ216PBTJ | Non-Ducted Indoor Units | 206000 | 11.6 | 19.2 | 230000 | 3.8 | 150000 | 2.6 | R-410A | 17.1667
4677076 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBTJ | RXYQ120PBTJ |  |  | RXYQ216PBTJ | Ducted Indoor Units | 206000 | 11.7 | 19.5 | 230000 | 3.6 | 150000 | 2.45 | R-410A | 17.1667
4677077 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBTJ | RXYQ120PBTJ |  |  | RXYQ216PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 19.35 | 230000 | 3.7 | 150000 | 2.52 | R-410A | 17.1667
4677078 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ120PBTJ | RXYQ120PBTJ |  |  | RXYQ240PBTJ | Non-Ducted Indoor Units | 228000 | 11.5 | 18.2 | 256000 | 3.6 | 168000 | 2.55 | R-410A | 19
4677099 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ72PBYD |  |  | RXYQ144PBYD | Non-Ducted Indoor Units | 138000 | 14 | 21.5 | 154000 | 3.9 | 100000 | 2.55 | R-410A | 11.5
4677100 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ72PBYD |  |  | RXYQ144PBYD | Ducted Indoor Units | 138000 | 12.7 | 22.1 | 154000 | 3.7 | 100000 | 2.45 | R-410A | 11.5
4677101 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ72PBYD |  |  | RXYQ144PBYD | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.35 | 21.8 | 154000 | 3.8 | 100000 | 2.5 | R-410A | 11.5
4677102 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ96PBYD |  |  | RXYQ168PBYD | Non-Ducted Indoor Units | 160000 | 12.4 | 22 | 180000 | 3.95 | 118000 | 2.65 | R-410A | 13.3333
4677103 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ96PBYD |  |  | RXYQ168PBYD | Ducted Indoor Units | 160000 | 12.1 | 20.2 | 180000 | 3.7 | 118000 | 2.45 | R-410A | 13.3333
4677104 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ96PBYD |  |  | RXYQ168PBYD | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.25 | 21.1 | 180000 | 3.82 | 118000 | 2.55 | R-410A | 13.3333
4677105 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ120PBYD |  |  | RXYQ192PBYD | Non-Ducted Indoor Units | 184000 | 11.7 | 19.9 | 206000 | 3.7 | 134000 | 2.55 | R-410A | 15.3333
4677106 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ120PBYD |  |  | RXYQ192PBYD | Ducted Indoor Units | 184000 | 11.8 | 19.1 | 206000 | 3.55 | 134000 | 2.45 | R-410A | 15.3333
4677107 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ120PBYD |  |  | RXYQ192PBYD | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.75 | 19.5 | 206000 | 3.62 | 134000 | 2.5 | R-410A | 15.3333
4677108 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBYD | RXYQ120PBYD |  |  | RXYQ216PBYD | Non-Ducted Indoor Units | 206000 | 11.6 | 19.2 | 230000 | 3.8 | 150000 | 2.6 | R-410A | 17.1667
4677109 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBYD | RXYQ120PBYD |  |  | RXYQ216PBYD | Ducted Indoor Units | 206000 | 11.7 | 19.5 | 230000 | 3.6 | 150000 | 2.45 | R-410A | 17.1667
4677110 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ96PBYD | RXYQ120PBYD |  |  | RXYQ216PBYD | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.65 | 19.35 | 230000 | 3.7 | 150000 | 2.52 | R-410A | 17.1667
4677111 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ120PBYD | RXYQ120PBYD |  |  | RXYQ240PBYD | Non-Ducted Indoor Units | 228000 | 11.5 | 18.2 | 256000 | 3.6 | 168000 | 2.55 | R-410A | 19
4677126 | 1/1/2027 | VRVIII | HMSR-A-CB | REYQ144PBTJ |  |  |  | REYQ144PBTJ | Non-Ducted Indoor Units | 138000 | 11.2 | 18.9 | 154000 | 3.6 | 104000 | 2.55 | R-410A | 11.5
4677129 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ |  |  | REYQ168PBTJ | Non-Ducted Indoor Units | 160000 | 12 | 20.3 | 180000 | 3.7 | 122000 | 2.5 | R-410A | 13.3333
4677130 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ |  |  | REYQ168PBTJ | Ducted Indoor Units | 160000 | 11.5 | 19.4 | 180000 | 3.5 | 122000 | 2.35 | R-410A | 13.3333
4677131 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ |  |  | REYQ168PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.75 | 19.85 | 180000 | 3.6 | 122000 | 2.42 | R-410A | 13.3333
4677132 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBTJ | REMQ96PBTJ |  |  | REYQ192PBTJ | Non-Ducted Indoor Units | 184000 | 11.2 | 18.7 | 206000 | 3.4 | 138000 | 2.5 | R-410A | 15.3333
4677150 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD |  |  | REYQ144PBYD | Non-Ducted Indoor Units | 138000 | 13.8 | 22.5 | 154000 | 3.8 | 104000 | 2.55 | R-410A | 11.5
4677151 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD |  |  | REYQ144PBYD | Ducted Indoor Units | 138000 | 13.7 | 20 | 154000 | 3.6 | 104000 | 2.4 | R-410A | 11.5
4677152 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD |  |  | REYQ144PBYD | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 13.75 | 21.25 | 154000 | 3.7 | 104000 | 2.47 | R-410A | 11.5
4677153 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD |  |  | REYQ168PBYD | Non-Ducted Indoor Units | 160000 | 12 | 20.3 | 180000 | 3.7 | 122000 | 2.5 | R-410A | 13.3333
4677154 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD |  |  | REYQ168PBYD | Ducted Indoor Units | 160000 | 11.5 | 19.4 | 180000 | 3.5 | 122000 | 2.35 | R-410A | 13.3333
4677155 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD |  |  | REYQ168PBYD | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.75 | 19.85 | 180000 | 3.6 | 122000 | 2.42 | R-410A | 13.3333
4677156 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBYD | REMQ96PBYD |  |  | REYQ192PBYD | Non-Ducted Indoor Units | 184000 | 11.2 | 18.7 | 206000 | 3.4 | 138000 | 2.5 | R-410A | 15.3333
4679538 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BT3 |  |  |  | ARUB144BT3 | Ducted Indoor Units | 138000 | 11.6 | 19.1 | 154000 | 3.45 | 100000 | 2.46 | R-410A | 11.5
4679539 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BT3 |  |  |  | ARUB144BT3 | Non-Ducted Indoor Units | 138000 | 11.8 | 18.9 | 154000 | 3.67 | 100000 | 2.65 | R-410A | 11.5
4679540 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DT3 |  |  |  | ARUB144DT3 | Ducted Indoor Units | 138000 | 11.6 | 19.1 | 154000 | 3.45 | 100000 | 2.46 | R-410A | 11.5
4679541 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DT3 |  |  |  | ARUB144DT3 | Non-Ducted Indoor Units | 138000 | 11.8 | 18.9 | 154000 | 3.67 | 100000 | 2.65 | R-410A | 11.5
4679542 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB096BT3 |  |  | ARUB168BT3 | Ducted Indoor Units | 160000 | 11.7 | 19.5 | 180000 | 3.33 | 118000 | 2.47 | R-410A | 13.3333
4679543 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB096BT3 |  |  | ARUB168BT3 | Non-Ducted Indoor Units | 160000 | 12.7 | 22.1 | 180000 | 3.77 | 118000 | 2.66 | R-410A | 13.3333
4679544 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB096DT3 |  |  | ARUB168DT3 | Ducted Indoor Units | 160000 | 11.7 | 19.5 | 180000 | 3.33 | 118000 | 2.47 | R-410A | 13.3333
4679545 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB096DT3 |  |  | ARUB168DT3 | Non-Ducted Indoor Units | 160000 | 12.7 | 22.1 | 180000 | 3.77 | 118000 | 2.66 | R-410A | 13.3333
4679546 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB121BT3 |  |  | ARUB192BT3 | Ducted Indoor Units | 184000 | 11.4 | 18.5 | 206000 | 3.32 | 134000 | 2.46 | R-410A | 15.3333
4679547 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB121BT3 |  |  | ARUB192BT3 | Non-Ducted Indoor Units | 184000 | 12.1 | 20 | 206000 | 3.73 | 134000 | 2.58 | R-410A | 15.3333
4679548 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB121DT3 |  |  | ARUB192DT3 | Ducted Indoor Units | 184000 | 12.1 | 20 | 206000 | 3.73 | 134000 | 2.58 | R-410A | 15.3333
4679549 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB121DT3 |  |  | ARUB192DT3 | Non-Ducted Indoor Units | 184000 | 12.1 | 20 | 206000 | 3.73 | 134000 | 2.58 | R-410A | 15.3333
4679550 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB144BT3 |  |  | ARUB216BT3 | Ducted Indoor Units | 206000 | 11 | 19.7 | 230000 | 3.41 | 150000 | 2.44 | R-410A | 17.1667
4679551 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB144BT3 |  |  | ARUB216BT3 | Non-Ducted Indoor Units | 206000 | 11.5 | 19.3 | 230000 | 3.71 | 150000 | 2.58 | R-410A | 17.1667
4679552 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB144DT3 |  |  | ARUB216DT3 | Ducted Indoor Units | 206000 | 11 | 19.7 | 230000 | 3.41 | 150000 | 2.44 | R-410A | 17.1667
4679553 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB144DT3 |  |  | ARUB216DT3 | Non-Ducted Indoor Units | 206000 | 11.5 | 19.3 | 230000 | 3.71 | 150000 | 2.37 | R-410A | 17.1667
4679555 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BT3 | ARUB144BT3 |  |  | ARUB240BT3 | Non-Ducted Indoor Units | 228000 | 11.9 | 18.3 | 256000 | 3.54 | 168000 | 2.57 | R-410A | 19
4679557 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DT3 | ARUB144DT3 |  |  | ARUB240DT3 | Non-Ducted Indoor Units | 228000 | 11.9 | 18.3 | 256000 | 3.54 | 168000 | 2.57 | R-410A | 19
4679582 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BT3 |  |  |  | ARUN144BT3 | Ducted Indoor Units | 138000 | 11.6 | 19.1 | 154000 | 3.45 | 100000 | 2.46 | R-410A | 11.5
4679583 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BT3 |  |  |  | ARUN144BT3 | Non-Ducted Indoor Units | 138000 | 11.8 | 18.9 | 154000 | 3.67 | 100000 | 2.65 | R-410A | 11.5
4679584 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DT3 |  |  |  | ARUN144DT3 | Ducted Indoor Units | 138000 | 11.6 | 19.1 | 154000 | 3.45 | 100000 | 2.46 | R-410A | 11.5
4679585 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DT3 |  |  |  | ARUN144DT3 | Non-Ducted Indoor Units | 138000 | 11.8 | 18.9 | 154000 | 3.67 | 100000 | 2.65 | R-410A | 11.5
4679586 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN096BT3 |  |  | ARUN168BT3 | Ducted Indoor Units | 160000 | 11.7 | 19.5 | 180000 | 3.33 | 118000 | 2.47 | R-410A | 13.3333
4679587 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN096BT3 |  |  | ARUN168BT3 | Non-Ducted Indoor Units | 160000 | 12.7 | 20 | 180000 | 3.77 | 118000 | 2.66 | R-410A | 13.3333
4679588 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN096DT3 |  |  | ARUN168DT3 | Ducted Indoor Units | 160000 | 11.7 | 19.5 | 180000 | 3.33 | 118000 | 2.47 | R-410A | 13.3333
4679589 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN096DT3 |  |  | ARUN168DT3 | Non-Ducted Indoor Units | 160000 | 12.7 | 22.1 | 180000 | 3.77 | 118000 | 2.66 | R-410A | 13.3333
4679590 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN121BT3 |  |  | ARUN192BT3 | Ducted Indoor Units | 184000 | 11.4 | 18.5 | 206000 | 3.32 | 134000 | 2.46 | R-410A | 15.3333
4679591 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN121BT3 |  |  | ARUN192BT3 | Non-Ducted Indoor Units | 184000 | 12.1 | 20 | 206000 | 3.73 | 134000 | 2.58 | R-410A | 15.3333
4679592 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN121DT3 |  |  | ARUN192DT3 | Ducted Indoor Units | 184000 | 11.4 | 18.5 | 206000 | 3.32 | 134000 | 2.46 | R-410A | 15.3333
4679593 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN121DT3 |  |  | ARUN192DT3 | Non-Ducted Indoor Units | 184000 | 12.1 | 20 | 206000 | 3.73 | 134000 | 2.58 | R-410A | 15.3333
4679594 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN144BT3 |  |  | ARUN216BT3 | Ducted Indoor Units | 206000 | 11 | 19.7 | 230000 | 3.41 | 150000 | 2.44 | R-410A | 17.1667
4679595 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN144BT3 |  |  | ARUN216BT3 | Non-Ducted Indoor Units | 206000 | 11.5 | 19.3 | 230000 | 3.71 | 150000 | 2.58 | R-410A | 17.1667
4679596 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN144DT3 |  |  | ARUN216DT3 | Ducted Indoor Units | 206000 | 11 | 19.7 | 230000 | 3.41 | 150000 | 2.44 | R-410A | 17.1667
4679597 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN144DT3 |  |  | ARUN216DT3 | Non-Ducted Indoor Units | 206000 | 11.5 | 19.3 | 230000 | 3.71 | 150000 | 2.58 | R-410A | 17.1667
4679599 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BT3 | ARUN144BT3 |  |  | ARUN240BT3 | Non-Ducted Indoor Units | 228000 | 11.9 | 18.3 | 256000 | 3.54 | 168000 | 2.57 | R-410A | 19
4679601 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DT3 | ARUN144DT3 |  |  | ARUN240DT3 | Non-Ducted Indoor Units | 228000 | 11.9 | 18.3 | 256000 | 3.54 | 168000 | 2.57 | R-410A | 19
5012629 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0724HT9UL | MMY-MAP0724HT9UL |  |  | MMY-AP1444HT9UL | Non-Ducted Indoor Units | 138000 | 10.9 | 20.9 | 162000 | 3.4 | 82000 | 2.25 | R-410A | 11.5
5194490 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0724HT6UL | MMY-MAP0724HT6UL |  |  | MMY-AP1444HT6UL | Non-Ducted Indoor Units | 138000 | 10.9 | 20.4 | 162000 | 3.4 | 82000 | 2.25 | R-410A | 11.5
5198217 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV | AOUA72RLBV |  |  | AOUA144RLBVG | Non-Ducted Indoor Units | 138000 | 12.4 | 19.5 | 154000 | 3.68 | 107000 | 2.36 | R-410A | 11.5
5198220 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV | AOUA72RLBV |  |  | AOUA168RLBVG | Non-Ducted Indoor Units | 160000 | 11.6 | 19.5 | 180000 | 3.6 | 118000 | 2.47 | R-410A | 13.3333
5198222 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV | AOUA72RLBV |  |  | AOUA168RLBVG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 18.3 | 180000 | 3.57 | 118000 | 2.34 | R-410A | 13.3333
5198223 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV | AOUA96RLBV |  |  | AOUA192RLBVG | Non-Ducted Indoor Units | 174000 | 11.4 | 19.6 | 196000 | 3.55 | 128000 | 2.53 | R-410A | 14.5
5198225 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV | AOUA96RLBV |  |  | AOUA192RLBVG | Mixed Ducted and Non-Ducted Indoor Units | 174000 | 11.25 | 18.45 | 196000 | 3.49 | 128000 | 2.41 | R-410A | 14.5
5198226 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV | AOUA72RLBV | AOUA72RLBV |  | AOUA216RLBVG | Non-Ducted Indoor Units | 206000 | 12 | 20.2 | 230000 | 3.72 | 160000 | 2.38 | R-410A | 17.1667
5198228 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA72RLBV | AOUA72RLBV | AOUA72RLBV |  | AOUA216RLBVG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12 | 18.7 | 230000 | 3.66 | 160000 | 2.32 | R-410A | 17.1667
5198229 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV | AOUA72RLBV | AOUA72RLBV |  | AOUA240RLBVG | Non-Ducted Indoor Units | 228000 | 11.3 | 19.6 | 258000 | 3.53 | 166000 | 2.24 | R-410A | 19
5198231 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV | AOUA72RLBV | AOUA72RLBV |  | AOUA240RLBVG | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 11.6 | 18.4 | 258000 | 3.55 | 166000 | 2.22 | R-410A | 19
5358528 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YKMU-A |  |  |  | PUHY-P144YKMU-A | Ducted Indoor Units | 136000 | 11.6 | 19.3 | 152000 | 3.56 | 108000 | 2.32 | R-410A | 11.3333
5358529 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YKMU-A |  |  |  | PUHY-P144YKMU-A | Non-Ducted Indoor Units | 136000 | 11.8 | 20.2 | 152000 | 3.72 | 109000 | 2.22 | R-410A | 11.3333
5358530 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144YKMU-A |  |  |  | PUHY-P144YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 11.7 | 19.75 | 152000 | 3.64 | 108000 | 2.27 | R-410A | 11.3333
5358531 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P144YSKMU-A | Ducted Indoor Units | 136000 | 12.8 | 19.3 | 152000 | 3.79 | 108000 | 2.56 | R-410A | 11.3333
5358532 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P144YSKMU-A | Non-Ducted Indoor Units | 136000 | 13.2 | 20.3 | 152000 | 3.95 | 109000 | 2.13 | R-410A | 11.3333
5358533 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P144YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13 | 19.8 | 152000 | 3.87 | 108000 | 2.34 | R-410A | 11.3333
5358534 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P168YSKMU-A | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
5358535 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P168YSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
5358536 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P168YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.75 | 19.65 | 178000 | 3.8 | 132000 | 2.39 | R-410A | 13.3333
5358537 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P192YSKMU-A | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 20400 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
5358538 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P192YSKMU-A | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
5358539 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  |  | PUHY-P192YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.45 | 19 | 112000 | 3.62 | 150000 | 2.31 | R-410A | 15.1667
5358540 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  |  | PUHY-P216YSKMU-A | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
5358541 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  |  | PUHY-P216YSKMU-A | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
5358542 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  |  | PUHY-P216YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.3 | 18.75 | 232000 | 3.6 | 164000 | 2.28 | R-410A | 17.1667
5358543 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A |  |  | PUHY-P240YSKMU-A | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
5358545 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A |  |  | PUHY-P240YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.05 | 18.35 | 258000 | 3.54 | 182000 | 2.23 | R-410A | 19
5358570 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TKMU-A |  |  |  | PUHY-P144TKMU-A | Ducted Indoor Units | 136000 | 11.6 | 19.3 | 152000 | 3.56 | 109000 | 2.32 | R-410A | 11.3333
5358571 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TKMU-A |  |  |  | PUHY-P144TKMU-A | Non-Ducted Indoor Units | 136000 | 11.8 | 20.2 | 152000 | 3.72 | 109000 | 2.22 | R-410A | 11.3333
5358572 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144TKMU-A |  |  |  | PUHY-P144TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 11.7 | 19.75 | 152000 | 3.64 | 109000 | 2.27 | R-410A | 11.3333
5358573 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P168TSKMU-A | Ducted Indoor Units | 160000 | 12.6 | 19.6 | 178000 | 3.78 | 132000 | 2.6 | R-410A | 13.3333
5358574 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P168TSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 19.7 | 178000 | 3.83 | 132000 | 2.19 | R-410A | 13.3333
5358575 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P168TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.75 | 19.65 | 178000 | 3.8 | 132000 | 2.39 | R-410A | 13.3333
5358576 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P192TSKMU-A | Ducted Indoor Units | 182000 | 12.4 | 18.9 | 204000 | 3.63 | 150000 | 2.45 | R-410A | 15.1667
5358577 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P192TSKMU-A | Non-Ducted Indoor Units | 182000 | 12.5 | 19.1 | 204000 | 3.61 | 150000 | 2.17 | R-410A | 15.1667
5358578 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  |  | PUHY-P192TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 12.45 | 19 | 204000 | 3.62 | 150000 | 2.31 | R-410A | 15.1667
5358579 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  |  | PUHY-P216TSKMU-A | Ducted Indoor Units | 206000 | 12.3 | 18.9 | 232000 | 3.65 | 164000 | 2.48 | R-410A | 17.1667
5358580 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  |  | PUHY-P216TSKMU-A | Non-Ducted Indoor Units | 206000 | 12.3 | 18.6 | 232000 | 3.56 | 164000 | 2.09 | R-410A | 17.1667
5358581 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  |  | PUHY-P216TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 12.3 | 18.75 | 232000 | 3.6 | 164000 | 2.28 | R-410A | 17.1667
5358582 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A |  |  | PUHY-P240TSKMU-A | Ducted Indoor Units | 228000 | 12.1 | 18.6 | 258000 | 3.55 | 182000 | 2.42 | R-410A | 19
5358584 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A |  |  | PUHY-P240TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 12.05 | 18.35 | 258000 | 3.54 | 182000 | 2.23 | R-410A | 19
5358609 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-A |  |  |  | PURY-P144YKMU-A | Ducted Indoor Units | 136000 | 11.7 | 18 | 152000 | 3.41 | 109000 | 2.32 | R-410A | 11.3333
5358611 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-A |  |  |  | PURY-P144YKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.2 | 19.45 | 152000 | 3.33 | 109000 | 2.19 | R-410A | 11.3333
5358612 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-A | PURY-P72YKMU-A |  |  | PURY-P144YSKMU-A | Ducted Indoor Units | 136000 | 12 | 18.8 | 152000 | 3.54 | 109000 | 2.41 | R-410A | 11.3333
5358613 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-A | PURY-P72YKMU-A |  |  | PURY-P144YSKMU-A | Non-Ducted Indoor Units | 136000 | 14.4 | 19.5 | 152000 | 3.62 | 109000 | 2.28 | R-410A | 11.3333
5358614 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P72YKMU-A | PURY-P72YKMU-A |  |  | PURY-P144YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 13.2 | 19.7 | 152000 | 3.58 | 109000 | 2.34 | R-410A | 11.3333
5358615 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A | PURY-P72YKMU-A |  |  | PURY-P168YSKMU-A | Ducted Indoor Units | 160000 | 12.1 | 19.4 | 178000 | 3.63 | 132000 | 2.54 | R-410A | 13.3333
5358616 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A | PURY-P72YKMU-A |  |  | PURY-P168YSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 18.2 | 178000 | 3.49 | 132000 | 2.2 | R-410A | 13.3333
5358617 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A | PURY-P72YKMU-A |  |  | PURY-P168YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.5 | 19.25 | 178000 | 3.56 | 132000 | 2.37 | R-410A | 13.3333
5358618 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A | PURY-P96YKMU-A |  |  | PURY-P192YSKMU-A | Ducted Indoor Units | 182000 | 11.6 | 19.3 | 204000 | 3.64 | 150000 | 2.54 | R-410A | 15.1667
5358620 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96YKMU-A | PURY-P96YKMU-A |  |  | PURY-P192YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 18.75 | 204000 | 3.54 | 150000 | 2.35 | R-410A | 15.1667
5358621 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-A | PURY-P96YKMU-A |  |  | PURY-P216YSKMU-A | Ducted Indoor Units | 206000 | 11.4 | 18.7 | 232000 | 3.54 | 164000 | 2.27 | R-410A | 17.1667
5358623 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-A | PURY-P96YKMU-A |  |  | PURY-P216YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.35 | 18.5 | 232000 | 3.47 | 164000 | 2.21 | R-410A | 17.1667
5358625 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-A | PURY-P120YKMU-A |  |  | PURY-P240YSKMU-A | Non-Ducted Indoor Units | 228000 | 10.9 | 18.1 | 258000 | 3.4 | 182000 | 2.14 | R-410A | 19
5358626 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120YKMU-A | PURY-P120YKMU-A |  |  | PURY-P240YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 18.15 | 258000 | 3.39 | 182000 | 2.13 | R-410A | 19
5358639 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-A |  |  |  | PURY-P144TKMU-A | Ducted Indoor Units | 136000 | 11.7 | 18 | 152000 | 3.41 | 109000 | 2.32 | R-410A | 11.3333
5358641 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-A |  |  |  | PURY-P144TKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 136000 | 12.2 | 19.45 | 152000 | 3.33 | 109000 | 2.19 | R-410A | 11.3333
5358642 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A | PURY-P72TKMU-A |  |  | PURY-P168TSKMU-A | Ducted Indoor Units | 160000 | 12.1 | 19.4 | 178000 | 3.63 | 132000 | 2.54 | R-410A | 13.3333
5358643 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A | PURY-P72TKMU-A |  |  | PURY-P168TSKMU-A | Non-Ducted Indoor Units | 160000 | 12.9 | 18.2 | 178000 | 3.49 | 132000 | 2.2 | R-410A | 13.3333
5358644 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A | PURY-P72TKMU-A |  |  | PURY-P168TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 12.5 | 19.25 | 178000 | 3.56 | 132000 | 2.37 | R-410A | 13.3333
5358645 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A | PURY-P96TKMU-A |  |  | PURY-P192TSKMU-A | Ducted Indoor Units | 182000 | 11.6 | 19.3 | 204000 | 3.64 | 150000 | 2.54 | R-410A | 15.1667
5358647 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96TKMU-A | PURY-P96TKMU-A |  |  | PURY-P192TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 182000 | 11.75 | 18.75 | 204000 | 3.54 | 150000 | 2.35 | R-410A | 15.1667
5358648 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-A | PURY-P96TKMU-A |  |  | PURY-P216TSKMU-A | Ducted Indoor Units | 206000 | 11.4 | 18.7 | 232000 | 3.54 | 164000 | 2.27 | R-410A | 17.1667
5358650 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-A | PURY-P96TKMU-A |  |  | PURY-P216TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 11.35 | 18.5 | 232000 | 3.47 | 164000 | 2.21 | R-410A | 17.1667
5358652 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-A | PURY-P120TKMU-A |  |  | PURY-P240TSKMU-A | Non-Ducted Indoor Units | 228000 | 10.9 | 18.1 | 258000 | 3.4 | 182000 | 2.14 | R-410A | 19
5358653 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120TKMU-A | PURY-P120TKMU-A |  |  | PURY-P240TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 18.15 | 258000 | 3.39 | 182000 | 2.13 | R-410A | 19
5733045 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM096FXVAFH |  |  | AM168FXVAFH | Ducted Indoor Units | 160000 | 11.4 | 20.8 | 180000 | 3.46 | 118000 | 2.43 | R-410A | 13.3333
5733046 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM096FXVAJH |  |  | AM168FXVAJH | Ducted Indoor Units | 160000 | 11.3 | 20.5 | 180000 | 3.44 | 118000 | 2.43 | R-410A | 13.3333
5733047 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM096FXVAFH |  |  | AM168FXVAFH | Non-Ducted Indoor Units | 160000 | 12.1 | 25.9 | 180000 | 3.94 | 118000 | 2.65 | R-410A | 13.3333
5733048 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM096FXVAJH |  |  | AM168FXVAJH | Non-Ducted Indoor Units | 160000 | 12.1 | 25.3 | 180000 | 3.94 | 118000 | 2.65 | R-410A | 13.3333
5733049 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM096FXVAFR |  |  | AM168FXVAFR | Ducted Indoor Units | 160000 | 11.4 | 20.8 | 180000 | 3.46 | 118000 | 2.43 | R-410A | 13.3333
5733050 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM096FXVAJR |  |  | AM168FXVAJR | Ducted Indoor Units | 160000 | 11.3 | 20.5 | 180000 | 3.44 | 118000 | 2.43 | R-410A | 13.3333
5733051 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM096FXVAFR |  |  | AM168FXVAFR | Non-Ducted Indoor Units | 160000 | 12.1 | 25.9 | 180000 | 3.94 | 118000 | 2.65 | R-410A | 13.3333
5733052 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM096FXVAJR |  |  | AM168FXVAJR | Non-Ducted Indoor Units | 160000 | 12.1 | 25.3 | 180000 | 3.94 | 118000 | 2.65 | R-410A | 13.3333
5733053 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM120FXVAFH |  |  | AM192FXVAFH | Ducted Indoor Units | 184000 | 10.9 | 21.5 | 206000 | 3.34 | 134000 | 2.42 | R-410A | 15.3333
5733054 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM120FXVAJH |  |  | AM192FXVAJH | Ducted Indoor Units | 184000 | 10.9 | 21.5 | 206000 | 3.34 | 134000 | 2.42 | R-410A | 15.3333
5733055 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM120FXVAFH |  |  | AM192FXVAFH | Non-Ducted Indoor Units | 184000 | 11.4 | 24.1 | 206000 | 3.83 | 134000 | 2.59 | R-410A | 15.3333
5733056 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM120FXVAJH |  |  | AM192FXVAJH | Non-Ducted Indoor Units | 184000 | 11.2 | 24.2 | 206000 | 3.83 | 134000 | 2.59 | R-410A | 15.3333
5733057 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM120FXVAFR |  |  | AM192FXVAFR | Ducted Indoor Units | 184000 | 10.9 | 21.5 | 206000 | 3.34 | 134000 | 2.42 | R-410A | 15.3333
5733058 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM120FXVAJR |  |  | AM192FXVAJR | Ducted Indoor Units | 184000 | 10.9 | 21.5 | 206000 | 3.34 | 134000 | 2.42 | R-410A | 15.3333
5733059 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM120FXVAFR |  |  | AM192FXVAFR | Non-Ducted Indoor Units | 184000 | 11.4 | 24.1 | 206000 | 3.83 | 134000 | 2.59 | R-410A | 15.3333
5733060 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM120FXVAJR |  |  | AM192FXVAJR | Non-Ducted Indoor Units | 184000 | 11.2 | 24.2 | 206000 | 3.83 | 134000 | 2.59 | R-410A | 15.3333
5733063 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM144FXVAFH |  |  | AM216FXVAFH | Non-Ducted Indoor Units | 206000 | 10.8 | 22.4 | 230000 | 3.63 | 150000 | 2.52 | R-410A | 17.1667
5733064 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM144FXVAJH |  |  | AM216FXVAJH | Non-Ducted Indoor Units | 206000 | 10.8 | 22.4 | 230000 | 3.63 | 150000 | 2.52 | R-410A | 17.1667
5733067 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM144FXVAFR |  |  | AM216FXVAFR | Non-Ducted Indoor Units | 206000 | 10.8 | 22.4 | 230000 | 3.63 | 150000 | 2.52 | R-410A | 17.1667
5733068 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM144FXVAJR |  |  | AM216FXVAJR | Non-Ducted Indoor Units | 206000 | 10.8 | 22.4 | 230000 | 3.63 | 150000 | 2.52 | R-410A | 17.1667
5733071 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAFH | AM120FXVAFH |  |  | AM240FXVAFH | Non-Ducted Indoor Units | 228000 | 11.1 | 21.8 | 258000 | 3.65 | 168000 | 2.54 | R-410A | 19
5733072 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAJH | AM120FXVAJH |  |  | AM240FXVAJH | Non-Ducted Indoor Units | 228000 | 10.7 | 22.1 | 258000 | 3.65 | 168000 | 2.54 | R-410A | 19
5733075 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAFR | AM120FXVAFR |  |  | AM240FXVAFR | Non-Ducted Indoor Units | 228000 | 11.1 | 21.8 | 258000 | 3.65 | 168000 | 2.54 | R-410A | 19
5733076 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAJR | AM120FXVAJR |  |  | AM240FXVAJR | Non-Ducted Indoor Units | 228000 | 10.7 | 22.1 | 258000 | 3.65 | 168000 | 2.54 | R-410A | 19
5924245 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0724HT9UL | MMY-MAP0724HT9UL |  |  | MMY-AP1444HT9UL | Mixed Ducted and Non-Ducted Indoor Units | 140000 | 10.8 | 18.85 | 162000 | 3.32 | 87000 | 2.35 | R-410A | 11.6667
5924246 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP0724HT6UL | MMY-MAP0724HT6UL |  |  | MMY-AP1444HT6UL | Mixed Ducted and Non-Ducted Indoor Units | 140000 | 10.8 | 18.5 | 162000 | 3.32 | 87000 | 2.35 | R-410A | 11.6667
6334550 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0964FT9UL | MMY-MAP0724FT9UL |  |  | MMY-AP1684FT9UL | Non-Ducted Indoor Units | 160000 | 11.7 | 19.4 | 180000 | 3.27 | 110000 | 2.16 | R-410A | 13.3333
6334551 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0964FT9UL | MMY-MAP0964FT9UL |  |  | MMY-AP1924FT9UL | Non-Ducted Indoor Units | 184000 | 11.4 | 18.9 | 206000 | 3.25 | 126000 | 2.12 | R-410A | 15.3333
6334570 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0724FT9UL | MMY-MAP0724FT9UL |  |  | MMY-AP1444FT9UL | Non-Ducted Indoor Units | 138000 | 11.3 | 20.4 | 154000 | 3.44 | 96000 | 2.19 | R-410A | 11.5
6334577 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0724FT6UL | MMY-MAP0724FT6UL |  |  | MMY-AP1444FT6UL | Non-Ducted Indoor Units | 138000 | 11.3 | 19.9 | 154000 | 3.44 | 96000 | 2.19 | R-410A | 11.5
6334578 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0964FT6UL | MMY-MAP0724FT6UL |  |  | MMY-AP1684FT6UL | Non-Ducted Indoor Units | 160000 | 11.7 | 19 | 180000 | 3.27 | 110000 | 2.16 | R-410A | 13.3333
6334579 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0964FT6UL | MMY-MAP0964FT6UL |  |  | MMY-AP1924FT6UL | Non-Ducted Indoor Units | 184000 | 11.4 | 18.5 | 206000 | 3.25 | 126000 | 2.12 | R-410A | 15.3333
6334587 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP0724FT9UL | MMY-MAP0724FT9UL |  |  | MMY-AP1444FT9UL | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.1 | 18.35 | 152000 | 3.32 | 96000 | 2.19 | R-410A | 11.5
6687546 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV | AOUA72TLBV |  |  | AOUA144TLBVG | Ducted Indoor Units | 138000 | 11.4 | 20.4 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
6687548 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA72TLBV |  |  | AOUA168TLBVG | Ducted Indoor Units | 160000 | 11 | 20 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
6687550 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA72TLBV |  |  | AOUA192TLBVG | Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.57 | 142000 | 2.36 | R-410A | 15.3333
6687552 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA96TLBV |  |  | AOUA216TLBVG | Ducted Indoor Units | 206000 | 10.9 | 19.2 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
6687554 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA120TLBV |  |  | AOUA240TLBVG | Ducted Indoor Units | 228000 | 10.9 | 20.2 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
6691440 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA72TLBV | AOUA72TLBV |  |  | AOUA144TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 11.4 | 21.3 | 154000 | 3.44 | 106000 | 2.28 | R-410A | 11.5
6691441 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA72TLBV |  |  | AOUA168TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11 | 21.1 | 180000 | 3.48 | 124000 | 2.32 | R-410A | 13.3333
6691442 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA72TLBV |  |  | AOUA192TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.15 | 22.4 | 206000 | 3.66 | 142000 | 2.42 | R-410A | 15.3333
6691443 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA96TLBV |  |  | AOUA216TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.9 | 19.6 | 232000 | 3.47 | 158000 | 2.35 | R-410A | 17.1667
6691444 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA120TLBV | AOUA120TLBV |  |  | AOUA240TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 228000 | 10.9 | 20.5 | 258000 | 3.36 | 172000 | 2.36 | R-410A | 19
8657017 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P144ZKMU-A |  |  |  | PUHY-P144ZKMU-A | Ducted Indoor Units | 136000 | 11.7 | 20.7 | 152000 | 3.46 | 109000 | 2.32 | R-410A | 11.3333
8657003 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P120ZKMU-A | PURY-P96ZKMU-A |  |  | PURY-P216ZSKMU-A | Ducted Indoor Units | 206000 | 11.4 | 19.5 | 232000 | 3.34 | 158000 | 2.19 | R-410A | 17.1667
8657001 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96ZKMU-A | PURY-P96ZKMU-A |  |  | PURY-P192ZSKMU-A | Ducted Indoor Units | 182000 | 11.2 | 19.9 | 204000 | 3.39 | 142000 | 2.19 | R-410A | 15.1667
8656999 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P96ZKMU-A | PURY-P72ZKMU-A |  |  | PURY-P168ZSKMU-A | Ducted Indoor Units | 160000 | 11.1 | 19.9 | 178000 | 3.31 | 119000 | 2.13 | R-410A | 13.3333
8657025 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  |  | PUHY-P240ZSKMU-A | Ducted Indoor Units | 228000 | 11.9 | 20.4 | 258000 | 3.45 | 182000 | 2.42 | R-410A | 19
8657023 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P96ZKMU-A |  |  | PUHY-P216ZSKMU-A | Ducted Indoor Units | 206000 | 11.8 | 20.7 | 232000 | 3.51 | 164000 | 2.48 | R-410A | 17.1667
8657021 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P72ZKMU-A |  |  | PUHY-P192ZSKMU-A | Ducted Indoor Units | 182000 | 12 | 20.7 | 204000 | 3.48 | 150000 | 2.45 | R-410A | 15.1667
8657019 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P72ZKMU-A |  |  | PUHY-P168ZSKMU-A | Ducted Indoor Units | 160000 | 11.9 | 21.2 | 178000 | 3.54 | 132000 | 2.6 | R-410A | 13.3333
205281453 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
202566102 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Non-Ducted Indoor Units | 138000 | 12.5 | 28.6 | 152000 | 3.84 | 98000 | 2.67 | R-410A | 11.5
202566103 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
202566104 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 |  |  |  | ARUM168CTE5 | Non-Ducted Indoor Units | 160000 | 11.7 | 25.4 | 180000 | 3.57 | 117000 | 2.45 | R-410A | 13.3333
202566106 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Non-Ducted Indoor Units | 184000 | 12.4 | 25.9 | 206000 | 3.75 | 134000 | 2.64 | R-410A | 15.3333
202566107 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Ducted Indoor Units | 184000 | 11 | 23 | 206000 | 3.3 | 134000 | 2.41 | R-410A | 15.3333
202566108 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 |  |  |  | ARUM216CTE5 | Non-Ducted Indoor Units | 206000 | 11.2 | 24.8 | 230000 | 3.53 | 150000 | 2.66 | R-410A | 17.1667
202534322 | 1/1/2027 | LG | HMSR-A-CB | ARUB144CTE4 |  |  |  | ARUB144CTE4 | Non-Ducted Indoor Units | 138000 | 11.7 | 24.2 | 152000 | 3.6 | 98000 | 2.53 | R-410A | 11.5
202534323 | 1/1/2027 | LG | HMSR-A-CB | ARUB168CTE4 |  |  |  | ARUB168CTE4 | Non-Ducted Indoor Units | 160000 | 11.1 | 22.1 | 180000 | 3.4 | 117000 | 2.34 | R-410A | 13.3333
202534324 | 1/1/2027 | LG | HMSR-A-CB | ARUB072CTE4 | ARUB121CTE4 |  |  | ARUB192CTE4 | Non-Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.62 | 134000 | 2.45 | R-410A | 15.3333
202534325 | 1/1/2027 | LG | HMSR-A-CB | ARUB072CTE4 | ARUB144CTE4 |  |  | ARUB216CTE4 | Non-Ducted Indoor Units | 206000 | 12.2 | 20 | 230000 | 3.72 | 150000 | 2.58 | R-410A | 17.1667
202534326 | 1/1/2027 | LG | HMSR-A-CB | ARUB096CTE4 | ARUB144CTE4 |  |  | ARUB240CTE4 | Non-Ducted Indoor Units | 228000 | 12.2 | 20.2 | 256000 | 3.67 | 168000 | 2.61 | R-410A | 19
202534334 | 1/1/2027 | LG | HMSR-A-CB | ARUB144CTE4 |  |  |  | ARUB144CTE4 | Ducted Indoor Units | 138000 | 11.8 | 22.5 | 152000 | 3.49 | 98000 | 2.52 | R-410A | 11.5
202534336 | 1/1/2027 | LG | HMSR-A-CB | ARUB072CTE4 | ARUB121CTE4 |  |  | ARUB192CTE4 | Ducted Indoor Units | 184000 | 12.5 | 21 | 206000 | 3.66 | 134000 | 2.49 | R-410A | 15.3333
202534337 | 1/1/2027 | LG | HMSR-A-CB | ARUB072CTE4 | ARUB144CTE4 |  |  | ARUB216CTE4 | Ducted Indoor Units | 206000 | 12 | 22.1 | 230000 | 3.66 | 150000 | 2.47 | R-410A | 17.1667
202534338 | 1/1/2027 | LG | HMSR-A-CB | ARUB096CTE4 | ARUB144CTE4 |  |  | ARUB240CTE4 | Ducted Indoor Units | 228000 | 11.6 | 18 | 256000 | 3.56 | 168000 | 2.4 | R-410A | 19
202534346 | 1/1/2027 | LG | HMSV-A-CB | ARUN144CTE4 |  |  |  | ARUN144CTE4 | Non-Ducted Indoor Units | 138000 | 11.7 | 24.2 | 152000 | 3.6 | 98000 | 2.53 | R-410A | 11.5
202534347 | 1/1/2027 | LG | HMSV-A-CB | ARUN168CTE4 |  |  |  | ARUN168CTE4 | Non-Ducted Indoor Units | 160000 | 11.1 | 22.1 | 180000 | 3.4 | 117000 | 2.34 | R-410A | 13.3333
202534348 | 1/1/2027 | LG | HMSV-A-CB | ARUN072CTE4 | ARUN121CTE4 |  |  | ARUN192CTE4 | Non-Ducted Indoor Units | 184000 | 11.5 | 22.5 | 206000 | 3.62 | 134000 | 2.45 | R-410A | 15.3333
202534349 | 1/1/2027 | LG | HMSV-A-CB | ARUN072CTE4 | ARUN144CTE4 |  |  | ARUN216CTE4 | Non-Ducted Indoor Units | 206000 | 12.2 | 21 | 230000 | 3.72 | 150000 | 2.58 | R-410A | 17.1667
202534350 | 1/1/2027 | LG | HMSV-A-CB | ARUN096CTE4 | ARUN144CTE4 |  |  | ARUN240CTE4 | Non-Ducted Indoor Units | 228000 | 12.2 | 20.2 | 256000 | 3.67 | 168000 | 2.61 | R-410A | 19
202534358 | 1/1/2027 | LG | HMSV-A-CB | ARUN144CTE4 |  |  |  | ARUN144CTE4 | Ducted Indoor Units | 138000 | 11.8 | 22.5 | 152000 | 3.49 | 98000 | 2.52 | R-410A | 11.5
202534360 | 1/1/2027 | LG | HMSV-A-CB | ARUN072CTE4 | ARUN121CTE4 |  |  | ARUN192CTE4 | Ducted Indoor Units | 184000 | 12.5 | 21 | 206000 | 3.66 | 134000 | 2.49 | R-410A | 15.3333
202534361 | 1/1/2027 | LG | HMSV-A-CB | ARUN072CTE4 | ARUN144CTE4 |  |  | ARUN216CTE4 | Ducted Indoor Units | 206000 | 12 | 20 | 230000 | 3.66 | 150000 | 2.47 | R-410A | 17.1667
202534362 | 1/1/2027 | LG | HMSV-A-CB | ARUN096CTE4 | ARUN144CTE4 |  |  | ARUN240CTE4 | Ducted Indoor Units | 228000 | 11.6 | 18 | 256000 | 3.56 | 168000 | 2.4 | R-410A | 19
206453550 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 |  |  |  | ARUM168CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.4 | 23.65 | 180000 | 3.38 | 117000 | 2.41 | R-410A | 13.3333
206453547 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 138000 | 12.3 | 25.8 | 152000 | 3.68 | 98000 | 2.57 | R-410A | 11.5
205281466 | 1/1/2027 | LG | HMSR-A-CB | ARUM144CTE5 |  |  |  | ARUM144CTE5 | Ducted Indoor Units | 138000 | 12.1 | 23 | 152000 | 3.52 | 98000 | 2.48 | R-410A | 11.5
206453535 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 |  |  |  | ARUM192CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 184000 | 11.7 | 24.45 | 206000 | 3.52 | 134000 | 2.52 | R-410A | 15.3333
206453536 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 |  |  |  | ARUM216CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 206000 | 10.95 | 23.6 | 230000 | 3.36 | 150000 | 2.5 | R-410A | 17.1667
208102095 | 1/1/2027 | LENNOX | HMSR-A-CB | VER096C432G | VER120C432G |  |  | VER216C432G | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
208102097 | 1/1/2027 | LENNOX | HMSR-A-CB | VER096C432Y | VER120C432Y |  |  | VER216C432Y | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
208102024 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP096C432G |  |  | VEP168C432G | Ducted Indoor Units | 160000 | 10.9 | 20 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
208102041 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G | VEP120C432G |  |  | VEP240C432G | Non-Ducted Indoor Units | 228000 | 10.8 | 22 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
208102043 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432Y | VEP120C432Y |  |  | VEP240C432Y | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
208102036 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP120C432G |  |  | VEP216C432G | Non-Ducted Indoor Units | 206000 | 11 | 23 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
208102038 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432Y | VEP096C432Y |  |  | VEP216C432Y | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
208102031 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G |  |  | VEP192C432G | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
208102033 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP096C432Y |  |  | VEP192C432Y | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
208102027 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y | VEP096C432Y |  |  | VEP168C432Y | Ducted Indoor Units | 160000 | 10.9 | 21.5 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
208102021 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP072C432G |  |  | VEP144C432G | Ducted Indoor Units | 138000 | 10.8 | 20.5 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
208102017 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y | VEP072C432Y |  |  | VEP140C432Y | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
10306470 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H6CDC712(A) | IOV072H6CDC712(A) |  |  | IOV144H6CDC725(A) | Ducted Indoor Units | 138000 | 10.8 | 20.5 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
10344560 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/B-F(U) | GMV-Q120WM/B-F(U) |  |  | GMV-Q216WM/B-F(U) | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
10341446 | 1/1/2027 | GREE | HMSR-A-CB | GMV-Q96WM/B-U(U) | GMV-Q120WM/B-U(U) |  |  | GMV-Q216WM/B-U(U) | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
10306441 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) | IOV072H3CDC712(A) |  |  | IOV144H3CDC725(A) | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
10306444 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) | IOV096H3CDC716(A) |  |  | IOV168H3CDC729(A) | Ducted Indoor Units | 160000 | 10.9 | 21.5 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
10306447 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV096H3CDC716(A) |  |  | IOV192H3CDC733(A) | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
10306449 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV120H3CDC720(A) |  |  | IOV216H3CDC737(A) | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
10306451 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC720(A) | IOV120H3CDC720(A) |  |  | IOV240H3CDC741(A) | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
201904248 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER096C432G | VER120C432G |  |  | VER216C432G | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
201903113 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432G | VEP120C432G |  |  | VEP240C432G | Non-Ducted Indoor Units | 228000 | 10.8 | 22 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
201903109 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP120C432G |  |  | VEP216C432G | Non-Ducted Indoor Units | 206000 | 11 | 23 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
201903105 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G |  |  | VEP192C432G | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
201902944 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP096C432G |  |  | VEP168C432G | Ducted Indoor Units | 160000 | 10.9 | 20 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
201902938 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP072C432G |  |  | VEP144C432G | Ducted Indoor Units | 138000 | 10.8 | 20.5 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
201874091 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  |  | PUHY-P144YSLMU-A | Ducted Indoor Units | 136000 | 12.6 | 21.3 | 152000 | 3.6 | 109000 | 2.43 | R-410A | 11.3333
204442761 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR |  |  |  | AM144FXVAJR | Non-Ducted Indoor Units | 138000 | 11.5 | 23.9 | 154000 | 3.81 | 100000 | 2.55 | R-410A | 11.5
204442762 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192HXVAJR |  |  |  | AM192HXVAJR | Non-Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.61 | 134000 | 2.53 | R-410A | 15.3333
204442764 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM168HXVAJR |  |  | AM240JXVAJR | Non-Ducted Indoor Units | 228000 | 10.8 | 23 | 258000 | 3.65 | 168000 | 2.5 | R-410A | 19
204442795 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM072KXVTFR |  | AM216KXVTFR | Non-Ducted Indoor Units | 206000 | 13.3 | 28.3 | 230000 | 3.81 | 230000 | 2.12 | R-410A | 17.1667
204442796 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM072KXVTFR | AM096KXVTFR |  | AM240KXVTFR | Non-Ducted Indoor Units | 228000 | 13.4 | 28.5 | 258000 | 3.77 | 258000 | 2.11 | R-410A | 19
204442801 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR |  |  | AM144KXVTJR | Non-Ducted Indoor Units | 138000 | 13.3 | 29.8 | 154000 | 3.71 | 154000 | 2.15 | R-410A | 11.5
204442802 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR |  |  | AM192KXVTJR | Non-Ducted Indoor Units | 184000 | 13.1 | 29.1 | 206000 | 3.78 | 206000 | 2.15 | R-410A | 15.3333
204442803 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM072KXVTJR |  | AM216KXVTJR | Non-Ducted Indoor Units | 206000 | 13.3 | 28.3 | 230000 | 3.81 | 230000 | 2.12 | R-410A | 17.1667
204442804 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM072KXVTJR | AM096KXVTJR |  | AM240KXVTJR | Non-Ducted Indoor Units | 228000 | 13.4 | 28.5 | 258000 | 3.77 | 258000 | 2.11 | R-410A | 19
204442810 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216KXVGJR |  |  |  | AM216KXVGJR | Non-Ducted Indoor Units | 206000 | 11 | 24.5 | 230000 | 3.82 | 150000 | 2.7 | R-410A | 17.1667
9088670 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712 | IOV096H3CDC713 |  |  | IOV168H3CDC728 | Ducted Indoor Units | 160000 | 10.9 | 21.5 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
9133486 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC120KHP/220V | TVRF-OC120KHP/220V |  |  | TVRF-OC240KHP/220V | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
9133448 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V | TVRF-OC120KHP/220V |  |  | TVRF-OC216KHP/220V | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
9133445 | 1/1/2027 | TOSOT | HMSV-A-CB | TVRF-OC96KHP/220V | TVRF-OC96KHP/220V |  |  | TVRF-OC192KHP/220V | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
9088676 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC713 | IOV096H3CDC713 |  |  | IOV192H3CDC732 | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
9088678 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC713 | IOV120H3CDC714 |  |  | IOV216H3CDC736 | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
9088686 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC714 | IOV120H3CDC714 |  |  | IOV240H3CDC734 | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
9088667 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712 | IOV072H3CDC712 |  |  | IOV144H3CDC724 | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
8176006 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) |  |  | GMV-192WM/B-F(U) | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
8176007 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-120WM/B-F(U) |  |  | GMV-216WM/B-F(U) | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
8176008 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-F(U) | GMV-120WM/B-F(U) |  |  | GMV-240WM/B-F(U) | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
8176009 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) | GMV-96WM/B-F(U) |  |  | GMV-168WM/B-F(U) | Ducted Indoor Units | 160000 | 10.9 | 21.5 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
9505334 | 1/1/2027 | INNOVAIR | HMSV-A-CB | V5BV-72WMBC | V5BV-96WMBC |  |  | V5BV-168WMBC | Ducted Indoor Units | 160000 | 10.9 | 21.5 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
10267482 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  |  | GMV-240WM/B-U(U) | Non-Ducted Indoor Units | 228000 | 10.8 | 22 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
10267479 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) |  |  | GMV-216WM/B-U(U) | Non-Ducted Indoor Units | 206000 | 11 | 23 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
10267476 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  |  | GMV-192WM/B-U(U) | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
10267470 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-72WM/B-U(U) |  |  | GMV-144WM/B-U(U) | Ducted Indoor Units | 138000 | 10.8 | 20.5 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
10267472 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-96WM/B-U(U) |  |  | GMV-168WM/B-U(U) | Ducted Indoor Units | 160000 | 10.9 | 20 | 180000 | 3.33 | 118000 | 2.28 | R-410A | 13.3333
9956558 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y | VEP072C432Y |  |  | VEP140C432Y | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
9956567 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y | VEP096C432Y |  |  | VEP192C432Y | Non-Ducted Indoor Units | 184000 | 11.3 | 23 | 206000 | 3.4 | 134000 | 2.1 | R-410A | 15.3333
9956569 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432Y | VEP096C432Y |  |  | VEP216C432Y | Non-Ducted Indoor Units | 206000 | 11 | 24.7 | 230000 | 3.52 | 150000 | 2.25 | R-410A | 17.1667
9956577 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432Y | VEP120C432Y |  |  | VEP240C432Y | Non-Ducted Indoor Units | 228000 | 10.8 | 23.4 | 256000 | 3.49 | 168000 | 2.23 | R-410A | 19
7793599 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) | GMV-72WM/B-F(U) |  |  | GMV-144WM/B-F(U) | Ducted Indoor Units | 138000 | 10.8 | 21.6 | 154000 | 3.3 | 100000 | 2.3 | R-410A | 11.5
204442747 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192HXVAFR |  |  |  | AM192HXVAFR | Non-Ducted Indoor Units | 184000 | 11.1 | 20.5 | 206000 | 3.61 | 134000 | 2.53 | R-410A | 15.3333
204442749 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM168HXVAFR |  |  | AM240JXVAFR | Non-Ducted Indoor Units | 228000 | 10.8 | 23 | 258000 | 3.65 | 168000 | 2.5 | R-410A | 19
201866461 | 1/1/2027 | LENNOX VRF | HMSR-A-CB | VER096C432Y | VER120C432Y |  |  | VER216C432Y | Non-Ducted Indoor Units | 200000 | 11.2 | 21 | 226000 | 3.3 | 160000 | 2.1 | R-410A | 16.6667
9119338 | 1/1/2027 | LG | HMSV-A-CB | ARUN144QTE4 |  |  |  | ARUN144QTE4 | Ducted Indoor Units | 138000 | 11.9 | 22.5 | 152000 | 3.49 | 98000 | 2.52 | R-410A | 11.5
9119339 | 1/1/2027 | LG | HMSV-A-CB | ARUN144QTE4 |  |  |  | ARUN144QTE4 | Non-Ducted Indoor Units | 138000 | 12.4 | 27 | 152000 | 3.8 | 98000 | 2.69 | R-410A | 11.5
202534368 | 1/1/2027 | LG | HMSV-A-CB | ARUN168QTE4 |  |  |  | ARUN168QTE4 | Non-Ducted Indoor Units | 160000 | 11.8 | 22.5 | 180000 | 3.6 | 117000 | 2.51 | R-410A | 13.3333
10567396 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-168U8S1B |  |  |  | AVWT-168U8S1B | Non-Ducted Indoor Units | 160000 | 12.25 | 27.15 | 170000 | 3.68 | 105000 | 2.5 | R-410A | 13.3333
10567400 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-168U8S1B |  |  |  | AVWT-168U8S1B | Mixed Ducted and Non-Ducted Indoor Units | 160000 | 11.57 | 24.72 | 170000 | 3.45 | 105000 | 2.35 | R-410A | 13.3333
10594387 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B |  |  |  | AVWT-144U8S1B | Ducted Indoor Units | 144000 | 10.8 | 21.3 | 154000 | 3.25 | 96000 | 2.3 | R-410A | 12
10594388 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B |  |  |  | AVWT-144U8S1B | Non-Ducted Indoor Units | 144000 | 12.1 | 27.2 | 154000 | 3.64 | 96000 | 2.45 | R-410A | 12
10594389 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-120U8STB | AVWT-072U8SNB |  |  | AVWT-192U8SZB | Non-Ducted Indoor Units | 184000 | 12.1 | 27.5 | 206000 | 3.75 | 136000 | 2.53 | R-410A | 15.3333
10594390 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-072U8SNB |  |  | AVWT-216U8SZB | Non-Ducted Indoor Units | 208000 | 11.35 | 25.2 | 230000 | 3.6 | 150000 | 2.4 | R-410A | 17.3333
10594391 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-96U8STB |  |  | AVWT-240U8SZB | Non-Ducted Indoor Units | 230000 | 11.3 | 24.95 | 256000 | 3.66 | 164000 | 2.42 | R-410A | 19.1667
10594398 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-120U8STB | AVWT-072U8SNB |  |  | AVWT-192U8SZB | Ducted Indoor Units | 184000 | 11.9 | 24.1 | 206000 | 3.28 | 136000 | 2.32 | R-410A | 15.3333
10594399 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-072U8SNB |  |  | AVWT-216U8SZB | Ducted Indoor Units | 208000 | 11.35 | 22.8 | 230000 | 3.25 | 150000 | 2.27 | R-410A | 17.3333
10594400 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-96U8STB |  |  | AVWT-240U8SZB | Ducted Indoor Units | 230000 | 11.45 | 23.75 | 256000 | 3.25 | 164000 | 2.32 | R-410A | 19.1667
10594407 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B |  |  |  | AVWT-144U8S1B | Mixed Ducted and Non-Ducted Indoor Units | 144000 | 11.45 | 24.25 | 154000 | 3.44 | 96000 | 2.37 | R-410A | 12
208931871 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA120ULBV5 |  |  | AOUA264ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.45 | 20.1 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931873 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 |  |  | AOUA288ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.9 | 19.8 | 308000 | 3.38 | 210000 | 2.16 | R-410A | 23
208931883 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA120ULBV5 |  | AOUA408ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 11 | 20.15 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931885 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULBV5 | AOUA144ULBV5 | AOUA144ULBV5 |  | AOUA432ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 10.8 | 20.2 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931875 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA144ULBV5 |  |  | AOUA312ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.9 | 19.8 | 320000 | 3.38 | 214000 | 2.16 | R-410A | 24.8333
208931877 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULBV5 | AOUA168ULBV5 |  |  | AOUA336ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.9 | 19.8 | 338000 | 3.38 | 224000 | 2.16 | R-410A | 26.6667
208931879 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA168ULBV5 |  |  | AOUA360ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 19.8 | 346000 | 3.38 | 232000 | 2.16 | R-410A | 28.6667
208931881 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULBV5 | AOUA192ULBV5 |  |  | AOUA384ULBVG5 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 19.8 | 354000 | 3.38 | 240000 | 2.16 | R-410A | 30.5
208931905 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA120ULCV5 |  | AOUA408ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 11 | 20.15 | 394000 | 3.46 | 260000 | 2.31 | R-410A | 32.5
208931907 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 | AOUA144ULCV5 |  | AOUA432ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 10.8 | 20.2 | 404000 | 3.53 | 280000 | 2.3 | R-410A | 34.3333
208931893 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA120ULCV5 |  |  | AOUA264ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.45 | 20.1 | 282000 | 3.52 | 194000 | 2.31 | R-410A | 21
208931895 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA144ULCV5 | AOUA144ULCV5 |  |  | AOUA288ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.9 | 19.8 | 308000 | 3.38 | 210000 | 2.16 | R-410A | 23
208931897 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA144ULCV5 |  |  | AOUA312ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.9 | 19.8 | 320000 | 3.38 | 214000 | 2.16 | R-410A | 24.8333
208931899 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA168ULCV5 | AOUA168ULCV5 |  |  | AOUA336ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.9 | 19.8 | 338000 | 3.38 | 224000 | 2.16 | R-410A | 26.6667
208931901 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA168ULCV5 |  |  | AOUA360ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 19.8 | 346000 | 3.38 | 232000 | 2.16 | R-410A | 28.6667
208931903 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA192ULCV5 | AOUA192ULCV5 |  |  | AOUA384ULCVG5 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 19.8 | 354000 | 3.38 | 240000 | 2.16 | R-410A | 30.5
213894144 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP2881HT6P-UL | Ducted Indoor Units | 276000 | 10.8 | 21.4 | 308000 | 3.81 | 216000 | 2.56 | R-410A | 23
213894097 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP2881HT6P-UL | Non-Ducted Indoor Units | 276000 | 9.95 | 20.6 | 308000 | 3.61 | 216000 | 2.27 | R-410A | 23
213894101 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3841HT6P-UL | Non-Ducted Indoor Units | 366000 | 9.6 | 18.4 | 412000 | 3.45 | 294000 | 2.28 | R-410A | 30.5
213894162 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3841HT6P-UL | Ducted Indoor Units | 366000 | 11 | 18.9 | 412000 | 3.48 | 294000 | 2.29 | R-410A | 30.5
213895028 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP2881HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.37 | 21 | 308000 | 3.71 | 216000 | 2.41 | R-410A | 23
213895040 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3841HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.3 | 18.65 | 412000 | 3.46 | 294000 | 2.28 | R-410A | 30.5
213895042 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4081HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.1 | 18.15 | 438000 | 3.36 | 310000 | 2.29 | R-410A | 32.5
213895044 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4321HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.95 | 18.05 | 462000 | 3.34 | 328000 | 2.29 | R-410A | 34.3333
213895046 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP1201HT6P-UL |  | MMY-UP4561HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.65 | 17.45 | 488000 | 3.3 | 350000 | 2.28 | R-410A | 36.1667
213895032 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP3121HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 20.2 | 334000 | 3.57 | 236000 | 2.44 | R-410A | 24.8333
213895034 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL |  |  | MMY-UP3361HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.35 | 20.35 | 360000 | 3.47 | 268000 | 2.29 | R-410A | 26.6667
213895036 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3601HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.42 | 18.9 | 386000 | 3.47 | 284000 | 2.29 | R-410A | 28.5
213895026 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2641HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.6 | 22.65 | 284000 | 3.76 | 200000 | 2.51 | R-410A | 21
213894157 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3601HT6P-UL | Ducted Indoor Units | 342000 | 11.2 | 19.4 | 386000 | 3.5 | 284000 | 2.45 | R-410A | 28.5
213894165 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4081HT6P-UL | Ducted Indoor Units | 390000 | 10.4 | 18.4 | 438000 | 3.38 | 310000 | 2.39 | R-410A | 32.5
213894168 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4321HT6P-UL | Ducted Indoor Units | 412000 | 9.9 | 17.6 | 462000 | 3.35 | 328000 | 2.41 | R-410A | 34.3333
213894096 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2641HT6P-UL | Non-Ducted Indoor Units | 252000 | 10.3 | 20.2 | 284000 | 3.74 | 200000 | 2.49 | R-410A | 21
213894102 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4081HT6P-UL | Non-Ducted Indoor Units | 390000 | 9.8 | 17.9 | 438000 | 3.34 | 310000 | 2.19 | R-410A | 32.5
213894103 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP4321HT6P-UL | Non-Ducted Indoor Units | 412000 | 10 | 18.5 | 462000 | 3.33 | 328000 | 2.17 | R-410A | 34.3333
213894104 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL | MMY-MUP1201HT6P-UL |  | MMY-UP4561HT6P-UL | Non-Ducted Indoor Units | 434000 | 9.8 | 17.6 | 488000 | 3.28 | 350000 | 2.21 | R-410A | 36.1667
213894098 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP3121HT6P-UL | Non-Ducted Indoor Units | 298000 | 9.6 | 20 | 334000 | 3.54 | 236000 | 2.44 | R-410A | 24.8333
213894099 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL |  |  | MMY-UP3361HT6P-UL | Non-Ducted Indoor Units | 320000 | 10.6 | 20.8 | 360000 | 3.53 | 268000 | 2.21 | R-410A | 26.6667
213894100 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL | MMY-MUP0961HT6P-UL |  | MMY-UP3601HT6P-UL | Non-Ducted Indoor Units | 342000 | 9.65 | 18.4 | 386000 | 3.44 | 284000 | 2.13 | R-410A | 28.5
213894139 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP0961HT6P-UL |  |  | MMY-UP2641HT6P-UL | Ducted Indoor Units | 252000 | 10.3 | 21 | 284000 | 3.82 | 200000 | 2.55 | R-410A | 21
213894149 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1441HT6P-UL |  |  | MMY-UP3121HT6P-UL | Ducted Indoor Units | 298000 | 10.1 | 20.4 | 334000 | 3.6 | 236000 | 2.44 | R-410A | 24.8333
213894152 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT6P-UL | MMY-MUP1681HT6P-UL |  |  | MMY-UP3361HT6P-UL | Ducted Indoor Units | 320000 | 10 | 18.4 | 360000 | 3.46 | 268000 | 2.39 | R-410A | 26.6667
213894146 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  | MMY-UP288H1HT6PUL | Ducted Indoor Units | 276000 | 11.2 | 18.8 | 308000 | 4.08 | 260000 | 2.48 | R-410A | 23
213894142 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  | MMY-UP288H1HT6PUL | Non-Ducted Indoor Units | 276000 | 11 | 19.3 | 308000 | 3.82 | 260000 | 2.31 | R-410A | 23
213895030 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL | MMY-MUP096H1HT6PUL |  | MMY-UP288H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.1 | 19.05 | 308000 | 3.95 | 260000 | 2.39 | R-410A | 23
213895038 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  | MMY-UP360H1HT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.45 | 19.4 | 386000 | 3.75 | 348000 | 2.47 | R-410A | 28.5
213894155 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  | MMY-UP360H1HT6PUL | Non-Ducted Indoor Units | 342000 | 10.1 | 19.3 | 386000 | 3.7 | 348000 | 2.46 | R-410A | 28.5
213894159 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL | MMY-MUP120H1HT6PUL |  | MMY-UP360H1HT6PUL | Ducted Indoor Units | 342000 | 10.8 | 19.5 | 386000 | 3.8 | 348000 | 2.48 | R-410A | 28.5
213895041 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3841HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.3 | 18.65 | 412000 | 3.46 | 294000 | 2.28 | R-410A | 30.5
213895029 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP2881HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.37 | 21 | 308000 | 3.71 | 216000 | 2.41 | R-410A | 23
213894145 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP2881HT9P-UL | Ducted Indoor Units | 276000 | 10.8 | 21.4 | 308000 | 3.81 | 216000 | 2.56 | R-410A | 23
213894141 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP2881HT9P-UL | Non-Ducted Indoor Units | 276000 | 9.95 | 20.6 | 308000 | 3.61 | 216000 | 2.27 | R-410A | 23
213894163 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3841HT9P-UL | Ducted Indoor Units | 366000 | 11 | 18.9 | 412000 | 3.48 | 294000 | 2.29 | R-410A | 30.5
213894161 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1441HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3841HT9P-UL | Non-Ducted Indoor Units | 366000 | 9.6 | 18.4 | 412000 | 3.45 | 294000 | 2.28 | R-410A | 30.5
213894148 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP3121HT9P-UL | Non-Ducted Indoor Units | 298000 | 9.6 | 20 | 334000 | 3.54 | 236000 | 2.44 | R-410A | 24.8333
213894164 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4081HT9P-UL | Non-Ducted Indoor Units | 390000 | 9.8 | 17.9 | 438000 | 3.34 | 310000 | 2.19 | R-410A | 32.5
213894158 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3601HT9P-UL | Ducted Indoor Units | 342000 | 11.2 | 19.4 | 386000 | 3.5 | 284000 | 2.45 | R-410A | 28.5
213894169 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4321HT9P-UL | Ducted Indoor Units | 412000 | 9.9 | 17.6 | 462000 | 3.35 | 328000 | 2.41 | R-410A | 34.3333
213894170 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP1201HT9P-UL |  | MMY-UP4561HT9P-UL | Non-Ducted Indoor Units | 434000 | 9.8 | 17.6 | 488000 | 3.28 | 350000 | 2.21 | R-410A | 36.1667
213894166 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4081HT9P-UL | Ducted Indoor Units | 390000 | 10.4 | 18.4 | 438000 | 3.38 | 310000 | 2.39 | R-410A | 32.5
213894167 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4321HT9P-UL | Non-Ducted Indoor Units | 412000 | 10 | 18.5 | 462000 | 3.33 | 328000 | 2.17 | R-410A | 34.3333
213894140 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2641HT9P-UL | Ducted Indoor Units | 252000 | 10.3 | 21 | 284000 | 3.82 | 200000 | 2.55 | R-410A | 21
213894153 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL |  |  | MMY-UP3361HT9P-UL | Ducted Indoor Units | 320000 | 10 | 18.4 | 360000 | 3.46 | 268000 | 2.39 | R-410A | 26.6667
213894154 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3601HT9P-UL | Non-Ducted Indoor Units | 342000 | 9.65 | 18.4 | 386000 | 3.44 | 284000 | 2.13 | R-410A | 28.5
213894150 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP3121HT9P-UL | Ducted Indoor Units | 298000 | 10.1 | 20.4 | 334000 | 3.6 | 236000 | 2.44 | R-410A | 24.8333
213894151 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL |  |  | MMY-UP3361HT9P-UL | Non-Ducted Indoor Units | 320000 | 10.6 | 20.8 | 360000 | 3.53 | 268000 | 2.21 | R-410A | 26.6667
213894138 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2641HT9P-UL | Non-Ducted Indoor Units | 252000 | 10.3 | 20.2 | 284000 | 3.74 | 200000 | 2.49 | R-410A | 21
213895027 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  |  | MMY-UP2641HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.6 | 22.65 | 284000 | 3.76 | 200000 | 2.51 | R-410A | 21
213895043 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4081HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.1 | 18.15 | 438000 | 3.36 | 310000 | 2.29 | R-410A | 32.5
213895047 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP1201HT9P-UL |  | MMY-UP4561HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.65 | 17.45 | 488000 | 3.3 | 350000 | 2.28 | R-410A | 36.1667
213895045 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP4321HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.95 | 18.05 | 462000 | 3.34 | 328000 | 2.29 | R-410A | 34.3333
213895037 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP0961HT9P-UL | MMY-MUP0961HT9P-UL |  | MMY-UP3601HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.42 | 18.9 | 386000 | 3.47 | 284000 | 2.29 | R-410A | 28.5
213895035 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1681HT9P-UL |  |  | MMY-UP3361HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 21.6 | 360000 | 3.47 | 268000 | 2.29 | R-410A | 26.6667
213895033 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP1681HT9P-UL | MMY-MUP1441HT9P-UL |  |  | MMY-UP3121HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 20.2 | 334000 | 3.57 | 236000 | 2.44 | R-410A | 24.8333
213894147 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  | MMY-UP288H1HT9PUL | Ducted Indoor Units | 276000 | 11.2 | 18.8 | 308000 | 4.08 | 260000 | 2.48 | R-410A | 23
213894143 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  | MMY-UP288H1HT9PUL | Non-Ducted Indoor Units | 276000 | 11 | 19.3 | 308000 | 3.82 | 260000 | 2.31 | R-410A | 23
213895031 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL | MMY-MUP096H1HT9PUL |  | MMY-UP288H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.1 | 19.05 | 308000 | 3.95 | 260000 | 2.39 | R-410A | 23
213895039 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  | MMY-UP360H1HT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.45 | 19.4 | 386000 | 3.75 | 348000 | 2.47 | R-410A | 28.5
213894156 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  | MMY-UP360H1HT9PUL | Non-Ducted Indoor Units | 342000 | 10.1 | 19.3 | 386000 | 3.7 | 348000 | 2.46 | R-410A | 28.5
213894160 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL | MMY-MUP120H1HT9PUL |  | MMY-UP360H1HT9PUL | Ducted Indoor Units | 342000 | 10.8 | 19.5 | 386000 | 3.8 | 348000 | 2.48 | R-410A | 28.5
213884978 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP3841FT6P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 20.4 | 412000 | 3.53 | 274000 | 2.6 | R-410A | 30.5
213884954 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP2881FT6P-UL | Non-Ducted Indoor Units | 276000 | 11.6 | 22.8 | 308000 | 3.88 | 200000 | 2.45 | R-410A | 23
213884958 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP2881FT6P-UL | Ducted Indoor Units | 276000 | 10.6 | 21.7 | 308000 | 3.27 | 200000 | 2.43 | R-410A | 23
213885204 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP2881FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.1 | 22.25 | 308000 | 3.57 | 200000 | 2.44 | R-410A | 23
213885217 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP3841FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.4 | 19.5 | 412000 | 3.38 | 274000 | 2.57 | R-410A | 30.5
213885219 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP4081FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.15 | 19.2 | 438000 | 3.37 | 296000 | 2.57 | R-410A | 32.5
213885212 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP3601FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.45 | 20.05 | 386000 | 3.39 | 270000 | 2.5 | R-410A | 28.5
213885208 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP3121FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.95 | 21.6 | 334000 | 3.55 | 222000 | 2.43 | R-410A | 24.8333
213885210 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL |  |  | MMY-UP3361FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 20.85 | 360000 | 3.4 | 244000 | 2.43 | R-410A | 26.6667
213885203 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2641FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.2 | 22.35 | 284000 | 3.6 | 196000 | 2.44 | R-410A | 21
213885221 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP4321FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.85 | 19.1 | 462000 | 3.35 | 318000 | 2.51 | R-410A | 34.3333
213885223 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL |  | MMY-UP4561FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.85 | 18.95 | 488000 | 3.34 | 322000 | 2.49 | R-410A | 36.1667
213885225 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL |  | MMY-UP4801FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 456000 | 9.7 | 18.95 | 514000 | 3.29 | 344000 | 2.47 | R-410A | 38
213884962 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP3121FT6P-UL | Non-Ducted Indoor Units | 298000 | 11.3 | 22.2 | 334000 | 3.86 | 222000 | 2.44 | R-410A | 24.8333
213884964 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL |  |  | MMY-UP3121FT6P-UL | Ducted Indoor Units | 298000 | 10.6 | 21 | 334000 | 3.25 | 222000 | 2.42 | R-410A | 24.8333
213884966 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL |  |  | MMY-UP3361FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.6 | 21.4 | 360000 | 3.57 | 244000 | 2.44 | R-410A | 26.6667
213884970 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP3601FT6P-UL | Non-Ducted Indoor Units | 342000 | 10.6 | 20.5 | 386000 | 3.54 | 270000 | 2.51 | R-410A | 28.5
213884950 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2641FT6P-UL | Non-Ducted Indoor Units | 252000 | 11.7 | 22.9 | 284000 | 3.92 | 196000 | 2.46 | R-410A | 21
213884952 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL |  |  | MMY-UP2641FT6P-UL | Ducted Indoor Units | 252000 | 10.7 | 21.8 | 284000 | 3.28 | 196000 | 2.43 | R-410A | 21
213884982 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP4081FT6P-UL | Non-Ducted Indoor Units | 390000 | 10.3 | 20.2 | 438000 | 3.51 | 296000 | 2.58 | R-410A | 32.5
213884986 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL | MMY-MUP0961FT6P-UL |  | MMY-UP4321FT6P-UL | Non-Ducted Indoor Units | 412000 | 9.9 | 20 | 462000 | 3.48 | 318000 | 2.52 | R-410A | 34.3333
213884990 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL | MMY-MUP1441FT6P-UL |  | MMY-UP4561FT6P-UL | Non-Ducted Indoor Units | 434000 | 9.9 | 19.8 | 488000 | 3.45 | 322000 | 2.5 | R-410A | 36.1667
213884994 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT6P-UL | MMY-MUP1681FT6P-UL | MMY-MUP1441FT6P-UL |  | MMY-UP4801FT6P-UL | Non-Ducted Indoor Units | 456000 | 9.7 | 19.8 | 514000 | 3.37 | 344000 | 2.49 | R-410A | 38
213884956 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  | MMY-UP288H1FT6PUL | Non-Ducted Indoor Units | 276000 | 12.6 | 21 | 308000 | 3.9 | 258000 | 2.48 | R-410A | 23
213884960 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  | MMY-UP288H1FT6PUL | Ducted Indoor Units | 276000 | 11.6 | 19.8 | 308000 | 3.59 | 258000 | 2.42 | R-410A | 23
213885206 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL | MMY-MUP096H1FT6PUL |  | MMY-UP288H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 12.1 | 20.4 | 308000 | 3.74 | 258000 | 2.45 | R-410A | 23
213885214 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  | MMY-UP360H1FT6PUL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.65 | 20.25 | 386000 | 3.62 | 330000 | 2.42 | R-410A | 28.5
213884972 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  | MMY-UP360H1FT6PUL | Non-Ducted Indoor Units | 342000 | 11.9 | 20.9 | 386000 | 3.69 | 330000 | 2.45 | R-410A | 28.5
213884976 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL | MMY-MUP120H1FT6PUL |  | MMY-UP360H1FT6PUL | Ducted Indoor Units | 342000 | 11.4 | 19.6 | 386000 | 3.55 | 330000 | 2.4 | R-410A | 28.5
213884979 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP3841FT9P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 20.4 | 412000 | 3.53 | 274000 | 2.6 | R-410A | 30.5
213884955 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP2881FT9P-UL | Non-Ducted Indoor Units | 276000 | 11.6 | 22.8 | 308000 | 3.88 | 200000 | 2.45 | R-410A | 23
213884959 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP2881FT9P-UL | Ducted Indoor Units | 276000 | 10.6 | 21.7 | 308000 | 3.27 | 200000 | 2.43 | R-410A | 23
213885205 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP2881FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.1 | 22.25 | 308000 | 3.57 | 200000 | 2.44 | R-410A | 23
213885216 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP3841FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.4 | 19.5 | 412000 | 3.38 | 274000 | 2.57 | R-410A | 30.5
213885224 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL |  | MMY-UP4801FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 456000 | 9.7 | 18.95 | 514000 | 3.29 | 344000 | 2.47 | R-410A | 38
213885222 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL |  | MMY-UP4561FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 434000 | 9.85 | 18.95 | 488000 | 3.34 | 322000 | 2.49 | R-410A | 36.1667
213885211 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL |  |  | MMY-UP3361FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 20.85 | 360000 | 3.4 | 244000 | 2.43 | R-410A | 26.6667
213885209 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP3121FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.95 | 21.6 | 334000 | 3.55 | 222000 | 2.43 | R-410A | 24.8333
213885213 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP3601FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.45 | 20.05 | 386000 | 3.39 | 270000 | 2.5 | R-410A | 28.5
213885220 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP4321FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.85 | 19.1 | 462000 | 3.35 | 318000 | 2.51 | R-410A | 34.3333
213885218 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP4081FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.15 | 19.2 | 438000 | 3.37 | 296000 | 2.57 | R-410A | 32.5
213885202 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2641FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.2 | 22.35 | 284000 | 3.6 | 196000 | 2.44 | R-410A | 21
213884965 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP3121FT9P-UL | Ducted Indoor Units | 298000 | 10.6 | 21 | 334000 | 3.25 | 222000 | 2.42 | R-410A | 24.8333
213884963 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL |  |  | MMY-UP3121FT9P-UL | Non-Ducted Indoor Units | 298000 | 11.3 | 22.2 | 334000 | 3.86 | 222000 | 2.44 | R-410A | 24.8333
213884971 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP3601FT9P-UL | Non-Ducted Indoor Units | 342000 | 10.6 | 20.5 | 386000 | 3.54 | 270000 | 2.51 | R-410A | 28.5
213884967 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL |  |  | MMY-UP3361FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.6 | 21.4 | 360000 | 3.57 | 244000 | 2.44 | R-410A | 26.6667
213884953 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2641FT9P-UL | Ducted Indoor Units | 252000 | 10.7 | 21.8 | 284000 | 3.28 | 196000 | 2.43 | R-410A | 21
213884951 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL |  |  | MMY-UP2641FT9P-UL | Non-Ducted Indoor Units | 252000 | 11.7 | 22.9 | 284000 | 3.92 | 196000 | 2.46 | R-410A | 21
213884987 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP4321FT9P-UL | Non-Ducted Indoor Units | 412000 | 9.9 | 20 | 462000 | 3.48 | 318000 | 2.52 | R-410A | 34.3333
213884983 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP0961FT9P-UL |  | MMY-UP4081FT9P-UL | Non-Ducted Indoor Units | 390000 | 10.3 | 20.2 | 438000 | 3.51 | 296000 | 2.58 | R-410A | 32.5
213884995 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL |  | MMY-UP4801FT9P-UL | Non-Ducted Indoor Units | 456000 | 9.7 | 19.8 | 514000 | 3.37 | 344000 | 2.49 | R-410A | 38
213884991 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP1681FT9P-UL | MMY-MUP1441FT9P-UL | MMY-MUP1441FT9P-UL |  | MMY-UP4561FT9P-UL | Non-Ducted Indoor Units | 434000 | 9.9 | 19.8 | 488000 | 3.45 | 322000 | 2.5 | R-410A | 36.1667
213885207 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  | MMY-UP288H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 12.1 | 20.4 | 308000 | 3.74 | 258000 | 2.45 | R-410A | 23
213884957 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  | MMY-UP288H1FT9PUL | Non-Ducted Indoor Units | 276000 | 12.6 | 21 | 308000 | 3.9 | 258000 | 2.48 | R-410A | 23
213884961 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL | MMY-MUP096H1FT9PUL |  | MMY-UP288H1FT9PUL | Ducted Indoor Units | 276000 | 11.6 | 19.8 | 308000 | 3.59 | 258000 | 2.42 | R-410A | 23
213884973 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  | MMY-UP360H1FT9PUL | Non-Ducted Indoor Units | 342000 | 11.9 | 20.9 | 386000 | 3.69 | 330000 | 2.45 | R-410A | 28.5
213884977 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  | MMY-UP360H1FT9PUL | Ducted Indoor Units | 342000 | 11.4 | 19.6 | 386000 | 3.55 | 330000 | 2.4 | R-410A | 28.5
213885215 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL | MMY-MUP120H1FT9PUL |  | MMY-UP360H1FT9PUL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.65 | 20.25 | 386000 | 3.62 | 330000 | 2.42 | R-410A | 28.5
201830249 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 | MV5-H96DXN1 |  | MV5-H312DXN1* | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201830250 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 | MV5-H96DXN1 |  | MV5-H312DXN1* | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201830251 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 | MV5-H96DXN1 |  | MV5-H336DXN1* | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201830252 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 | MV5-H96DXN1 |  | MV5-H336DXN1* | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201850139 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201850140 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201850141 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201850142 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201994686 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201994687 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201994689 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201994691 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201850256 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201850257 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201850258 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201850259 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
202073595 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 | MV5-H96DXN1 |  | MV5-H312DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.25 | 18.76 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
202073596 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 | MV5-H96DXN1 |  | MV5-H336DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 9.9 | 17.92 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
204723056 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
204723057 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
204723058 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
204723059 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
207591034 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
207591035 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
207591036 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
207591037 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201830281 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 | MV5-H96DZN1 |  | MV5-H312DZN1* | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201830282 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 | MV5-H96DZN1 |  | MV5-H312DZN1* | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201830283 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 | MV5-H96DZN1 |  | MV5-H336DZN1* | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201830284 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 | MV5-H96DZN1 |  | MV5-H336DZN1* | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201850171 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201850172 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201850173 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201850174 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201850288 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201850289 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201850290 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201850291 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
201994739 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
201994741 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
201994742 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
201994744 | 1/1/2027 | Day&night | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
202073611 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 | MV5-H96DZN1 |  | MV5-H312DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.25 | 18.76 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
202073612 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 | MV5-H96DZN1 |  | MV5-H336DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 9.9 | 17.92 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
204723088 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
204723089 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
204723090 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
204723091 | 1/1/2027 | ICP | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
207591066 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 10.49 | 19 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
207591067 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.07 | 18.52 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
207591068 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.03 | 18.05 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
207591069 | 1/1/2027 | Arcoaire | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 9.85 | 17.8 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
204723118 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201850201 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201850318 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201830311 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DXN1 |  |  |  | MV5-2R264DXN1* | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201994790 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
202073626 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DXN1 |  |  |  | MV5-2R264DXN1* | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.1 | 19.9 | 274000 | 3.29 | 186000 | 2.24 | R-410A | 20.6667
207591096 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
207591122 | 1/1/2027 | Arcoaire | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
202073639 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DZN1 |  |  |  | MV5-2R264DZN1* | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.1 | 19.9 | 274000 | 3.29 | 186000 | 2.24 | R-410A | 20.6667
201850344 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201994832 | 1/1/2027 | Day&night | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201830337 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DZN1 |  |  |  | MV5-2R264DZN1* | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
201850228 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
204723144 | 1/1/2027 | ICP | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.1 | 20 | 274000 | 3.36 | 186000 | 2.3 | R-410A | 20.6667
202918881 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y | VPB120H4M-3Y |  |  | VPB264H4M-3Y | Non-Ducted Indoor Units | 252000 | 11 | 20.9 | 282000 | 3.64 | 200000 | 2.4 | R-410A | 21
202918882 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y | VPB120H4M-3Y |  |  | VPB264H4M-3Y | Ducted Indoor Units | 252000 | 11 | 20.5 | 282000 | 3.53 | 200000 | 2.42 | R-410A | 21
202918883 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3Y | VPB120H4M-3Y |  |  | VPB264H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.7 | 282000 | 3.58 | 200000 | 2.41 | R-410A | 21
202897242 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 | MV6-X120DXN1 |  |  | MV6-X264DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.7 | 282000 | 3.58 | 200000 | 2.41 | R-410A | 21
202897168 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 | MV6-X120DXN1 |  |  | MV6-X264DXN1 | Non-Ducted Indoor Units | 252000 | 11 | 20.9 | 282000 | 3.64 | 200000 | 2.4 | R-410A | 21
202897169 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DXN1 | MV6-X120DXN1 |  |  | MV6-X264DXN1 | Ducted Indoor Units | 252000 | 11 | 20.5 | 282000 | 3.53 | 200000 | 2.42 | R-410A | 21
202897206 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 | MV6-X120DZN1 |  |  | MV6-X264DZN1 | Non-Ducted Indoor Units | 252000 | 11 | 20.9 | 282000 | 3.64 | 200000 | 2.4 | R-410A | 21
202897207 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 | MV6-X120DZN1 |  |  | MV6-X264DZN1 | Ducted Indoor Units | 252000 | 11 | 20.5 | 282000 | 3.53 | 200000 | 2.42 | R-410A | 21
202897243 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X144DZN1 | MV6-X120DZN1 |  |  | MV6-X264DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.7 | 282000 | 3.58 | 200000 | 2.41 | R-410A | 21
202918878 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G | VPB120H4M-3G |  |  | VPB264H4M-3G | Non-Ducted Indoor Units | 252000 | 11 | 20.9 | 282000 | 3.64 | 200000 | 2.4 | R-410A | 21
202918879 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G | VPB120H4M-3G |  |  | VPB264H4M-3G | Ducted Indoor Units | 252000 | 11 | 20.5 | 282000 | 3.53 | 200000 | 2.42 | R-410A | 21
202918880 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB144H4M-3G | VPB120H4M-3G |  |  | VPB264H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.7 | 282000 | 3.58 | 200000 | 2.41 | R-410A | 21
202918989 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y | VRB120H4M-3Y |  |  | VRB264H4M-3Y | Non-Ducted Indoor Units | 252000 | 11.1 | 20.1 | 282000 | 3.61 | 200000 | 2.4 | R-410A | 21
202918990 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y | VRB120H4M-3Y |  |  | VRB264H4M-3Y | Ducted Indoor Units | 252000 | 11.1 | 19.9 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
202918991 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3Y | VRB120H4M-3Y |  |  | VRB264H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20 | 282000 | 3.55 | 200000 | 2.4 | R-410A | 21
202897244 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 | MV6-R120DXN1 |  |  | MV6-R264DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20 | 282000 | 3.55 | 200000 | 2.4 | R-410A | 21
202897208 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 | MV6-R120DXN1 |  |  | MV6-R264DXN1 | Non-Ducted Indoor Units | 252000 | 11.1 | 20.1 | 282000 | 3.61 | 200000 | 2.4 | R-410A | 21
202897209 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DXN1 | MV6-R120DXN1 |  |  | MV6-R264DXN1 | Ducted Indoor Units | 252000 | 11.1 | 19.9 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
202897210 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 | MV6-R120DZN1 |  |  | MV6-R264DZN1 | Non-Ducted Indoor Units | 252000 | 11.1 | 20.1 | 282000 | 3.61 | 200000 | 2.4 | R-410A | 21
202897211 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 | MV6-R120DZN1 |  |  | MV6-R264DZN1 | Ducted Indoor Units | 252000 | 11.1 | 19.9 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
202897245 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R144DZN1 | MV6-R120DZN1 |  |  | MV6-R264DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20 | 282000 | 3.55 | 200000 | 2.4 | R-410A | 21
202918986 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G | VRB120H4M-3G |  |  | VRB264H4M-3G | Non-Ducted Indoor Units | 252000 | 11.1 | 20.1 | 282000 | 3.61 | 200000 | 2.4 | R-410A | 21
202918987 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G | VRB120H4M-3G |  |  | VRB264H4M-3G | Ducted Indoor Units | 252000 | 11.1 | 19.9 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
202918988 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB144H4M-3G | VRB120H4M-3G |  |  | VRB264H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20 | 282000 | 3.55 | 200000 | 2.4 | R-410A | 21
202918887 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB120H4M-3Y |  |  | VPB288H4M-3Y | Non-Ducted Indoor Units | 276000 | 10.5 | 20.1 | 308000 | 3.49 | 210000 | 2.35 | R-410A | 23
202918888 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB120H4M-3Y |  |  | VPB288H4M-3Y | Ducted Indoor Units | 276000 | 10.1 | 19.4 | 308000 | 3.46 | 210000 | 2.32 | R-410A | 23
202918889 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB120H4M-3Y |  |  | VPB288H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.3 | 19.75 | 308000 | 3.47 | 210000 | 2.33 | R-410A | 23
202918899 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB168H4M-3Y |  |  | VPB336H4M-3Y | Non-Ducted Indoor Units | 320000 | 10.6 | 20.2 | 360000 | 3.34 | 244000 | 2.38 | R-410A | 26.6667
202918900 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB168H4M-3Y |  |  | VPB336H4M-3Y | Ducted Indoor Units | 320000 | 10.4 | 18.7 | 360000 | 3.42 | 244000 | 2.4 | R-410A | 26.6667
202918901 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3Y | VPB168H4M-3Y |  |  | VPB336H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.45 | 360000 | 3.38 | 244000 | 2.39 | R-410A | 26.6667
202897246 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X120DXN1 |  |  | MV6-X288DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.3 | 19.75 | 308000 | 3.47 | 210000 | 2.33 | R-410A | 23
202897174 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X168DXN1 |  |  | MV6-X336DXN1 | Non-Ducted Indoor Units | 320000 | 10.6 | 20.2 | 360000 | 3.34 | 244000 | 2.38 | R-410A | 26.6667
202897175 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X168DXN1 |  |  | MV6-X336DXN1 | Ducted Indoor Units | 320000 | 10.4 | 18.7 | 360000 | 3.42 | 244000 | 2.4 | R-410A | 26.6667
202897254 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X168DXN1 |  |  | MV6-X336DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.45 | 360000 | 3.38 | 244000 | 2.39 | R-410A | 26.6667
202897170 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X120DXN1 |  |  | MV6-X288DXN1 | Non-Ducted Indoor Units | 276000 | 10.5 | 20.1 | 308000 | 3.49 | 210000 | 2.35 | R-410A | 23
202897171 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DXN1 | MV6-X120DXN1 |  |  | MV6-X288DXN1 | Ducted Indoor Units | 276000 | 10.1 | 19.4 | 308000 | 3.46 | 210000 | 2.32 | R-410A | 23
202897212 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X120DZN1 |  |  | MV6-X288DZN1 | Non-Ducted Indoor Units | 276000 | 10.5 | 20.1 | 308000 | 3.49 | 210000 | 2.35 | R-410A | 23
202897213 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X120DZN1 |  |  | MV6-X288DZN1 | Ducted Indoor Units | 276000 | 10.1 | 19.4 | 308000 | 3.46 | 210000 | 2.32 | R-410A | 23
202897255 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X168DZN1 |  |  | MV6-X336DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.45 | 360000 | 3.38 | 244000 | 2.39 | R-410A | 26.6667
202897224 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X168DZN1 |  |  | MV6-X336DZN1 | Non-Ducted Indoor Units | 320000 | 10.6 | 20.2 | 360000 | 3.34 | 244000 | 2.38 | R-410A | 26.6667
202897225 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X168DZN1 |  |  | MV6-X336DZN1 | Ducted Indoor Units | 320000 | 10.4 | 18.7 | 360000 | 3.42 | 244000 | 2.4 | R-410A | 26.6667
202897247 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X168DZN1 | MV6-X120DZN1 |  |  | MV6-X288DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.3 | 19.75 | 308000 | 3.47 | 210000 | 2.33 | R-410A | 23
202918896 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB168H4M-3G |  |  | VPB336H4M-3G | Non-Ducted Indoor Units | 320000 | 10.6 | 20.2 | 360000 | 3.34 | 244000 | 2.38 | R-410A | 26.6667
202918897 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB168H4M-3G |  |  | VPB336H4M-3G | Ducted Indoor Units | 320000 | 10.4 | 18.7 | 360000 | 3.42 | 244000 | 2.4 | R-410A | 26.6667
202918898 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB168H4M-3G |  |  | VPB336H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.45 | 360000 | 3.38 | 244000 | 2.39 | R-410A | 26.6667
202918884 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB120H4M-3G |  |  | VPB288H4M-3G | Non-Ducted Indoor Units | 276000 | 10.5 | 20.1 | 308000 | 3.49 | 210000 | 2.35 | R-410A | 23
202918885 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB120H4M-3G |  |  | VPB288H4M-3G | Ducted Indoor Units | 276000 | 10.1 | 19.4 | 308000 | 3.46 | 210000 | 2.32 | R-410A | 23
202918886 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB168H4M-3G | VPB120H4M-3G |  |  | VPB288H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.3 | 19.75 | 308000 | 3.47 | 210000 | 2.33 | R-410A | 23
202918995 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB120H4M-3Y |  |  | VRB288H4M-3Y | Non-Ducted Indoor Units | 276000 | 10.6 | 19.3 | 308000 | 3.46 | 210000 | 2.33 | R-410A | 23
202918996 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB120H4M-3Y |  |  | VRB288H4M-3Y | Ducted Indoor Units | 276000 | 10.2 | 18.9 | 308000 | 3.42 | 210000 | 2.3 | R-410A | 23
202918997 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB120H4M-3Y |  |  | VRB288H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.4 | 19.1 | 308000 | 3.44 | 210000 | 2.31 | R-410A | 23
202919007 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB168H4M-3Y |  |  | VRB336H4M-3Y | Non-Ducted Indoor Units | 320000 | 10.6 | 19.4 | 360000 | 3.3 | 244000 | 2.3 | R-410A | 26.6667
202919008 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB168H4M-3Y |  |  | VRB336H4M-3Y | Ducted Indoor Units | 320000 | 10.4 | 19.3 | 360000 | 3.39 | 244000 | 2.38 | R-410A | 26.6667
202919009 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3Y | VRB168H4M-3Y |  |  | VRB336H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.35 | 360000 | 3.34 | 244000 | 2.34 | R-410A | 26.6667
202897248 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R120DXN1 |  |  | MV6-R288DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.4 | 19.1 | 308000 | 3.44 | 210000 | 2.31 | R-410A | 23
202897226 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R168DXN1 |  |  | MV6-R336DXN1 | Non-Ducted Indoor Units | 320000 | 10.6 | 19.4 | 360000 | 3.3 | 244000 | 2.3 | R-410A | 26.6667
202897227 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R168DXN1 |  |  | MV6-R336DXN1 | Ducted Indoor Units | 320000 | 10.4 | 19.3 | 360000 | 3.39 | 244000 | 2.38 | R-410A | 26.6667
202897256 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R168DXN1 |  |  | MV6-R336DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.35 | 360000 | 3.34 | 244000 | 2.34 | R-410A | 26.6667
202897214 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R120DXN1 |  |  | MV6-R288DXN1 | Non-Ducted Indoor Units | 276000 | 10.6 | 19.3 | 308000 | 3.46 | 210000 | 2.33 | R-410A | 23
202897215 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DXN1 | MV6-R120DXN1 |  |  | MV6-R288DXN1 | Ducted Indoor Units | 276000 | 10.2 | 18.9 | 308000 | 3.42 | 210000 | 2.3 | R-410A | 23
202897216 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R120DZN1 |  |  | MV6-R288DZN1 | Non-Ducted Indoor Units | 276000 | 10.6 | 19.3 | 308000 | 3.46 | 210000 | 2.33 | R-410A | 23
202897217 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R120DZN1 |  |  | MV6-R288DZN1 | Ducted Indoor Units | 276000 | 10.2 | 18.9 | 308000 | 3.42 | 210000 | 2.3 | R-410A | 23
202897257 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R168DZN1 |  |  | MV6-R336DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.35 | 360000 | 3.34 | 244000 | 2.34 | R-410A | 26.6667
202897228 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R168DZN1 |  |  | MV6-R336DZN1 | Non-Ducted Indoor Units | 320000 | 10.6 | 19.4 | 360000 | 3.3 | 244000 | 2.3 | R-410A | 26.6667
202897229 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R168DZN1 |  |  | MV6-R336DZN1 | Ducted Indoor Units | 320000 | 10.4 | 19.3 | 360000 | 3.39 | 244000 | 2.38 | R-410A | 26.6667
202897249 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R168DZN1 | MV6-R120DZN1 |  |  | MV6-R288DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.4 | 19.1 | 308000 | 3.44 | 210000 | 2.31 | R-410A | 23
202919004 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB168H4M-3G |  |  | VRB336H4M-3G | Non-Ducted Indoor Units | 320000 | 10.6 | 19.4 | 360000 | 3.3 | 244000 | 2.3 | R-410A | 26.6667
202919005 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB168H4M-3G |  |  | VRB336H4M-3G | Ducted Indoor Units | 320000 | 10.4 | 19.3 | 360000 | 3.39 | 244000 | 2.38 | R-410A | 26.6667
202919006 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB168H4M-3G |  |  | VRB336H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.35 | 360000 | 3.34 | 244000 | 2.34 | R-410A | 26.6667
202918992 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB120H4M-3G |  |  | VRB288H4M-3G | Non-Ducted Indoor Units | 276000 | 10.6 | 19.3 | 308000 | 3.46 | 210000 | 2.33 | R-410A | 23
202918993 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB120H4M-3G |  |  | VRB288H4M-3G | Ducted Indoor Units | 276000 | 10.2 | 18.9 | 308000 | 3.42 | 210000 | 2.3 | R-410A | 23
202918994 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB168H4M-3G | VRB120H4M-3G |  |  | VRB288H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.4 | 19.1 | 308000 | 3.44 | 210000 | 2.31 | R-410A | 23
202918906 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3Y | VPB168H4M-3Y |  |  | VPB360H4M-3Y | Ducted Indoor Units | 344000 | 10 | 18.6 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202918907 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3Y | VPB168H4M-3Y |  |  | VPB360H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10 | 18.95 | 380000 | 3.27 | 258000 | 2.32 | R-410A | 28.6667
202918893 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3Y | VPB120H4M-3Y |  |  | VPB312H4M-3Y | Non-Ducted Indoor Units | 298000 | 10.6 | 19 | 334000 | 3.32 | 222000 | 2.26 | R-410A | 24.8333
202918894 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3Y | VPB120H4M-3Y |  |  | VPB312H4M-3Y | Ducted Indoor Units | 298000 | 10.2 | 18.9 | 334000 | 3.33 | 222000 | 2.3 | R-410A | 24.8333
202918895 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3Y | VPB120H4M-3Y |  |  | VPB312H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.4 | 18.95 | 334000 | 3.32 | 222000 | 2.28 | R-410A | 24.8333
202897250 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DXN1 | MV6-X120DXN1 |  |  | MV6-X312DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.4 | 18.95 | 334000 | 3.32 | 222000 | 2.28 | R-410A | 24.8333
202897259 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DXN1 | MV6-X168DXN1 |  |  | MV6-X360DXN1 | Ducted Indoor Units | 344000 | 10 | 18.6 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202897302 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DXN1 | MV6-X168DXN1 |  |  | MV6-X360DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10 | 18.95 | 380000 | 3.27 | 258000 | 2.32 | R-410A | 28.6667
202897172 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DXN1 | MV6-X120DXN1 |  |  | MV6-X312DXN1 | Non-Ducted Indoor Units | 298000 | 10.6 | 19 | 334000 | 3.32 | 222000 | 2.26 | R-410A | 24.8333
202897173 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DXN1 | MV6-X120DXN1 |  |  | MV6-X312DXN1 | Ducted Indoor Units | 298000 | 10.2 | 18.9 | 334000 | 3.33 | 222000 | 2.3 | R-410A | 24.8333
202897218 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DZN1 | MV6-X120DZN1 |  |  | MV6-X312DZN1 | Non-Ducted Indoor Units | 298000 | 10.6 | 19 | 334000 | 3.32 | 222000 | 2.26 | R-410A | 24.8333
202897219 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DZN1 | MV6-X120DZN1 |  |  | MV6-X312DZN1 | Ducted Indoor Units | 298000 | 10.2 | 18.9 | 334000 | 3.33 | 222000 | 2.3 | R-410A | 24.8333
202897303 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DZN1 | MV6-X168DZN1 |  |  | MV6-X360DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10 | 18.95 | 380000 | 3.27 | 258000 | 2.32 | R-410A | 28.6667
202897271 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DZN1 | MV6-X168DZN1 |  |  | MV6-X360DZN1 | Ducted Indoor Units | 344000 | 10 | 18.6 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202897251 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X192DZN1 | MV6-X120DZN1 |  |  | MV6-X312DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.4 | 18.95 | 334000 | 3.32 | 222000 | 2.28 | R-410A | 24.8333
202918903 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3G | VPB168H4M-3G |  |  | VPB360H4M-3G | Ducted Indoor Units | 344000 | 10 | 18.6 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202918904 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3G | VPB168H4M-3G |  |  | VPB360H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10 | 18.95 | 380000 | 3.27 | 258000 | 2.32 | R-410A | 28.6667
202918890 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3G | VPB120H4M-3G |  |  | VPB312H4M-3G | Non-Ducted Indoor Units | 298000 | 10.6 | 19 | 334000 | 3.32 | 222000 | 2.26 | R-410A | 24.8333
202918891 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3G | VPB120H4M-3G |  |  | VPB312H4M-3G | Ducted Indoor Units | 298000 | 10.2 | 18.9 | 334000 | 3.33 | 222000 | 2.3 | R-410A | 24.8333
202918892 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB192H4M-3G | VPB120H4M-3G |  |  | VPB312H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.4 | 18.95 | 334000 | 3.32 | 222000 | 2.28 | R-410A | 24.8333
202919001 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3Y | VRB120H4M-3Y |  |  | VRB312H4M-3Y | Non-Ducted Indoor Units | 298000 | 10.5 | 18.4 | 334000 | 3.25 | 222000 | 2.19 | R-410A | 24.8333
202919002 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3Y | VRB120H4M-3Y |  |  | VRB312H4M-3Y | Ducted Indoor Units | 298000 | 10 | 18.5 | 334000 | 3.3 | 222000 | 2.24 | R-410A | 24.8333
202919003 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3Y | VRB120H4M-3Y |  |  | VRB312H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.25 | 18.45 | 334000 | 3.27 | 222000 | 2.21 | R-410A | 24.8333
202919014 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3Y | VRB168H4M-3Y |  |  | VRB360H4M-3Y | Ducted Indoor Units | 344000 | 9.9 | 18.3 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202919015 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3Y | VRB168H4M-3Y |  |  | VRB360H4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 18.35 | 380000 | 3.27 | 258000 | 2.31 | R-410A | 28.6667
202897252 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DXN1 | MV6-R120DXN1 |  |  | MV6-R312DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.25 | 18.45 | 334000 | 3.27 | 222000 | 2.21 | R-410A | 24.8333
202897273 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DXN1 | MV6-R168DXN1 |  |  | MV6-R360DXN1 | Ducted Indoor Units | 344000 | 9.9 | 18.3 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202897304 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DXN1 | MV6-R168DXN1 |  |  | MV6-R360DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 18.35 | 380000 | 3.27 | 258000 | 2.31 | R-410A | 28.6667
202897220 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DXN1 | MV6-R120DXN1 |  |  | MV6-R312DXN1 | Non-Ducted Indoor Units | 298000 | 10.5 | 18.4 | 334000 | 3.25 | 222000 | 2.19 | R-410A | 24.8333
202897221 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DXN1 | MV6-R120DXN1 |  |  | MV6-R312DXN1 | Ducted Indoor Units | 298000 | 10 | 18.5 | 334000 | 3.3 | 222000 | 2.24 | R-410A | 24.8333
202897222 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DZN1 | MV6-R120DZN1 |  |  | MV6-R312DZN1 | Non-Ducted Indoor Units | 298000 | 10.5 | 18.4 | 334000 | 3.25 | 222000 | 2.19 | R-410A | 24.8333
202897223 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DZN1 | MV6-R120DZN1 |  |  | MV6-R312DZN1 | Ducted Indoor Units | 298000 | 10 | 18.5 | 334000 | 3.3 | 222000 | 2.24 | R-410A | 24.8333
202897305 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DZN1 | MV6-R168DZN1 |  |  | MV6-R360DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 18.35 | 380000 | 3.27 | 258000 | 2.31 | R-410A | 28.6667
202897275 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DZN1 | MV6-R168DZN1 |  |  | MV6-R360DZN1 | Ducted Indoor Units | 344000 | 9.9 | 18.3 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202897253 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R192DZN1 | MV6-R120DZN1 |  |  | MV6-R312DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.25 | 18.45 | 334000 | 3.27 | 222000 | 2.21 | R-410A | 24.8333
202919011 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3G | VRB168H4M-3G |  |  | VRB360H4M-3G | Ducted Indoor Units | 344000 | 9.9 | 18.3 | 380000 | 3.35 | 258000 | 2.33 | R-410A | 28.6667
202919012 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3G | VRB168H4M-3G |  |  | VRB360H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 18.35 | 380000 | 3.27 | 258000 | 2.31 | R-410A | 28.6667
202918998 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3G | VRB120H4M-3G |  |  | VRB312H4M-3G | Non-Ducted Indoor Units | 298000 | 10.5 | 18.4 | 334000 | 3.25 | 222000 | 2.19 | R-410A | 24.8333
202918999 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3G | VRB120H4M-3G |  |  | VRB312H4M-3G | Ducted Indoor Units | 298000 | 10 | 18.5 | 334000 | 3.3 | 222000 | 2.24 | R-410A | 24.8333
202919000 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB192H4M-3G | VRB120H4M-3G |  |  | VRB312H4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.25 | 18.45 | 334000 | 3.27 | 222000 | 2.21 | R-410A | 24.8333
213893584 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P96YNU-A |  | PUHY-P264YSNU-A | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893585 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P96YNU-A |  | PUHY-P264YSNU-A | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893592 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P120YNU-A |  | PUHY-P288YSNU-A | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893593 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P120YNU-A |  | PUHY-P288YSNU-A | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893600 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P312YSNU-A | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213916640 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P96YNU-A |  | PUHY-P264YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916641 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P96YNU-A | PUHY-P120YNU-A |  | PUHY-P288YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916642 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P312YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213916643 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P336YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213893608 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P336YSNU-A | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893609 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P336YSNU-A | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213893614 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P360YSNU-A | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893618 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A | PUHY-P120YNU-A | PUHY-P144YNU-A |  | PUHY-P384YSNU-A | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893622 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A | PUHY-P144YNU-A | PUHY-P144YNU-A |  | PUHY-P408YSNU-A | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213916644 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P360YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213893626 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A | PUHY-P144YNU-A | PUHY-P144YNU-A |  | PUHY-P432YSNU-A | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213893580 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P96TNU-A |  | PUHY-P264TSNU-A | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893581 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P96TNU-A |  | PUHY-P264TSNU-A | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893588 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P120TNU-A |  | PUHY-P288TSNU-A | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893589 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P120TNU-A |  | PUHY-P288TSNU-A | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893596 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P312TSNU-A | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213916601 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P96TNU-A |  | PUHY-P264TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916602 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P96TNU-A | PUHY-P120TNU-A |  | PUHY-P288TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916603 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P312TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213916604 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P336TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213893604 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P336TSNU-A | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893605 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P336TSNU-A | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213893620 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A | PUHY-P144TNU-A | PUHY-P144TNU-A |  | PUHY-P408TSNU-A | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893616 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A | PUHY-P120TNU-A | PUHY-P144TNU-A |  | PUHY-P384TSNU-A | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893612 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P360TSNU-A | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213916605 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P360TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213893624 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A | PUHY-P144TNU-A | PUHY-P144TNU-A |  | PUHY-P432TSNU-A | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213893478 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  | PUHY-EP264YSNU-A | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893479 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  | PUHY-EP264YSNU-A | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893486 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP120YNU-A |  | PUHY-EP288YSNU-A | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893487 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP120YNU-A |  | PUHY-EP288YSNU-A | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893494 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP312YSNU-A | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893495 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP312YSNU-A | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213916619 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP96YNU-A |  | PUHY-EP264YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916620 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP96YNU-A | PUHY-EP120YNU-A |  | PUHY-EP288YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916621 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP312YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213916622 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP336YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213893502 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP336YSNU-A | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893503 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP336YSNU-A | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213893510 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP360YSNU-A | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893511 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP360YSNU-A | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893516 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A | PUHY-EP120YNU-A | PUHY-EP144YNU-A |  | PUHY-EP384YSNU-A | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893520 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A | PUHY-EP144YNU-A | PUHY-EP144YNU-A |  | PUHY-EP408YSNU-A | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213916623 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP360YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213893838 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A | PUHY-EP144YNU-A | PUHY-EP144YNU-A |  | PUHY-EP432YSNU-A | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213916580 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  | PUHY-EP264TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916581 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP120TNU-A |  | PUHY-EP288TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916582 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP312TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213893474 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  | PUHY-EP264TSNU-A | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893475 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP96TNU-A |  | PUHY-EP264TSNU-A | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893490 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP312TSNU-A | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893491 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP312TSNU-A | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893482 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP120TNU-A |  | PUHY-EP288TSNU-A | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893483 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP72TNU-A | PUHY-EP96TNU-A | PUHY-EP120TNU-A |  | PUHY-EP288TSNU-A | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893498 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP336TSNU-A | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893499 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP336TSNU-A | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213916583 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP96TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP336TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213916584 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP360TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213893506 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP360TSNU-A | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893507 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP360TSNU-A | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893518 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A | PUHY-EP144TNU-A | PUHY-EP144TNU-A |  | PUHY-EP408TSNU-A | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893514 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP120TNU-A | PUHY-EP120TNU-A | PUHY-EP144TNU-A |  | PUHY-EP384TSNU-A | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893836 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A | PUHY-EP144TNU-A | PUHY-EP144TNU-A |  | PUHY-EP432TSNU-A | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213893716 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP0964AN40AN |  | TUHYP2644BN40AN | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893717 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP0964AN40AN |  | TUHYP2644BN40AN | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893720 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP1204AN40AN |  | TUHYP2884BN40AN | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893721 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP1204AN40AN |  | TUHYP2884BN40AN | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213893724 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3124BN40AN | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213916827 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP1204AN40AN |  | TUHYP2884BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916831 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3124BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213916823 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0724AN40AN | TUHYP0964AN40AN | TUHYP0964AN40AN |  | TUHYP2644BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916835 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3364BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213893728 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3364BN40AN | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893729 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0964AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3364BN40AN | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213893731 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3604BN40AN | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893733 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN40AN | TUHYP1204AN40AN | TUHYP1444AN40AN |  | TUHYP3844BN40AN | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213893735 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN40AN | TUHYP1444AN40AN | TUHYP1444AN40AN |  | TUHYP4084BN40AN | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213916839 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1204AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3604BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213893737 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN40AN | TUHYP1444AN40AN | TUHYP1444AN40AN |  | TUHYP4324BN40AN | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213893714 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP0963AN40AN |  | TUHYP2643BN40AN | Ducted Indoor Units | 252000 | 10.5 | 20.2 | 282000 | 3.66 | 186000 | 2.33 | R-410A | 21
213893715 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP0963AN40AN |  | TUHYP2643BN40AN | Non-Ducted Indoor Units | 252000 | 10.6 | 22.5 | 282000 | 3.84 | 186000 | 2.55 | R-410A | 21
213893722 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3123BN40AN | Ducted Indoor Units | 298000 | 9.9 | 18.2 | 334000 | 3.5 | 216000 | 2.22 | R-410A | 24.8333
213893718 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP1203AN40AN |  | TUHYP2883BN40AN | Ducted Indoor Units | 276000 | 10.2 | 19 | 308000 | 3.58 | 200000 | 2.27 | R-410A | 23
213893719 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP1203AN40AN |  | TUHYP2883BN40AN | Non-Ducted Indoor Units | 276000 | 10.1 | 20.8 | 308000 | 3.78 | 200000 | 2.49 | R-410A | 23
213916821 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP0963AN40AN |  | TUHYP2643BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.55 | 21.35 | 282000 | 3.75 | 186000 | 2.44 | R-410A | 21
213916829 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3123BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.7 | 19.05 | 334000 | 3.56 | 216000 | 2.3 | R-410A | 24.8333
213916825 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0723AN40AN | TUHYP0963AN40AN | TUHYP1203AN40AN |  | TUHYP2883BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.15 | 19.9 | 308000 | 3.68 | 200000 | 2.38 | R-410A | 23
213916833 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3363BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.8 | 19.2 | 360000 | 3.53 | 234000 | 2.27 | R-410A | 26.6667
213893726 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3363BN40AN | Ducted Indoor Units | 320000 | 10 | 18.1 | 360000 | 3.5 | 234000 | 2.25 | R-410A | 26.6667
213893727 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP0963AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3363BN40AN | Non-Ducted Indoor Units | 320000 | 9.6 | 20.3 | 360000 | 3.57 | 234000 | 2.3 | R-410A | 26.6667
213893730 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3603BN40AN | Ducted Indoor Units | 344000 | 9.8 | 17.3 | 386000 | 3.42 | 248000 | 2.2 | R-410A | 28.6667
213893734 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN40AN | TUHYP1443AN40AN | TUHYP1443AN40AN |  | TUHYP4083BN40AN | Ducted Indoor Units | 390000 | 9.7 | 17.2 | 430000 | 3.35 | 278000 | 2.13 | R-410A | 32.5
213893732 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN40AN | TUHYP1203AN40AN | TUHYP1443AN40AN |  | TUHYP3843BN40AN | Ducted Indoor Units | 364000 | 9.7 | 17.2 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 30.3333
213916837 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1203AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3603BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.46 | 248000 | 2.22 | R-410A | 28.6667
213893736 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN40AN | TUHYP1443AN40AN | TUHYP1443AN40AN |  | TUHYP4323BN40AN | Ducted Indoor Units | 410000 | 9.7 | 17.2 | 454000 | 3.31 | 292000 | 2.1 | R-410A | 34.1667
213893662 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE1204AN40AN |  | TUHYE2884BN40AN | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893663 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE1204AN40AN |  | TUHYE2884BN40AN | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893666 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3124BN40AN | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893667 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3124BN40AN | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893658 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE0964AN40AN |  | TUHYE2644BN40AN | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893659 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE0964AN40AN |  | TUHYE2644BN40AN | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213916742 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE0964AN40AN |  | TUHYE2644BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213916746 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE0964AN40AN | TUHYE1204AN40AN |  | TUHYE2884BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916750 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0724AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3124BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213916754 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3364BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213893670 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3364BN40AN | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893671 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0964AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3364BN40AN | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213893674 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3604BN40AN | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893675 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3604BN40AN | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893677 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN40AN | TUHYE1204AN40AN | TUHYE1444AN40AN |  | TUHYE3844BN40AN | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893679 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN40AN | TUHYE1444AN40AN | TUHYE1444AN40AN |  | TUHYE4084BN40AN | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213916758 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1204AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3604BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213893841 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN40AN | TUHYE1444AN40AN | TUHYE1444AN40AN |  | TUHYE4324BN40AN | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
213916748 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3123BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 21.05 | 334000 | 3.68 | 266000 | 2.13 | R-410A | 24.8333
213916744 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE1203AN40AN |  | TUHYE2883BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.75 | 22.05 | 308000 | 3.78 | 234000 | 2.13 | R-410A | 23
213916740 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE0963AN40AN |  | TUHYE2643BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.4 | 22.7 | 282000 | 3.83 | 212000 | 2.12 | R-410A | 21
213893656 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE0963AN40AN |  | TUHYE2643BN40AN | Ducted Indoor Units | 252000 | 11.4 | 21.7 | 282000 | 3.72 | 212000 | 2.1 | R-410A | 21
213893657 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE0963AN40AN |  | TUHYE2643BN40AN | Non-Ducted Indoor Units | 252000 | 11.4 | 23.7 | 282000 | 3.94 | 212000 | 2.14 | R-410A | 21
213893664 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3123BN40AN | Ducted Indoor Units | 298000 | 10.4 | 20.5 | 334000 | 3.58 | 266000 | 2.1 | R-410A | 24.8333
213893665 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3123BN40AN | Non-Ducted Indoor Units | 298000 | 9.9 | 21.6 | 334000 | 3.78 | 266000 | 2.16 | R-410A | 24.8333
213893660 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE1203AN40AN |  | TUHYE2883BN40AN | Ducted Indoor Units | 276000 | 10.8 | 21.2 | 308000 | 3.65 | 234000 | 2.1 | R-410A | 23
213893661 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0723AN40AN | TUHYE0963AN40AN | TUHYE1203AN40AN |  | TUHYE2883BN40AN | Non-Ducted Indoor Units | 276000 | 10.7 | 22.9 | 308000 | 3.91 | 234000 | 2.17 | R-410A | 23
213893668 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3363BN40AN | Ducted Indoor Units | 320000 | 10.5 | 21 | 360000 | 3.58 | 280000 | 2.1 | R-410A | 26.6667
213893669 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3363BN40AN | Non-Ducted Indoor Units | 320000 | 10 | 22.4 | 360000 | 3.68 | 280000 | 2.13 | R-410A | 26.6667
213916752 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE0963AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3363BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.25 | 21.7 | 360000 | 3.63 | 280000 | 2.11 | R-410A | 26.6667
213916756 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3603BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.9 | 21.25 | 386000 | 3.58 | 312000 | 2.13 | R-410A | 28.6667
213893676 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN40AN | TUHYE1203AN40AN | TUHYE1443AN40AN |  | TUHYE3843BN40AN | Ducted Indoor Units | 364000 | 9.9 | 19.7 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 30.3333
213893672 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3603BN40AN | Ducted Indoor Units | 344000 | 10.1 | 20.5 | 386000 | 3.51 | 312000 | 2.1 | R-410A | 28.6667
213893673 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3603BN40AN | Non-Ducted Indoor Units | 344000 | 9.7 | 22 | 386000 | 3.65 | 312000 | 2.17 | R-410A | 28.6667
213893678 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1203AN40AN | TUHYE1443AN40AN | TUHYE1443AN40AN |  | TUHYE4083BN40AN | Ducted Indoor Units | 390000 | 9.8 | 19.1 | 430000 | 3.45 | 346000 | 2.17 | R-410A | 32.5
213893840 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN40AN | TUHYE1443AN40AN | TUHYE1443AN40AN |  | TUHYE4323BN40AN | Ducted Indoor Units | 410000 | 9.8 | 18.8 | 454000 | 3.41 | 362000 | 2.21 | R-410A | 34.1667
205818960 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y | VPB072L4M-3Y |  | VPB264L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20.9 | 282000 | 3.87 | 240000 | 2.54 | R-410A | 21
205818964 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y | VPB072L4M-3Y |  | VPB288L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.98 | 308000 | 3.78 | 262000 | 2.52 | R-410A | 23
205818896 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y | VPB072L4M-3Y |  | VPB264L4M-3Y | Non-Ducted Indoor Units | 252000 | 11.25 | 21.48 | 282000 | 3.9 | 240000 | 2.52 | R-410A | 21
205818897 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB072L4M-3Y | VPB072L4M-3Y |  | VPB264L4M-3Y | Ducted Indoor Units | 252000 | 11 | 20.32 | 282000 | 3.84 | 240000 | 2.57 | R-410A | 21
205818904 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y | VPB072L4M-3Y |  | VPB288L4M-3Y | Non-Ducted Indoor Units | 276000 | 11 | 20.68 | 308000 | 3.78 | 262000 | 2.47 | R-410A | 23
205818905 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB096L4M-3Y | VPB072L4M-3Y |  | VPB288L4M-3Y | Ducted Indoor Units | 276000 | 10.65 | 19.29 | 308000 | 3.79 | 262000 | 2.57 | R-410A | 23
205818912 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB072L4M-3Y |  | VPB312L4M-3Y | Non-Ducted Indoor Units | 298000 | 10.95 | 19.79 | 334000 | 3.55 | 284000 | 2.31 | R-410A | 24.8333
205818913 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB072L4M-3Y |  | VPB312L4M-3Y | Ducted Indoor Units | 298000 | 10.5 | 18.79 | 334000 | 3.73 | 284000 | 2.51 | R-410A | 24.8333
205818920 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB096L4M-3Y |  | VPB336L4M-3Y | Non-Ducted Indoor Units | 320000 | 10.6 | 20.12 | 360000 | 3.55 | 306000 | 2.37 | R-410A | 26.6667
205818921 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB096L4M-3Y |  | VPB336L4M-3Y | Ducted Indoor Units | 320000 | 10.45 | 20 | 360000 | 3.72 | 306000 | 2.53 | R-410A | 26.6667
205818968 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB072L4M-3Y |  | VPB312L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 19.29 | 334000 | 3.64 | 284000 | 2.41 | R-410A | 24.8333
205818972 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB096L4M-3Y |  | VPB336L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20.06 | 360000 | 3.63 | 306000 | 2.45 | R-410A | 26.6667
205818976 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB120L4M-3Y |  | VPB360L4M-3Y | Non-Ducted Indoor Units | 344000 | 10.05 | 19.55 | 380000 | 3.48 | 324000 | 2.32 | R-410A | 28.6667
205818977 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB120L4M-3Y |  | VPB360L4M-3Y | Ducted Indoor Units | 344000 | 10.2 | 19.64 | 380000 | 3.73 | 324000 | 2.49 | R-410A | 28.6667
205818978 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3Y | VPB120L4M-3Y | VPB120L4M-3Y |  | VPB360L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.1 | 19.59 | 380000 | 3.6 | 324000 | 2.4 | R-410A | 28.6667
205811986 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X264DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20.9 | 282000 | 3.87 | 240000 | 2.54 | R-410A | 21
205811990 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X288DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.98 | 308000 | 3.78 | 262000 | 2.52 | R-410A | 23
205811922 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X264DXN1C-(A) | Non-Ducted Indoor Units | 252000 | 11.25 | 21.48 | 282000 | 3.9 | 240000 | 2.52 | R-410A | 21
205811923 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X264DXN1C-(A) | Ducted Indoor Units | 252000 | 11 | 20.32 | 282000 | 3.84 | 240000 | 2.57 | R-410A | 21
205811930 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X288DXN1C-(A) | Non-Ducted Indoor Units | 276000 | 11 | 20.68 | 308000 | 3.78 | 262000 | 2.47 | R-410A | 23
205811931 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X288DXN1C-(A) | Ducted Indoor Units | 276000 | 10.65 | 19.29 | 308000 | 3.79 | 262000 | 2.57 | R-410A | 23
205811938 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X312DXN1C-(A) | Non-Ducted Indoor Units | 298000 | 10.95 | 19.79 | 334000 | 3.55 | 284000 | 2.31 | R-410A | 24.8333
205811939 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X312DXN1C-(A) | Ducted Indoor Units | 298000 | 10.5 | 18.79 | 334000 | 3.73 | 284000 | 2.51 | R-410A | 24.8333
205811946 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  | MV6-X336DXN1C-(A) | Non-Ducted Indoor Units | 320000 | 10.6 | 20.12 | 360000 | 3.55 | 306000 | 2.37 | R-410A | 26.6667
205811947 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  | MV6-X336DXN1C-(A) | Ducted Indoor Units | 320000 | 10.45 | 20 | 360000 | 3.72 | 306000 | 2.53 | R-410A | 26.6667
205811994 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X72DXN1C-(A) |  | MV6-X312DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 19.29 | 334000 | 3.64 | 284000 | 2.41 | R-410A | 24.8333
205811998 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X96DXN1C-(A) |  | MV6-X336DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20.06 | 360000 | 3.63 | 306000 | 2.45 | R-410A | 26.6667
205812002 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  | MV6-X360DXN1C-(A) | Non-Ducted Indoor Units | 344000 | 10.05 | 19.55 | 380000 | 3.48 | 324000 | 2.32 | R-410A | 28.6667
205812003 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  | MV6-X360DXN1C-(A) | Ducted Indoor Units | 344000 | 10.2 | 19.64 | 380000 | 3.73 | 324000 | 2.49 | R-410A | 28.6667
205812004 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) | MV6-X120DXN1C-(A) |  | MV6-X360DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.1 | 19.59 | 380000 | 3.6 | 324000 | 2.4 | R-410A | 28.6667
205812005 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  | MV6-X360DZN1C-(A) | Non-Ducted Indoor Units | 344000 | 10.05 | 19.55 | 380000 | 3.48 | 324000 | 2.32 | R-410A | 28.6667
205812006 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  | MV6-X360DZN1C-(A) | Ducted Indoor Units | 344000 | 10.2 | 19.64 | 380000 | 3.73 | 324000 | 2.49 | R-410A | 28.6667
205812007 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) |  | MV6-X360DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.1 | 19.59 | 380000 | 3.6 | 324000 | 2.4 | R-410A | 28.6667
205811999 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  | MV6-X336DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20.06 | 360000 | 3.63 | 306000 | 2.45 | R-410A | 26.6667
205811995 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X312DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 19.29 | 334000 | 3.64 | 284000 | 2.41 | R-410A | 24.8333
205811948 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  | MV6-X336DZN1C-(A) | Non-Ducted Indoor Units | 320000 | 10.6 | 20.12 | 360000 | 3.55 | 306000 | 2.37 | R-410A | 26.6667
205811949 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) |  | MV6-X336DZN1C-(A) | Ducted Indoor Units | 320000 | 10.45 | 20 | 360000 | 3.72 | 306000 | 2.53 | R-410A | 26.6667
205811940 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X312DZN1C-(A) | Non-Ducted Indoor Units | 298000 | 10.95 | 19.79 | 334000 | 3.55 | 284000 | 2.31 | R-410A | 24.8333
205811941 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X312DZN1C-(A) | Ducted Indoor Units | 298000 | 10.5 | 18.79 | 334000 | 3.73 | 284000 | 2.51 | R-410A | 24.8333
205811932 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X288DZN1C-(A) | Non-Ducted Indoor Units | 276000 | 11 | 20.68 | 308000 | 3.78 | 262000 | 2.47 | R-410A | 23
205811933 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X288DZN1C-(A) | Ducted Indoor Units | 276000 | 10.65 | 19.29 | 308000 | 3.79 | 262000 | 2.57 | R-410A | 23
205811924 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X264DZN1C-(A) | Non-Ducted Indoor Units | 252000 | 11.25 | 21.48 | 282000 | 3.9 | 240000 | 2.52 | R-410A | 21
205811925 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X264DZN1C-(A) | Ducted Indoor Units | 252000 | 11 | 20.32 | 282000 | 3.84 | 240000 | 2.57 | R-410A | 21
205811991 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X96DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X288DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.98 | 308000 | 3.78 | 262000 | 2.52 | R-410A | 23
205811987 | 1/1/2027 | MIDEA | HMSV-A-CB | MV6-X120DZN1C-(A) | MV6-X72DZN1C-(A) | MV6-X72DZN1C-(A) |  | MV6-X264DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20.9 | 282000 | 3.87 | 240000 | 2.54 | R-410A | 21
205818979 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB120L4M-3G |  | VPB360L4M-3G | Non-Ducted Indoor Units | 344000 | 10.05 | 19.55 | 380000 | 3.48 | 324000 | 2.32 | R-410A | 28.6667
205818980 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB120L4M-3G |  | VPB360L4M-3G | Ducted Indoor Units | 344000 | 10.2 | 19.64 | 380000 | 3.73 | 324000 | 2.49 | R-410A | 28.6667
205818981 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB120L4M-3G |  | VPB360L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.1 | 19.59 | 380000 | 3.6 | 324000 | 2.4 | R-410A | 28.6667
205818973 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB096L4M-3G |  | VPB336L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20.06 | 360000 | 3.63 | 306000 | 2.45 | R-410A | 26.6667
205818969 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB072L4M-3G |  | VPB312L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 19.29 | 334000 | 3.64 | 284000 | 2.41 | R-410A | 24.8333
205818922 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB096L4M-3G |  | VPB336L4M-3G | Non-Ducted Indoor Units | 320000 | 10.6 | 20.12 | 360000 | 3.55 | 306000 | 2.37 | R-410A | 26.6667
205818923 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB096L4M-3G |  | VPB336L4M-3G | Ducted Indoor Units | 320000 | 10.45 | 20 | 360000 | 3.72 | 306000 | 2.53 | R-410A | 26.6667
205818914 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB072L4M-3G |  | VPB312L4M-3G | Non-Ducted Indoor Units | 298000 | 10.95 | 19.79 | 334000 | 3.55 | 284000 | 2.31 | R-410A | 24.8333
205818915 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB120L4M-3G | VPB072L4M-3G |  | VPB312L4M-3G | Ducted Indoor Units | 298000 | 10.5 | 18.79 | 334000 | 3.73 | 284000 | 2.51 | R-410A | 24.8333
205818906 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G | VPB072L4M-3G |  | VPB288L4M-3G | Non-Ducted Indoor Units | 276000 | 11 | 20.68 | 308000 | 3.78 | 262000 | 2.47 | R-410A | 23
205818907 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G | VPB072L4M-3G |  | VPB288L4M-3G | Ducted Indoor Units | 276000 | 10.65 | 19.29 | 308000 | 3.79 | 262000 | 2.57 | R-410A | 23
205818898 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G | VPB072L4M-3G |  | VPB264L4M-3G | Non-Ducted Indoor Units | 252000 | 11.25 | 21.48 | 282000 | 3.9 | 240000 | 2.52 | R-410A | 21
205818899 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G | VPB072L4M-3G |  | VPB264L4M-3G | Ducted Indoor Units | 252000 | 11 | 20.32 | 282000 | 3.84 | 240000 | 2.57 | R-410A | 21
205818965 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB096L4M-3G | VPB072L4M-3G |  | VPB288L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.98 | 308000 | 3.78 | 262000 | 2.52 | R-410A | 23
205818961 | 1/1/2027 | LENNOX | HMSV-A-CB | VPB120L4M-3G | VPB072L4M-3G | VPB072L4M-3G |  | VPB264L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.1 | 20.9 | 282000 | 3.87 | 240000 | 2.54 | R-410A | 21
205818962 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y | VRB072L4M-3Y |  | VRB264L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.15 | 19.79 | 282000 | 3.79 | 240000 | 2.5 | R-410A | 21
205818966 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y | VRB072L4M-3Y |  | VRB288L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.28 | 308000 | 3.71 | 262000 | 2.47 | R-410A | 23
205818900 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y | VRB072L4M-3Y |  | VRB264L4M-3Y | Non-Ducted Indoor Units | 252000 | 11.2 | 20.56 | 282000 | 3.81 | 240000 | 2.48 | R-410A | 21
205818901 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB072L4M-3Y | VRB072L4M-3Y |  | VRB264L4M-3Y | Ducted Indoor Units | 252000 | 11.15 | 19.02 | 282000 | 3.77 | 240000 | 2.52 | R-410A | 21
205818908 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y | VRB072L4M-3Y |  | VRB288L4M-3Y | Non-Ducted Indoor Units | 276000 | 11.05 | 19.88 | 308000 | 3.7 | 262000 | 2.42 | R-410A | 23
205818909 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB096L4M-3Y | VRB072L4M-3Y |  | VRB288L4M-3Y | Ducted Indoor Units | 276000 | 10.6 | 18.69 | 308000 | 3.72 | 262000 | 2.53 | R-410A | 23
205818916 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB072L4M-3Y |  | VRB312L4M-3Y | Non-Ducted Indoor Units | 298000 | 10.7 | 19.25 | 334000 | 3.59 | 284000 | 2.3 | R-410A | 24.8333
205818917 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB072L4M-3Y |  | VRB312L4M-3Y | Ducted Indoor Units | 298000 | 10.4 | 17.97 | 334000 | 3.66 | 284000 | 2.46 | R-410A | 24.8333
205818924 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB096L4M-3Y |  | VRB336L4M-3Y | Non-Ducted Indoor Units | 320000 | 10.65 | 19.85 | 360000 | 3.48 | 306000 | 2.33 | R-410A | 26.6667
205818925 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB096L4M-3Y |  | VRB336L4M-3Y | Ducted Indoor Units | 320000 | 10.5 | 19.82 | 360000 | 3.65 | 306000 | 2.47 | R-410A | 26.6667
205818970 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB072L4M-3Y |  | VRB312L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 18.61 | 334000 | 3.62 | 284000 | 2.38 | R-410A | 24.8333
205818974 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB096L4M-3Y |  | VRB336L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 19.83 | 360000 | 3.56 | 306000 | 2.4 | R-410A | 26.6667
205818982 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB120L4M-3Y |  | VRB360L4M-3Y | Non-Ducted Indoor Units | 344000 | 10.2 | 18.93 | 380000 | 3.4 | 324000 | 2.23 | R-410A | 28.6667
205818983 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB120L4M-3Y |  | VRB360L4M-3Y | Ducted Indoor Units | 344000 | 10.15 | 18.76 | 380000 | 3.7 | 324000 | 2.38 | R-410A | 28.6667
205818984 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3Y | VRB120L4M-3Y | VRB120L4M-3Y |  | VRB360L4M-3Y | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 18.84 | 380000 | 3.55 | 324000 | 2.3 | R-410A | 28.6667
205811988 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R264DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.15 | 19.79 | 282000 | 3.79 | 240000 | 2.5 | R-410A | 21
205811992 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R288DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.28 | 308000 | 3.71 | 262000 | 2.47 | R-410A | 23
205811926 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R264DXN1C-(A) | Non-Ducted Indoor Units | 252000 | 11.2 | 20.56 | 282000 | 3.81 | 240000 | 2.48 | R-410A | 21
205811927 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R264DXN1C-(A) | Ducted Indoor Units | 252000 | 11.15 | 19.02 | 282000 | 3.77 | 240000 | 2.52 | R-410A | 21
205811934 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R288DXN1C-(A) | Non-Ducted Indoor Units | 276000 | 11.05 | 19.88 | 308000 | 3.7 | 262000 | 2.42 | R-410A | 23
205811935 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R288DXN1C-(A) | Ducted Indoor Units | 276000 | 10.6 | 18.69 | 308000 | 3.72 | 262000 | 2.53 | R-410A | 23
205811942 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R312DXN1C-(A) | Non-Ducted Indoor Units | 298000 | 10.7 | 19.25 | 334000 | 3.59 | 284000 | 2.3 | R-410A | 24.8333
205811943 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R312DXN1C-(A) | Ducted Indoor Units | 298000 | 10.4 | 17.97 | 334000 | 3.66 | 284000 | 2.46 | R-410A | 24.8333
205811950 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  | MV6-R336DXN1C-(A) | Non-Ducted Indoor Units | 320000 | 10.65 | 19.85 | 360000 | 3.48 | 306000 | 2.33 | R-410A | 26.6667
205811951 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  | MV6-R336DXN1C-(A) | Ducted Indoor Units | 320000 | 10.5 | 19.82 | 360000 | 3.65 | 306000 | 2.47 | R-410A | 26.6667
205811996 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R72DXN1C-(A) |  | MV6-R312DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 18.61 | 334000 | 3.62 | 284000 | 2.38 | R-410A | 24.8333
205812000 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R96DXN1C-(A) |  | MV6-R336DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 19.83 | 360000 | 3.56 | 306000 | 2.4 | R-410A | 26.6667
205812008 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  | MV6-R360DXN1C-(A) | Non-Ducted Indoor Units | 344000 | 10.2 | 18.93 | 380000 | 3.4 | 324000 | 2.23 | R-410A | 28.6667
205812009 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  | MV6-R360DXN1C-(A) | Ducted Indoor Units | 344000 | 10.15 | 18.76 | 380000 | 3.7 | 324000 | 2.38 | R-410A | 28.6667
205812010 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) | MV6-R120DXN1C-(A) |  | MV6-R360DXN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 18.84 | 380000 | 3.55 | 324000 | 2.3 | R-410A | 28.6667
205812011 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  | MV6-R360DZN1C-(A) | Non-Ducted Indoor Units | 344000 | 10.2 | 18.93 | 380000 | 3.4 | 324000 | 2.23 | R-410A | 28.6667
205812012 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  | MV6-R360DZN1C-(A) | Ducted Indoor Units | 344000 | 10.15 | 18.76 | 380000 | 3.7 | 324000 | 2.38 | R-410A | 28.6667
205812013 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) |  | MV6-R360DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 18.84 | 380000 | 3.55 | 324000 | 2.3 | R-410A | 28.6667
205812001 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  | MV6-R336DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 19.83 | 360000 | 3.56 | 306000 | 2.4 | R-410A | 26.6667
205811997 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R312DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 18.61 | 334000 | 3.62 | 284000 | 2.38 | R-410A | 24.8333
205811952 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  | MV6-R336DZN1C-(A) | Non-Ducted Indoor Units | 320000 | 10.65 | 19.85 | 360000 | 3.48 | 306000 | 2.33 | R-410A | 26.6667
205811953 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) |  | MV6-R336DZN1C-(A) | Ducted Indoor Units | 320000 | 10.5 | 19.82 | 360000 | 3.65 | 306000 | 2.47 | R-410A | 26.6667
205811944 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R312DZN1C-(A) | Non-Ducted Indoor Units | 298000 | 10.7 | 19.25 | 334000 | 3.59 | 284000 | 2.3 | R-410A | 24.8333
205811945 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R312DZN1C-(A) | Ducted Indoor Units | 298000 | 10.4 | 17.97 | 334000 | 3.66 | 284000 | 2.46 | R-410A | 24.8333
205811936 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R288DZN1C-(A) | Non-Ducted Indoor Units | 276000 | 11.05 | 19.88 | 308000 | 3.7 | 262000 | 2.42 | R-410A | 23
205811937 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R288DZN1C-(A) | Ducted Indoor Units | 276000 | 10.6 | 18.69 | 308000 | 3.72 | 262000 | 2.53 | R-410A | 23
205811928 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R264DZN1C-(A) | Non-Ducted Indoor Units | 252000 | 11.2 | 20.56 | 282000 | 3.81 | 240000 | 2.48 | R-410A | 21
205811929 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R264DZN1C-(A) | Ducted Indoor Units | 252000 | 11.15 | 19.02 | 282000 | 3.77 | 240000 | 2.52 | R-410A | 21
205811993 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R96DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R288DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.28 | 308000 | 3.71 | 262000 | 2.47 | R-410A | 23
205811989 | 1/1/2027 | MIDEA | HMSR-A-CB | MV6-R120DZN1C-(A) | MV6-R72DZN1C-(A) | MV6-R72DZN1C-(A) |  | MV6-R264DZN1C-(A) | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.15 | 19.79 | 282000 | 3.79 | 240000 | 2.5 | R-410A | 21
205818985 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB120L4M-3G |  | VRB360L4M-3G | Non-Ducted Indoor Units | 344000 | 10.2 | 18.93 | 380000 | 3.4 | 324000 | 2.23 | R-410A | 28.6667
205818986 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB120L4M-3G |  | VRB360L4M-3G | Ducted Indoor Units | 344000 | 10.15 | 18.76 | 380000 | 3.7 | 324000 | 2.38 | R-410A | 28.6667
205818987 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB120L4M-3G |  | VRB360L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.15 | 18.84 | 380000 | 3.55 | 324000 | 2.3 | R-410A | 28.6667
205818975 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB096L4M-3G |  | VRB336L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.55 | 19.83 | 360000 | 3.56 | 306000 | 2.4 | R-410A | 26.6667
205818971 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB072L4M-3G |  | VRB312L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 18.61 | 334000 | 3.62 | 284000 | 2.38 | R-410A | 24.8333
205818926 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB096L4M-3G |  | VRB336L4M-3G | Non-Ducted Indoor Units | 320000 | 10.65 | 19.85 | 360000 | 3.48 | 306000 | 2.33 | R-410A | 26.6667
205818927 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB096L4M-3G |  | VRB336L4M-3G | Ducted Indoor Units | 320000 | 10.5 | 19.82 | 360000 | 3.65 | 306000 | 2.47 | R-410A | 26.6667
205818918 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB072L4M-3G |  | VRB312L4M-3G | Non-Ducted Indoor Units | 298000 | 10.7 | 19.25 | 334000 | 3.59 | 284000 | 2.3 | R-410A | 24.8333
205818919 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB120L4M-3G | VRB072L4M-3G |  | VRB312L4M-3G | Ducted Indoor Units | 298000 | 10.4 | 17.97 | 334000 | 3.66 | 284000 | 2.46 | R-410A | 24.8333
205818910 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G | VRB072L4M-3G |  | VRB288L4M-3G | Non-Ducted Indoor Units | 276000 | 11.05 | 19.88 | 308000 | 3.7 | 262000 | 2.42 | R-410A | 23
205818911 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G | VRB072L4M-3G |  | VRB288L4M-3G | Ducted Indoor Units | 276000 | 10.6 | 18.69 | 308000 | 3.72 | 262000 | 2.53 | R-410A | 23
205818902 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G | VRB072L4M-3G |  | VRB264L4M-3G | Non-Ducted Indoor Units | 252000 | 11.2 | 20.56 | 282000 | 3.81 | 240000 | 2.48 | R-410A | 21
205818903 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G | VRB072L4M-3G |  | VRB264L4M-3G | Ducted Indoor Units | 252000 | 11.15 | 19.02 | 282000 | 3.77 | 240000 | 2.52 | R-410A | 21
205818967 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB096L4M-3G | VRB072L4M-3G |  | VRB288L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.8 | 19.28 | 308000 | 3.71 | 262000 | 2.47 | R-410A | 23
205818963 | 1/1/2027 | LENNOX | HMSR-A-CB | VRB120L4M-3G | VRB072L4M-3G | VRB072L4M-3G |  | VRB264L4M-3G | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.15 | 19.79 | 282000 | 3.79 | 240000 | 2.5 | R-410A | 21
213896325 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P264ZSKMU-A | Ducted Indoor Units | 252000 | 11.3 | 19 | 280000 | 3.47 | 200000 | 2.52 | R-410A | 21
213896327 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P288ZSKMU-A | Ducted Indoor Units | 276000 | 11.1 | 18.1 | 308000 | 3.49 | 216000 | 2.53 | R-410A | 23
213896329 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P312ZSKMU-A | Ducted Indoor Units | 298000 | 11 | 17.3 | 334000 | 3.46 | 236000 | 2.43 | R-410A | 24.8333
213896359 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P264ZSKMU-A | Non-Ducted Indoor Units | 252000 | 10.8 | 18.2 | 280000 | 3.62 | 200000 | 2.16 | R-410A | 21
213896365 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P288ZSKMU-A | Non-Ducted Indoor Units | 276000 | 10.6 | 18.9 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 23
213896366 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P312ZSKMU-A | Non-Ducted Indoor Units | 298000 | 10 | 17.5 | 334000 | 3.59 | 236000 | 2.22 | R-410A | 24.8333
213916472 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P264ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.05 | 18.6 | 280000 | 3.54 | 200000 | 2.34 | R-410A | 21
213916473 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P288ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.85 | 18.5 | 308000 | 3.54 | 216000 | 2.37 | R-410A | 23
213916474 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P72ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P312ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.5 | 17.4 | 334000 | 3.52 | 236000 | 2.32 | R-410A | 24.8333
213916475 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P336ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 17.65 | 360000 | 3.42 | 268000 | 2.25 | R-410A | 26.6667
213896360 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P336ZSKMU-A | Non-Ducted Indoor Units | 320000 | 10.1 | 17.9 | 360000 | 3.42 | 268000 | 2.13 | R-410A | 26.6667
213896331 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P96ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P336ZSKMU-A | Ducted Indoor Units | 320000 | 10.9 | 17.4 | 360000 | 3.42 | 268000 | 2.38 | R-410A | 26.6667
213896333 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P360ZSKMU-A | Ducted Indoor Units | 344000 | 10.8 | 16.8 | 386000 | 3.32 | 284000 | 2.32 | R-410A | 28.6667
213916476 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P360ZSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.45 | 17.1 | 386000 | 3.36 | 284000 | 2.18 | R-410A | 28.6667
8175957 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  | PUHY-P264YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 13 | 22.55 | 280000 | 3.67 | 200000 | 2.27 | R-410A | 21
8175958 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  | PUHY-P288YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 12.75 | 22.2 | 308000 | 3.58 | 216000 | 2.3 | R-410A | 22.8333
8175959 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  | PUHY-P312YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 12.7 | 21.85 | 334000 | 3.55 | 236000 | 2.26 | R-410A | 24.6667
8175960 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  | PUHY-P336YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 12.5 | 21.85 | 360000 | 3.47 | 268000 | 2.19 | R-410A | 26.6667
8175961 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P120YLMU-A |  | PUHY-P360YSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 12.45 | 21.4 | 386000 | 3.46 | 284000 | 2.12 | R-410A | 28.5
8175972 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  | PUHY-P264TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 13 | 22.55 | 280000 | 3.67 | 200000 | 2.27 | R-410A | 21
8175973 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  | PUHY-P288TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 12.75 | 22.2 | 308000 | 3.58 | 216000 | 2.3 | R-410A | 22.8333
8175974 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  | PUHY-P312TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 12.7 | 21.85 | 334000 | 3.55 | 236000 | 2.26 | R-410A | 24.6667
8175975 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  | PUHY-P336TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 12.5 | 21.85 | 360000 | 3.47 | 268000 | 2.19 | R-410A | 26.6667
8175976 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P120TLMU-A |  | PUHY-P360TSLMU-A | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 12.45 | 21.4 | 386000 | 3.46 | 284000 | 2.12 | R-410A | 28.5
9122299 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 | MV5-H96DXN1 |  | MV5-H336DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 10.65 | 19.1 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
9302773 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 10.65 | 19.1 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
10091389 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DXN1 |  |  |  | MV5-2R264DXN1 | Non-Ducted Indoor Units | 248000 | 10.7 | 22 | 282000 | 3.52 | 186000 | 2.42 | R-410A | 20.6667
10091390 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DXN1 |  |  |  | MV5-2R264DXN1 | Ducted Indoor Units | 248000 | 10.4 | 21 | 282000 | 3.49 | 186000 | 2.3 | R-410A | 20.6667
10091391 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R288DXN1 |  |  |  | MV5-2R288DXN1 | Non-Ducted Indoor Units | 274000 | 10.4 | 21 | 298000 | 3.38 | 198000 | 2.2 | R-410A | 22.8333
10091392 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R288DXN1 |  |  |  | MV5-2R288DXN1 | Ducted Indoor Units | 274000 | 9.8 | 20.5 | 298000 | 3.42 | 198000 | 2.26 | R-410A | 22.8333
9363503 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 10.65 | 19.1 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
200084131 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.7 | 22 | 282000 | 3.52 | 186000 | 2.42 | R-410A | 20.6667
200084132 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Non-Ducted Indoor Units | 248000 | 10.7 | 22 | 282000 | 3.52 | 186000 | 2.42 | R-410A | 20.6667
200084133 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Ducted Indoor Units | 248000 | 10.4 | 21 | 282000 | 3.49 | 186000 | 2.3 | R-410A | 20.6667
200084134 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Ducted Indoor Units | 248000 | 10.4 | 21 | 282000 | 3.49 | 186000 | 2.3 | R-410A | 20.6667
200084137 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA288RDS5-1 |  |  |  | 38VMA288RDS5-1 | Non-Ducted Indoor Units | 274000 | 10.4 | 21 | 298000 | 3.38 | 198000 | 2.2 | R-410A | 22.8333
200084138 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA288RDS5-1 |  |  |  | 38VMA288RDS5-1 | Non-Ducted Indoor Units | 274000 | 10.4 | 21 | 298000 | 3.38 | 198000 | 2.2 | R-410A | 22.8333
200084139 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA288RDS5-1 |  |  |  | 38VMA288RDS5-1 | Ducted Indoor Units | 274000 | 9.8 | 20.5 | 298000 | 3.42 | 198000 | 2.26 | R-410A | 22.8333
200084140 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA288RDS5-1 |  |  |  | 38VMA288RDS5-1 | Ducted Indoor Units | 274000 | 9.8 | 20.5 | 298000 | 3.42 | 198000 | 2.26 | R-410A | 22.8333
208102065 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.2 | 19.25 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
208685685 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-144FFFH |  |  | AVWT-264FFFH | Ducted Indoor Units | 252000 | 10.5 | 19.5 | 276000 | 3.28 | 186000 | 2.3 | R-410A | 21
208685686 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-144FFFH |  |  | AVWT-264FFFH | Non-Ducted Indoor Units | 252000 | 11.5 | 20.9 | 276000 | 3.59 | 186000 | 2.41 | R-410A | 21
208685687 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-144FFFH |  |  | AVWT-264FFFH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.2 | 276000 | 3.43 | 186000 | 2.35 | R-410A | 21
208685689 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-144FFFH |  |  | AVWT-288FFFH | Non-Ducted Indoor Units | 276000 | 10.8 | 20.5 | 300000 | 3.33 | 210000 | 2.29 | R-410A | 23
208685690 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-144FFFH |  |  | AVWT-288FFFH | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 19.8 | 300000 | 3.28 | 210000 | 2.25 | R-410A | 23
208685692 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-168FFFH |  |  | AVWT-312FFFH | Non-Ducted Indoor Units | 298000 | 10.7 | 19.8 | 320000 | 3.26 | 220000 | 2.22 | R-410A | 24.8333
208685704 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-144FFFH | AVWT-144FFFH |  | AVWT-408FFFH | Non-Ducted Indoor Units | 388000 | 11 | 18.1 | 426000 | 3.4 | 290000 | 2.36 | R-410A | 32.3333
208685705 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFH | AVWT-144FFFH | AVWT-144FFFH |  | AVWT-408FFFH | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 10.7 | 17.85 | 426000 | 3.3 | 290000 | 2.32 | R-410A | 32.3333
208685707 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-144FFFH | AVWT-144FFFH |  | AVWT-432FFFH | Non-Ducted Indoor Units | 414000 | 10.8 | 18.3 | 450000 | 3.33 | 314000 | 2.29 | R-410A | 34.5
208685708 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-144FFFH | AVWT-144FFFH |  | AVWT-432FFFH | Mixed Ducted and Non-Ducted Indoor Units | 414000 | 10.5 | 17.95 | 450000 | 3.27 | 314000 | 2.26 | R-410A | 34.5
208685710 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FFFH | AVWT-144FFFH | AVWT-168FFFH |  | AVWT-456FFFH | Non-Ducted Indoor Units | 436000 | 10.7 | 17.6 | 470000 | 3.29 | 324000 | 2.24 | R-410A | 36.3333
208758288 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-144URB |  |  | CHV6-264URB | Ducted Indoor Units | 252000 | 10.5 | 19.5 | 276000 | 3.28 | 186000 | 2.3 | R-410A | 21
208758289 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-144URB |  |  | CHV6-264URB | Non-Ducted Indoor Units | 252000 | 11.5 | 20.9 | 276000 | 3.59 | 186000 | 2.41 | R-410A | 21
208758290 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-144URB |  |  | CHV6-264URB | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.2 | 276000 | 3.43 | 186000 | 2.35 | R-410A | 21
208758292 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-144URB |  |  | CHV6-288URB | Non-Ducted Indoor Units | 276000 | 10.8 | 20.5 | 300000 | 3.33 | 210000 | 2.29 | R-410A | 23
208758293 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-144URB |  |  | CHV6-288URB | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 19.8 | 300000 | 3.28 | 210000 | 2.25 | R-410A | 23
208758295 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-168URB |  |  | CHV6-312URB | Non-Ducted Indoor Units | 298000 | 10.7 | 19.8 | 320000 | 3.26 | 220000 | 2.22 | R-410A | 24.8333
208758307 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-144URB | CHV6-144URB |  | CHV6-408URB | Non-Ducted Indoor Units | 388000 | 11 | 18.1 | 426000 | 3.4 | 290000 | 2.36 | R-410A | 32.3333
208758308 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-120URB | CHV6-144URB | CHV6-144URB |  | CHV6-408URB | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 10.7 | 17.85 | 426000 | 3.3 | 290000 | 2.32 | R-410A | 32.3333
208758310 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-144URB | CHV6-144URB |  | CHV6-432URB | Non-Ducted Indoor Units | 414000 | 10.8 | 18.3 | 450000 | 3.33 | 314000 | 2.29 | R-410A | 34.5
208758311 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-144URB | CHV6-144URB |  | CHV6-432URB | Mixed Ducted and Non-Ducted Indoor Units | 414000 | 10.5 | 17.95 | 450000 | 3.27 | 314000 | 2.26 | R-410A | 34.5
208758313 | 1/1/2027 | Cooper & Hunter | HMSR-A-CB | CHV6-144URB | CHV6-144URB | CHV6-168URB |  | CHV6-456URB | Non-Ducted Indoor Units | 436000 | 10.7 | 17.6 | 470000 | 3.29 | 324000 | 2.24 | R-410A | 36.3333
209842194 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM312BXVTFR | Ducted Indoor Units | 296000 | 11.15 | 22.6 | 334000 | 3.51 | 334000 | 2.11 | R-410A | 24.6667
209842195 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM336BXVTFR | Ducted Indoor Units | 320000 | 10.95 | 22.3 | 360000 | 3.38 | 360000 | 2.09 | R-410A | 26.6667
209842204 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM312BXVTFR | Non-Ducted Indoor Units | 296000 | 12.4 | 29.9 | 334000 | 3.61 | 334000 | 2.12 | R-410A | 24.6667
209842205 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM336BXVTFR | Non-Ducted Indoor Units | 320000 | 12.2 | 29.6 | 360000 | 3.53 | 360000 | 2.07 | R-410A | 26.6667
209842412 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM312BXVTFH | Ducted Indoor Units | 296000 | 11.15 | 22.6 | 334000 | 3.51 | 334000 | 2.11 | R-410A | 24.6667
209842413 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM336BXVTFH | Ducted Indoor Units | 320000 | 10.95 | 22.3 | 360000 | 3.38 | 360000 | 2.09 | R-410A | 26.6667
209842422 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM312BXVTFH | Non-Ducted Indoor Units | 296000 | 12.4 | 29.9 | 334000 | 3.61 | 334000 | 2.12 | R-410A | 24.6667
209842423 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM336BXVTFH | Non-Ducted Indoor Units | 320000 | 12.2 | 29.6 | 360000 | 3.53 | 360000 | 2.07 | R-410A | 26.6667
209842432 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM312BXVTJH | Ducted Indoor Units | 296000 | 11.15 | 22.6 | 334000 | 3.51 | 334000 | 2.11 | R-410A | 24.6667
209842433 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM336BXVTJH | Ducted Indoor Units | 320000 | 10.95 | 22.3 | 360000 | 3.38 | 360000 | 2.09 | R-410A | 26.6667
209842442 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM312BXVTJH | Non-Ducted Indoor Units | 296000 | 12.4 | 29.9 | 334000 | 3.61 | 334000 | 2.12 | R-410A | 24.6667
209842443 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM336BXVTJH | Non-Ducted Indoor Units | 320000 | 12.2 | 29.6 | 360000 | 3.53 | 360000 | 2.07 | R-410A | 26.6667
209842452 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM312BXVTJR | Ducted Indoor Units | 296000 | 11.15 | 22.6 | 334000 | 3.51 | 334000 | 2.11 | R-410A | 24.6667
209842453 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM336BXVTJR | Ducted Indoor Units | 320000 | 10.95 | 22.3 | 360000 | 3.38 | 360000 | 2.09 | R-410A | 26.6667
209842462 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM312BXVTJR | Non-Ducted Indoor Units | 296000 | 12.4 | 29.9 | 334000 | 3.61 | 334000 | 2.12 | R-410A | 24.6667
209842463 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM336BXVTJR | Non-Ducted Indoor Units | 320000 | 12.2 | 29.6 | 360000 | 3.53 | 360000 | 2.07 | R-410A | 26.6667
209863178 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM312BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.77 | 26.25 | 334000 | 3.56 | 334000 | 2.11 | R-410A | 24.6667
209863179 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTFR | AM120BXVTFR | AM120BXVTFR |  | AM336BXVTFR | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.57 | 25.95 | 360000 | 3.45 | 360000 | 2.08 | R-410A | 26.6667
209863188 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM312BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.77 | 26.25 | 334000 | 3.56 | 334000 | 2.11 | R-410A | 24.6667
209863189 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTFH | AM120BXVTFH | AM120BXVTFH |  | AM336BXVTFH | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.57 | 25.95 | 360000 | 3.45 | 360000 | 2.08 | R-410A | 26.6667
209863198 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM312BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.77 | 26.25 | 334000 | 3.56 | 334000 | 2.11 | R-410A | 24.6667
209863199 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096BXVTJH | AM120BXVTJH | AM120BXVTJH |  | AM336BXVTJH | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.57 | 25.95 | 360000 | 3.45 | 360000 | 2.08 | R-410A | 26.6667
209863208 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM312BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.77 | 26.25 | 334000 | 3.56 | 334000 | 2.11 | R-410A | 24.6667
209863209 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096BXVTJR | AM120BXVTJR | AM120BXVTJR |  | AM336BXVTJR | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.57 | 25.95 | 360000 | 3.45 | 360000 | 2.08 | R-410A | 26.6667
207826251 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR | AM216BXVGFR |  |  | AM432BXVGFR | Ducted Indoor Units | 412000 | 9.6 | 20 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
207826256 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR | AM216BXVGFR |  |  | AM432BXVGFR | Non-Ducted Indoor Units | 412000 | 9.6 | 21 | 462000 | 3.3 | 300000 | 2.45 | R-410A | 34.3333
207826725 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGFH | AM216BXVGFH |  |  | AM432BXVGFH | Ducted Indoor Units | 412000 | 9.6 | 20 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
207826729 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGFH | AM216BXVGFH |  |  | AM432BXVGFH | Non-Ducted Indoor Units | 412000 | 9.6 | 21 | 462000 | 3.3 | 300000 | 2.45 | R-410A | 34.3333
207826733 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGJH | AM216BXVGJH |  |  | AM432BXVGJH | Ducted Indoor Units | 412000 | 9.6 | 20 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
207826737 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGJH | AM216BXVGJH |  |  | AM432BXVGJH | Non-Ducted Indoor Units | 412000 | 9.6 | 21 | 462000 | 3.3 | 300000 | 2.45 | R-410A | 34.3333
207826741 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGJR | AM216BXVGJR |  |  | AM432BXVGJR | Ducted Indoor Units | 412000 | 9.6 | 20 | 462000 | 3.25 | 300000 | 2.35 | R-410A | 34.3333
207826745 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGJR | AM216BXVGJR |  |  | AM432BXVGJR | Non-Ducted Indoor Units | 412000 | 9.6 | 21 | 462000 | 3.3 | 300000 | 2.45 | R-410A | 34.3333
207827277 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGFR |  |  |  | AM432BXVGFR | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.6 | 20.5 | 462000 | 3.27 | 300000 | 2.4 | R-410A | 34.3333
207827292 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGFH |  |  |  | AM432BXVGFH | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.6 | 20.5 | 462000 | 3.27 | 300000 | 2.4 | R-410A | 34.3333
207827296 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216BXVGJH |  |  |  | AM432BXVGJH | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.6 | 20.5 | 462000 | 3.27 | 300000 | 2.4 | R-410A | 34.3333
207827300 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216BXVGJR |  |  |  | AM432BXVGJR | Mixed Ducted and Non-Ducted Indoor Units | 412000 | 9.6 | 20.5 | 462000 | 3.27 | 300000 | 2.4 | R-410A | 34.3333
206453552 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 12 | 21.75 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
206453553 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM121BTE5 |  |  | ARUM336BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.3 | 20.5 | 358000 | 3.38 | 234000 | 2.3 | R-410A | 26.6667
206453554 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.75 | 21.5 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
206453555 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11 | 21.5 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
206453556 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM144BTE5 |  |  | ARUM360BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.5 | 19.75 | 384000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
206453557 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM168BTE5 |  |  | ARUM384BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 19.15 | 410000 | 3.31 | 266000 | 2.24 | R-410A | 30.5
206453558 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM192BTE5 |  |  | ARUM408BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.75 | 18.9 | 434000 | 3.28 | 284000 | 2.22 | R-410A | 32.5
206453559 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM121BTE5 | ARUM121BTE5 |  | ARUM432BTE5 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.15 | 19.9 | 460000 | 3.25 | 298000 | 2.24 | R-410A | 34.1667
206453560 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 12 | 21.75 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
206453561 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.75 | 21.5 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
206453562 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11 | 21.5 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
206453563 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM121DTE5 |  |  | ARUM336DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.3 | 20.5 | 358000 | 3.38 | 234000 | 2.3 | R-410A | 26.6667
206453564 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM144DTE5 |  |  | ARUM360DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.5 | 19.75 | 384000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
206453565 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM168DTE5 |  |  | ARUM384DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 19.15 | 410000 | 3.31 | 266000 | 2.24 | R-410A | 30.5
206453566 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM192DTE5 |  |  | ARUM408DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.75 | 18.9 | 434000 | 3.28 | 284000 | 2.22 | R-410A | 32.5
206453567 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM121DTE5 | ARUM121DTE5 |  | ARUM432DTE5 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.15 | 19.9 | 460000 | 3.25 | 298000 | 2.24 | R-410A | 34.1667
208102045 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.32 | 186000 | 2.2 | R-410A | 20.8333
208102046 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
208102048 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y | VEP096C432Y | VEP096C432Y |  | VEP264C432Y | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
208102050 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.35 | 20.25 | 308000 | 3.27 | 200000 | 2.2 | R-410A | 22.8333
208102051 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
208102055 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.35 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
208102053 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP096C432Y |  | VEP288C432Y | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
210691242 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-144FHFSHA |  |  | AVWT-264FHFSHA | Ducted Indoor Units | 252000 | 10.5 | 19.5 | 276000 | 3.28 | 186000 | 2.3 | R-410A | 21
210691243 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-144FHFSHA |  |  | AVWT-264FHFSHA | Non-Ducted Indoor Units | 252000 | 11.5 | 20.9 | 276000 | 3.59 | 186000 | 2.41 | R-410A | 21
210691244 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-144FHFSHA |  |  | AVWT-264FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.2 | 276000 | 3.43 | 186000 | 2.35 | R-410A | 21
210691246 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-144FHFSHA |  |  | AVWT-288FHFSHA | Non-Ducted Indoor Units | 276000 | 10.8 | 20.5 | 300000 | 3.33 | 210000 | 2.29 | R-410A | 23
210691247 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-144FHFSHA |  |  | AVWT-288FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 19.8 | 300000 | 3.28 | 210000 | 2.25 | R-410A | 23
210691249 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-168FHFSHA |  |  | AVWT-312FHFSHA | Non-Ducted Indoor Units | 298000 | 10.7 | 19.8 | 320000 | 3.26 | 220000 | 2.22 | R-410A | 24.8333
210691261 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-144FHFSHA | AVWT-144FHFSHA |  | AVWT-408FHFSHA | Non-Ducted Indoor Units | 388000 | 11 | 18.1 | 426000 | 3.4 | 290000 | 2.36 | R-410A | 32.3333
210691262 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHA | AVWT-144FHFSHA | AVWT-144FHFSHA |  | AVWT-408FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 10.7 | 17.85 | 426000 | 3.3 | 290000 | 2.32 | R-410A | 32.3333
210691264 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-144FHFSHA | AVWT-144FHFSHA |  | AVWT-432FHFSHA | Non-Ducted Indoor Units | 414000 | 10.8 | 18.3 | 450000 | 3.33 | 314000 | 2.29 | R-410A | 34.5
210691265 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-144FHFSHA | AVWT-144FHFSHA |  | AVWT-432FHFSHA | Mixed Ducted and Non-Ducted Indoor Units | 414000 | 10.5 | 17.95 | 450000 | 3.27 | 314000 | 2.26 | R-410A | 34.5
210691267 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FHFSHA | AVWT-144FHFSHA | AVWT-168FHFSHA |  | AVWT-456FHFSHA | Non-Ducted Indoor Units | 436000 | 10.7 | 17.6 | 470000 | 3.29 | 324000 | 2.24 | R-410A | 36.3333
212511013 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
212511014 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
212511015 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Ducted Indoor Units | 276000 | 11.3 | 20 | 308000 | 3.81 | 216000 | 2.88 | R-410A | 23
212511016 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
212511017 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Ducted Indoor Units | 276000 | 11.2 | 19.6 | 308000 | 3.76 | 216000 | 2.8 | R-410A | 23
212511018 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
212511019 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Ducted Indoor Units | 298000 | 10.8 | 19.7 | 334000 | 3.66 | 236000 | 2.72 | R-410A | 24.8333
212511020 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
212511021 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Ducted Indoor Units | 320000 | 10.4 | 19.6 | 360000 | 3.49 | 268000 | 2.57 | R-410A | 26.6667
212511022 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 384000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
212511023 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Ducted Indoor Units | 342000 | 11.8 | 20.3 | 384000 | 3.66 | 284000 | 2.72 | R-410A | 28.5
212511032 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Ducted Indoor Units | 252000 | 12 | 20.4 | 282000 | 3.9 | 200000 | 2.88 | R-410A | 21
212511033 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
212511034 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Ducted Indoor Units | 366000 | 11 | 19.8 | 410000 | 3.55 | 294000 | 2.63 | R-410A | 30.5
212511035 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
212511036 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Ducted Indoor Units | 410000 | 10.2 | 19.1 | 460000 | 3.32 | 328000 | 2.52 | R-410A | 34.1667
212511050 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
212511051 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
212511052 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Ducted Indoor Units | 276000 | 11.3 | 20 | 308000 | 3.81 | 216000 | 2.88 | R-410A | 23
212511053 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
212511054 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Ducted Indoor Units | 276000 | 11.2 | 19.6 | 308000 | 3.76 | 216000 | 2.8 | R-410A | 23
212511055 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
212511056 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Ducted Indoor Units | 298000 | 10.8 | 19.7 | 334000 | 3.66 | 236000 | 2.72 | R-410A | 24.8333
212511057 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
212511058 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Ducted Indoor Units | 320000 | 10.4 | 19.6 | 360000 | 3.49 | 268000 | 2.57 | R-410A | 26.6667
212511059 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 384000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
212511060 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Ducted Indoor Units | 342000 | 11.8 | 20.3 | 384000 | 3.66 | 284000 | 2.72 | R-410A | 28.5
212511070 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Ducted Indoor Units | 252000 | 12 | 20.4 | 282000 | 3.9 | 200000 | 2.88 | R-410A | 21
212511111 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Non-Ducted Indoor Units | 252000 | 10.9 | 23.1 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
212511112 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Ducted Indoor Units | 252000 | 10.9 | 20.5 | 282000 | 3.46 | 200000 | 2.37 | R-410A | 21
212511113 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Non-Ducted Indoor Units | 252000 | 10.9 | 23.1 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
212511114 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Ducted Indoor Units | 252000 | 10.9 | 20.5 | 282000 | 3.46 | 200000 | 2.37 | R-410A | 21
212511115 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.8 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
212511116 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Ducted Indoor Units | 276000 | 11 | 20.2 | 308000 | 3.46 | 216000 | 2.37 | R-410A | 23
212511117 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.8 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
212511118 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Ducted Indoor Units | 276000 | 11 | 20.2 | 308000 | 3.46 | 216000 | 2.37 | R-410A | 23
212511119 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Non-Ducted Indoor Units | 276000 | 10.3 | 22.4 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
212511120 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Ducted Indoor Units | 276000 | 9.8 | 19.7 | 308000 | 3.37 | 216000 | 2.32 | R-410A | 23
212511121 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Non-Ducted Indoor Units | 276000 | 10.3 | 22.4 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
212511122 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Ducted Indoor Units | 276000 | 9.8 | 19.7 | 308000 | 3.37 | 216000 | 2.32 | R-410A | 23
212511123 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Non-Ducted Indoor Units | 298000 | 10.3 | 22.1 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
212511124 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Ducted Indoor Units | 298000 | 10 | 19.7 | 334000 | 3.29 | 236000 | 2.33 | R-410A | 24.8333
212511125 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Non-Ducted Indoor Units | 298000 | 10.3 | 22.1 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
212511126 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Ducted Indoor Units | 298000 | 10 | 19.7 | 334000 | 3.29 | 236000 | 2.33 | R-410A | 24.8333
212511127 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.7 | 23.9 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
212511128 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Ducted Indoor Units | 320000 | 10.2 | 20.7 | 360000 | 3.32 | 268000 | 2.38 | R-410A | 26.6667
212511129 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.7 | 23.9 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
212511130 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Ducted Indoor Units | 320000 | 10.2 | 20.7 | 360000 | 3.32 | 268000 | 2.38 | R-410A | 26.6667
212511131 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1686FT6P-UL |  |  | MMY-AP336S6FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.1 | 21.9 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
212511133 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1686FT9P-UL |  |  | MMY-AP336S6FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.1 | 21.9 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
212511135 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Non-Ducted Indoor Units | 342000 | 9.7 | 23.3 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
212511137 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Non-Ducted Indoor Units | 342000 | 9.7 | 23.3 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
212511139 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
212511140 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Ducted Indoor Units | 366000 | 11 | 19.8 | 410000 | 3.55 | 294000 | 2.63 | R-410A | 30.5
212511145 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
212511146 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Ducted Indoor Units | 410000 | 10.2 | 19.1 | 460000 | 3.32 | 328000 | 2.52 | R-410A | 34.1667
212511151 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 436000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
212511152 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Ducted Indoor Units | 390000 | 11 | 19.6 | 436000 | 3.37 | 310000 | 2.57 | R-410A | 32.5
212511153 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 436000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
212511154 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Ducted Indoor Units | 390000 | 11 | 19.6 | 436000 | 3.37 | 310000 | 2.57 | R-410A | 32.5
212511155 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 436000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
212511156 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Ducted Indoor Units | 390000 | 10.6 | 19.3 | 436000 | 3.32 | 310000 | 2.55 | R-410A | 32.5
212511157 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 436000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
212511158 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Ducted Indoor Units | 390000 | 10.6 | 19.3 | 436000 | 3.32 | 310000 | 2.55 | R-410A | 32.5
212511164 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4566HT6P-UL | Ducted Indoor Units | 430000 | 9.9 | 19.3 | 488000 | 3.26 | 350000 | 2.5 | R-410A | 35.8333
212511166 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4566HT9P-UL | Ducted Indoor Units | 430000 | 9.9 | 19.3 | 488000 | 3.26 | 350000 | 2.5 | R-410A | 35.8333
212512485 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.7 | 21.6 | 282000 | 3.77 | 200000 | 2.77 | R-410A | 21
212512486 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 21.8 | 282000 | 3.43 | 200000 | 2.41 | R-410A | 21
212512487 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 21.8 | 282000 | 3.43 | 200000 | 2.41 | R-410A | 21
212512488 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.2 | 21.25 | 308000 | 3.7 | 216000 | 2.76 | R-410A | 23
212512489 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.2 | 21.25 | 308000 | 3.7 | 216000 | 2.76 | R-410A | 23
212512490 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 20.9 | 308000 | 3.63 | 216000 | 2.69 | R-410A | 23
212512491 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 20.9 | 308000 | 3.63 | 216000 | 2.69 | R-410A | 23
212512492 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 21.5 | 308000 | 3.45 | 216000 | 2.43 | R-410A | 23
212512493 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 21.5 | 308000 | 3.45 | 216000 | 2.43 | R-410A | 23
212512494 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.05 | 21.05 | 308000 | 3.36 | 216000 | 2.33 | R-410A | 23
212512495 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.05 | 21.05 | 308000 | 3.36 | 216000 | 2.33 | R-410A | 23
212512496 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.54 | 236000 | 2.66 | R-410A | 24.8333
212512497 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.54 | 236000 | 2.66 | R-410A | 24.8333
212512498 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 20.9 | 334000 | 3.29 | 236000 | 2.36 | R-410A | 24.8333
212512499 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 20.9 | 334000 | 3.29 | 236000 | 2.36 | R-410A | 24.8333
212512500 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.35 | 20.8 | 360000 | 3.42 | 268000 | 2.51 | R-410A | 26.6667
212512501 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.35 | 20.8 | 360000 | 3.42 | 268000 | 2.51 | R-410A | 26.6667
212512502 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 22.3 | 360000 | 3.36 | 268000 | 2.39 | R-410A | 26.6667
212512503 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 22.3 | 360000 | 3.36 | 268000 | 2.39 | R-410A | 26.6667
212512506 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.7 | 21.35 | 384000 | 3.59 | 284000 | 2.65 | R-410A | 28.5
212512507 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.7 | 21.35 | 384000 | 3.59 | 284000 | 2.65 | R-410A | 28.5
212512508 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.6 | 21.75 | 386000 | 3.33 | 284000 | 2.31 | R-410A | 28.5
212512509 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.6 | 21.75 | 386000 | 3.33 | 284000 | 2.31 | R-410A | 28.5
212512510 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.8 | 20.8 | 410000 | 3.47 | 294000 | 2.59 | R-410A | 30.5
212512511 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3846FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 21.25 | 412000 | 3.25 | 294000 | 2.26 | R-410A | 30.5
212512512 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3846FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 21.25 | 412000 | 3.25 | 294000 | 2.26 | R-410A | 30.5
212512513 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.7 | 20.5 | 436000 | 3.37 | 310000 | 2.53 | R-410A | 32.5
212512514 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.4 | 20.15 | 436000 | 3.31 | 310000 | 2.51 | R-410A | 32.5
212512517 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.1 | 20.2 | 460000 | 3.3 | 328000 | 2.5 | R-410A | 34.1667
212512531 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.7 | 21.6 | 282000 | 3.77 | 200000 | 2.77 | R-410A | 21
212512532 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.8 | 20.8 | 410000 | 3.47 | 294000 | 2.59 | R-410A | 30.5
212512533 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.7 | 20.5 | 436000 | 3.37 | 310000 | 2.53 | R-410A | 32.5
212512534 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.4 | 20.15 | 436000 | 3.31 | 310000 | 2.51 | R-410A | 32.5
212512535 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.1 | 20.2 | 460000 | 3.3 | 328000 | 2.5 | R-410A | 34.1667
212928536 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB | AVWT-120FFFSHB |  |  | AVWT-240FFFSHB | Ducted Indoor Units | 240000 | 11.4 | 18.7 | 258000 | 3.5 | 162000 | 2.36 | R-410A | 20
212928537 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB | AVWT-120FFFSHB |  |  | AVWT-240FFFSHB | Non-Ducted Indoor Units | 240000 | 11.8 | 19 | 258000 | 3.8 | 162000 | 2.38 | R-410A | 20
212928541 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB | AVWT-120FHFSHB |  |  | AVWT-240FHFSHB | Ducted Indoor Units | 240000 | 11.4 | 18.7 | 258000 | 3.5 | 162000 | 2.36 | R-410A | 20
212928542 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB | AVWT-120FHFSHB |  |  | AVWT-240FHFSHB | Non-Ducted Indoor Units | 240000 | 11.8 | 19 | 258000 | 3.8 | 162000 | 2.38 | R-410A | 20
212928545 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FFFSHB | AVWT-120FFFSHB |  |  | AVWT-240FFFSHB | Mixed Ducted and Non-Ducted Indoor Units | 240000 | 11.6 | 18.85 | 258000 | 3.65 | 162000 | 2.37 | R-410A | 20
212928548 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FHFSHB | AVWT-120FHFSHB |  |  | AVWT-240FHFSHB | Mixed Ducted and Non-Ducted Indoor Units | 240000 | 11.6 | 18.85 | 258000 | 3.65 | 162000 | 2.37 | R-410A | 20
213686159 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-144FLFSH |  |  | AVWT-264FLFSH | Ducted Indoor Units | 252000 | 10.5 | 19.5 | 276000 | 3.28 | 186000 | 2.3 | R-410A | 21
213686160 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-144FLFSH |  |  | AVWT-264FLFSH | Non-Ducted Indoor Units | 252000 | 11.5 | 20.9 | 276000 | 3.59 | 186000 | 2.41 | R-410A | 21
213686161 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-144FLFSH |  |  | AVWT-264FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.2 | 276000 | 3.43 | 186000 | 2.35 | R-410A | 21
213686163 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-144FLFSH |  |  | AVWT-288FLFSH | Non-Ducted Indoor Units | 276000 | 10.8 | 20.5 | 300000 | 3.33 | 210000 | 2.29 | R-410A | 23
213686164 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-144FLFSH |  |  | AVWT-288FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.5 | 19.8 | 300000 | 3.28 | 210000 | 2.25 | R-410A | 23
213686166 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-168FLFSH |  |  | AVWT-312FLFSH | Non-Ducted Indoor Units | 298000 | 10.7 | 19.8 | 320000 | 3.26 | 220000 | 2.22 | R-410A | 24.8333
213686178 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-144FLFSH | AVWT-144FLFSH |  | AVWT-408FLFSH | Non-Ducted Indoor Units | 388000 | 11 | 18.1 | 426000 | 3.4 | 290000 | 2.36 | R-410A | 32.3333
213686179 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-120FLFSH | AVWT-144FLFSH | AVWT-144FLFSH |  | AVWT-408FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 388000 | 10.7 | 17.85 | 426000 | 3.3 | 290000 | 2.32 | R-410A | 32.3333
213686181 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-144FLFSH | AVWT-144FLFSH |  | AVWT-432FLFSH | Non-Ducted Indoor Units | 414000 | 10.8 | 18.3 | 450000 | 3.33 | 314000 | 2.29 | R-410A | 34.5
213686182 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-144FLFSH | AVWT-144FLFSH |  | AVWT-432FLFSH | Mixed Ducted and Non-Ducted Indoor Units | 414000 | 10.5 | 17.95 | 450000 | 3.27 | 314000 | 2.26 | R-410A | 34.5
213686184 | 1/1/2027 | HISENSE | HMSR-A-CB | AVWT-144FLFSH | AVWT-144FLFSH | AVWT-168FLFSH |  | AVWT-456FLFSH | Non-Ducted Indoor Units | 436000 | 10.7 | 17.6 | 470000 | 3.29 | 324000 | 2.24 | R-410A | 36.3333
200084141 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA288RDS5-1 |  |  |  | 38VMA288RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.1 | 20.75 | 298000 | 3.4 | 198000 | 2.23 | R-410A | 22.8333
200084142 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA288RDS5-1 |  |  |  | 38VMA288RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.1 | 20.75 | 298000 | 3.4 | 198000 | 2.23 | R-410A | 22.8333
200084135 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.55 | 21.5 | 282000 | 3.5 | 186000 | 2.36 | R-410A | 20.6667
200084136 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS5-1 |  |  |  | 38VMA264RDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.55 | 21.5 | 282000 | 3.5 | 186000 | 2.36 | R-410A | 20.6667
10306455 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV096H3CDC716(A) | IOV096H3CDC716(A) |  | IOV288H3CDC749(A) | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
10267498 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-360WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.2 | 19.25 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
10306453 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) | IOV096H3CDC716(A) | IOV096H3CDC716(A) |  | IOV264H3CDC745(A) | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
201874094 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  | PUHY-P288TSKMU-A | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
201874096 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  | PUHY-P288TSLMU-A | Ducted Indoor Units | 274000 | 12 | 20.4 | 308000 | 3.47 | 216000 | 2.4 | R-410A | 22.8333
201874098 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  | PUHY-P288YSKMU-A | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
201874100 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  | PUHY-P288YSLMU-A | Ducted Indoor Units | 274000 | 12 | 20.4 | 308000 | 3.47 | 216000 | 2.4 | R-410A | 22.8333
201874157 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  | PUHY-P264TSLMU-A | Non-Ducted Indoor Units | 252000 | 13.6 | 24 | 280000 | 3.75 | 200000 | 2.16 | R-410A | 21
201874161 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  | PUHY-P264YSLMU-A | Non-Ducted Indoor Units | 252000 | 13.6 | 24 | 280000 | 3.75 | 200000 | 2.16 | R-410A | 21
201874168 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  | PUHY-P288TSLMU-A | Non-Ducted Indoor Units | 274000 | 13.5 | 24 | 308000 | 3.7 | 216000 | 2.21 | R-410A | 22.8333
201874170 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  | PUHY-P288YSLMU-A | Non-Ducted Indoor Units | 274000 | 13.5 | 24 | 308000 | 3.7 | 216000 | 2.21 | R-410A | 22.8333
201874786 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  | PUHY-P312TSLMU-A | Non-Ducted Indoor Units | 282000 | 13.4 | 22.1 | 316000 | 3.66 | 236000 | 2.22 | R-410A | 23.5
201874787 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  | PUHY-P336TSLMU-A | Non-Ducted Indoor Units | 304000 | 13.2 | 20.9 | 342000 | 3.52 | 268000 | 2.13 | R-410A | 25.3333
201874789 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  | PUHY-P312YSLMU-A | Non-Ducted Indoor Units | 282000 | 13.4 | 22.1 | 316000 | 3.66 | 236000 | 2.22 | R-410A | 23.5
201874790 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  | PUHY-P336YSLMU-A | Non-Ducted Indoor Units | 304000 | 13.2 | 20.9 | 342000 | 3.52 | 268000 | 2.13 | R-410A | 25.3333
201874070 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  | PUHY-P312TSLMU-A | Ducted Indoor Units | 296000 | 12 | 20.3 | 334000 | 3.45 | 236000 | 2.31 | R-410A | 24.6667
201874071 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  | PUHY-P336TSLMU-A | Ducted Indoor Units | 320000 | 11.8 | 20.3 | 360000 | 3.43 | 268000 | 2.26 | R-410A | 26.6667
201874072 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P120TLMU-A |  | PUHY-P360TSLMU-A | Ducted Indoor Units | 342000 | 11.8 | 20.1 | 386000 | 3.41 | 284000 | 2.2 | R-410A | 28.5
201874075 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  | PUHY-P312YSLMU-A | Ducted Indoor Units | 296000 | 12 | 20.3 | 334000 | 3.45 | 236000 | 2.31 | R-410A | 24.6667
201874076 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  | PUHY-P336YSLMU-A | Ducted Indoor Units | 320000 | 11.8 | 20.3 | 360000 | 3.43 | 268000 | 2.26 | R-410A | 26.6667
201874077 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P120YLMU-A |  | PUHY-P360YSLMU-A | Ducted Indoor Units | 342000 | 11.8 | 20.1 | 386000 | 3.41 | 284000 | 2.2 | R-410A | 28.5
201874079 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A | PUHY-P72TKMU-A |  | PUHY-P264TSKMU-A | Ducted Indoor Units | 252000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 21
201874082 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  | PUHY-P264TSLMU-A | Ducted Indoor Units | 252000 | 12.4 | 21.1 | 280000 | 3.6 | 200000 | 2.39 | R-410A | 21
201874086 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  | PUHY-P264YSKMU-A | Ducted Indoor Units | 250000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 20.8333
201874090 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  | PUHY-P264YSLMU-A | Ducted Indoor Units | 252000 | 12.4 | 21.1 | 280000 | 3.6 | 200000 | 2.39 | R-410A | 21
201903117 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
201903119 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.32 | 186000 | 2.2 | R-410A | 20.8333
201903122 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
201903123 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.35 | 20.25 | 308000 | 3.27 | 200000 | 2.2 | R-410A | 22.8333
201903127 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.35 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
201903135 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.2 | 19.25 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
202516769 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
202516770 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Non-Ducted Indoor Units | 252000 | 12.5 | 22 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
202516771 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DTE4 | ARUN144DTE4 |  |  | ARUN264DTE4 | Ducted Indoor Units | 250000 | 11.4 | 21.4 | 280000 | 3.38 | 182000 | 2.38 | R-410A | 20.8333
202516772 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DTE4 | ARUN144DTE4 |  |  | ARUN264DTE4 | Non-Ducted Indoor Units | 250000 | 11.9 | 21.8 | 280000 | 3.6 | 182000 | 2.49 | R-410A | 20.8333
202517448 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN121DTE4 | ARUN144DTE4 |  | ARUN360DTE4 | Ducted Indoor Units | 342000 | 11 | 21.2 | 386000 | 3.3 | 248000 | 2.4 | R-410A | 28.5
202519360 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
202519361 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Non-Ducted Indoor Units | 276000 | 12.2 | 22 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
202519362 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DTE4 | ARUN144DTE4 |  |  | ARUN288DTE4 | Ducted Indoor Units | 274000 | 11.2 | 19.5 | 306000 | 3.31 | 198000 | 2.35 | R-410A | 22.8333
202519363 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DTE4 | ARUN144DTE4 |  |  | ARUN288DTE4 | Non-Ducted Indoor Units | 274000 | 11.9 | 21.4 | 306000 | 3.55 | 198000 | 2.47 | R-410A | 22.8333
202519364 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
202519365 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Non-Ducted Indoor Units | 298000 | 11 | 22 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
202519367 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DTE4 | ARUN168DTE4 |  |  | ARUN313DTE4 | Non-Ducted Indoor Units | 296000 | 11.3 | 22 | 334000 | 3.56 | 222000 | 2.36 | R-410A | 24.6667
202519368 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM121BTE5 |  |  | ARUM336BTE5 | Non-Ducted Indoor Units | 320000 | 9.8 | 20.5 | 358000 | 3.52 | 234000 | 2.36 | R-410A | 26.6667
202519369 | 1/1/2027 | LG | HMSV-A-CB | ARUN168DTE4 | ARUN168DTE4 |  |  | ARUN337DTE4 | Non-Ducted Indoor Units | 320000 | 10.7 | 20.5 | 360000 | 3.52 | 234000 | 2.34 | R-410A | 26.6667
202519371 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM144BTE5 |  |  | ARUM360BTE5 | Non-Ducted Indoor Units | 344000 | 10.8 | 20 | 384000 | 3.51 | 248000 | 2.3 | R-410A | 28.6667
202519372 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN121DTE4 | ARUN144DTE4 |  | ARUN360DTE4 | Non-Ducted Indoor Units | 342000 | 10.5 | 22.8 | 386000 | 3.51 | 248000 | 2.4 | R-410A | 28.5
202519374 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM168BTE5 |  |  | ARUM384BTE5 | Non-Ducted Indoor Units | 366000 | 10 | 19 | 410000 | 3.4 | 266000 | 2.28 | R-410A | 30.5
202519375 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN145DTE4 | ARUN145DTE4 |  | ARUN384DTE4 | Ducted Indoor Units | 366000 | 10.8 | 20.9 | 410000 | 3.4 | 266000 | 2.38 | R-410A | 30.5
202519376 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN145DTE4 | ARUN145DTE4 |  | ARUN384DTE4 | Non-Ducted Indoor Units | 366000 | 9.9 | 21 | 410000 | 3.4 | 266000 | 2.4 | R-410A | 30.5
202519378 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM192BTE5 |  |  | ARUM408BTE5 | Non-Ducted Indoor Units | 390000 | 9.8 | 18.8 | 434000 | 3.34 | 284000 | 2.26 | R-410A | 32.5
202519379 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DTE4 | ARUN145DTE4 | ARUN145DTE4 |  | ARUN408DTE4 | Ducted Indoor Units | 390000 | 10.6 | 20.5 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202519380 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DTE4 | ARUN145DTE4 | ARUN145DTE4 |  | ARUN408DTE4 | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202519382 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM121BTE5 | ARUM121BTE5 |  | ARUM432BTE5 | Non-Ducted Indoor Units | 410000 | 9.8 | 19.8 | 460000 | 3.28 | 298000 | 2.32 | R-410A | 34.1667
202524555 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Non-Ducted Indoor Units | 252000 | 12.5 | 22 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
202524556 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
202524557 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Non-Ducted Indoor Units | 276000 | 12.2 | 22 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
202524558 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
202524559 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Non-Ducted Indoor Units | 298000 | 11 | 22 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
202524560 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
202524561 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM121DTE5 |  |  | ARUM336DTE5 | Non-Ducted Indoor Units | 320000 | 9.8 | 20.5 | 358000 | 3.52 | 234000 | 2.36 | R-410A | 26.6667
202524563 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM144DTE5 |  |  | ARUM360DTE5 | Non-Ducted Indoor Units | 344000 | 10.8 | 20 | 384000 | 3.51 | 248000 | 2.3 | R-410A | 28.6667
202524565 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM168DTE5 |  |  | ARUM384DTE5 | Non-Ducted Indoor Units | 366000 | 10 | 19 | 410000 | 3.4 | 266000 | 2.28 | R-410A | 30.5
202524567 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM192DTE5 |  |  | ARUM408DTE5 | Non-Ducted Indoor Units | 390000 | 9.8 | 18.8 | 434000 | 3.34 | 284000 | 2.26 | R-410A | 32.5
202524569 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM121DTE5 | ARUM121DTE5 |  | ARUM432DTE5 | Non-Ducted Indoor Units | 410000 | 9.8 | 19.8 | 460000 | 3.28 | 298000 | 2.32 | R-410A | 34.1667
202534243 | 1/1/2027 | LG | HMSV-A-CB | ARUN145DTE4 | ARUN145DTE4 | ARUN145DTE4 |  | ARUN432DTE4 | Ducted Indoor Units | 410000 | 10.4 | 19.8 | 460000 | 3.3 | 298000 | 2.25 | R-410A | 34.1667
202534244 | 1/1/2027 | LG | HMSV-A-CB | ARUN145DTE4 | ARUN145DTE4 | ARUN145DTE4 |  | ARUN432DTE4 | Non-Ducted Indoor Units | 410000 | 9.8 | 19.5 | 460000 | 3.3 | 298000 | 2.3 | R-410A | 34.1667
202534284 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DTE4 | ARUB144DTE4 |  |  | ARUB264DTE4 | Non-Ducted Indoor Units | 250000 | 11.9 | 21.8 | 280000 | 3.6 | 182000 | 2.49 | R-410A | 20.8333
202534285 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BTE4 | ARUB144BTE4 |  |  | ARUB264BTE4 | Non-Ducted Indoor Units | 250000 | 11.9 | 21.8 | 280000 | 3.6 | 182000 | 2.49 | R-410A | 20.8333
202534287 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BTE4 | ARUN144BTE4 |  |  | ARUN288BTE4 | Non-Ducted Indoor Units | 274000 | 11.9 | 21.4 | 306000 | 3.55 | 198000 | 2.47 | R-410A | 22.8333
202534288 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BTE4 | ARUB144BTE4 |  |  | ARUB288BTE4 | Non-Ducted Indoor Units | 274000 | 11.9 | 21.4 | 306000 | 3.55 | 198000 | 2.47 | R-410A | 22.8333
202534289 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DTE4 | ARUB144DTE4 |  |  | ARUB288DTE4 | Non-Ducted Indoor Units | 274000 | 11.9 | 21.4 | 306000 | 3.55 | 198000 | 2.47 | R-410A | 22.8333
202534290 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DTE4 | ARUB144DTE4 |  |  | ARUB288DTE4 | Ducted Indoor Units | 274000 | 11.2 | 19.5 | 306000 | 3.31 | 198000 | 2.35 | R-410A | 22.8333
202534291 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BTE4 | ARUB144BTE4 |  |  | ARUB288BTE4 | Ducted Indoor Units | 274000 | 11.2 | 19.5 | 306000 | 3.31 | 198000 | 2.35 | R-410A | 22.8333
202534292 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BTE4 | ARUN144BTE4 |  |  | ARUN288BTE4 | Ducted Indoor Units | 274000 | 11.2 | 19.5 | 306000 | 3.31 | 198000 | 2.35 | R-410A | 22.8333
202534293 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN121BTE4 | ARUN144BTE4 |  | ARUN360BTE4 | Ducted Indoor Units | 342000 | 11 | 21.2 | 386000 | 3.3 | 248000 | 2.4 | R-410A | 28.5
202534294 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 | ARUB121BTE4 | ARUB144BTE4 |  | ARUB360BTE4 | Ducted Indoor Units | 342000 | 11 | 21.2 | 386000 | 3.3 | 248000 | 2.4 | R-410A | 28.5
202534295 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB121DTE4 | ARUB144DTE4 |  | ARUB360DTE4 | Ducted Indoor Units | 342000 | 11 | 21.2 | 386000 | 3.3 | 248000 | 2.4 | R-410A | 28.5
202534296 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB121DTE4 | ARUB144DTE4 |  | ARUB360DTE4 | Non-Ducted Indoor Units | 342000 | 10.5 | 22.8 | 386000 | 3.51 | 248000 | 2.4 | R-410A | 28.5
202534297 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 | ARUB121BTE4 | ARUB144BTE4 |  | ARUB360BTE4 | Non-Ducted Indoor Units | 342000 | 10.5 | 22.8 | 386000 | 3.51 | 248000 | 2.4 | R-410A | 28.5
202534298 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN121BTE4 | ARUN144BTE4 |  | ARUN360BTE4 | Non-Ducted Indoor Units | 342000 | 10.5 | 22.8 | 386000 | 3.51 | 248000 | 2.4 | R-410A | 28.5
202534299 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN145BTE4 | ARUN145BTE4 |  | ARUN384BTE4 | Ducted Indoor Units | 366000 | 10.8 | 20.9 | 410000 | 3.4 | 266000 | 2.38 | R-410A | 30.5
202534300 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN145BTE4 | ARUN145BTE4 |  | ARUN384BTE4 | Non-Ducted Indoor Units | 366000 | 9.9 | 21 | 410000 | 3.4 | 266000 | 2.4 | R-410A | 30.5
202534301 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB145DTE4 | ARUB145DTE4 |  | ARUB384DTE4 | Ducted Indoor Units | 366000 | 10.8 | 20.9 | 410000 | 3.4 | 266000 | 2.38 | R-410A | 30.5
202534302 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB145DTE4 | ARUB145DTE4 |  | ARUB384DTE4 | Non-Ducted Indoor Units | 366000 | 9.9 | 21 | 410000 | 3.4 | 266000 | 2.4 | R-410A | 30.5
202534303 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 | ARUB145BTE4 | ARUB145BTE4 |  | ARUB384BTE4 | Ducted Indoor Units | 366000 | 10.8 | 20.9 | 410000 | 3.4 | 266000 | 2.38 | R-410A | 30.5
202534304 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 | ARUB145BTE4 | ARUB145BTE4 |  | ARUB384BTE4 | Non-Ducted Indoor Units | 366000 | 9.9 | 21 | 410000 | 3.4 | 266000 | 2.4 | R-410A | 30.5
202534305 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BTE4 | ARUN145BTE4 | ARUN145BTE4 |  | ARUN408BTE4 | Ducted Indoor Units | 390000 | 10.6 | 20.5 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202534306 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BTE4 | ARUN145BTE4 | ARUN145BTE4 |  | ARUN408BTE4 | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202534307 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DTE4 | ARUB145DTE4 | ARUB145DTE4 |  | ARUB408DTE4 | Ducted Indoor Units | 390000 | 10.6 | 20.5 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202534308 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DTE4 | ARUB145DTE4 | ARUB145DTE4 |  | ARUB408DTE4 | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202534309 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BTE4 | ARUB145BTE4 | ARUB145BTE4 |  | ARUB408BTE4 | Ducted Indoor Units | 390000 | 10.6 | 20.5 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202534310 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BTE4 | ARUB145BTE4 | ARUB145BTE4 |  | ARUB408BTE4 | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 434000 | 3.35 | 284000 | 2.35 | R-410A | 32.5
202534311 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DTE4 | ARUB168DTE4 |  |  | ARUB313DTE4 | Non-Ducted Indoor Units | 296000 | 11.3 | 22 | 334000 | 3.56 | 222000 | 2.36 | R-410A | 24.6667
202534312 | 1/1/2027 | LG | HMSR-A-CB | ARUB168DTE4 | ARUB168DTE4 |  |  | ARUB337DTE4 | Non-Ducted Indoor Units | 320000 | 10.7 | 20.5 | 360000 | 3.52 | 234000 | 2.34 | R-410A | 26.6667
202534313 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BTE4 | ARUB168BTE4 |  |  | ARUB313BTE4 | Non-Ducted Indoor Units | 296000 | 11.3 | 22 | 334000 | 3.56 | 222000 | 2.36 | R-410A | 24.6667
202534314 | 1/1/2027 | LG | HMSR-A-CB | ARUB168BTE4 | ARUB168BTE4 |  |  | ARUB337BTE4 | Non-Ducted Indoor Units | 320000 | 10.7 | 20.5 | 360000 | 3.52 | 234000 | 2.34 | R-410A | 26.6667
202534315 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BTE4 | ARUN168BTE4 |  |  | ARUN313BTE4 | Non-Ducted Indoor Units | 296000 | 11.3 | 22 | 334000 | 3.56 | 222000 | 2.36 | R-410A | 24.6667
202534316 | 1/1/2027 | LG | HMSV-A-CB | ARUN168BTE4 | ARUN168BTE4 |  |  | ARUN337BTE4 | Non-Ducted Indoor Units | 320000 | 10.7 | 20.5 | 360000 | 3.52 | 234000 | 2.34 | R-410A | 26.6667
202517467 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BTE4 | ARUB144BTE4 |  |  | ARUB264BTE4 | Ducted Indoor Units | 250000 | 11.4 | 21.4 | 280000 | 3.38 | 182000 | 2.38 | R-410A | 20.8333
202517468 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BTE4 | ARUN144BTE4 |  |  | ARUN264BTE4 | Ducted Indoor Units | 250000 | 11.4 | 21.4 | 280000 | 3.38 | 182000 | 2.38 | R-410A | 20.8333
202517490 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DTE4 | ARUB144DTE4 |  |  | ARUB264DTE4 | Ducted Indoor Units | 250000 | 11.4 | 21.4 | 280000 | 3.38 | 182000 | 2.38 | R-410A | 20.8333
202534373 | 1/1/2027 | LG | HMSR-A-CB | ARUB145BTE4 | ARUB145BTE4 | ARUB145BTE4 |  | ARUB432BTE4 | Ducted Indoor Units | 410000 | 10.4 | 19.8 | 460000 | 3.3 | 298000 | 2.25 | R-410A | 34.1667
202534374 | 1/1/2027 | LG | HMSR-A-CB | ARUB145BTE4 | ARUB145BTE4 | ARUB145BTE4 |  | ARUB432BTE4 | Non-Ducted Indoor Units | 410000 | 9.8 | 19.5 | 460000 | 3.3 | 298000 | 2.3 | R-410A | 34.1667
203297525 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TKMU-A | PURY-P120TKMU-A |  |  | PURY-P264TSKMU-A | Ducted Indoor Units | 250000 | 11 | 17.3 | 280000 | 3.38 | 200000 | 2.35 | R-410A | 20.8333
203297529 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YKMU-A | PURY-P120YKMU-A |  |  | PURY-P264YSKMU-A | Ducted Indoor Units | 250000 | 11 | 17.3 | 280000 | 3.38 | 200000 | 2.35 | R-410A | 20.8333
203297535 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TKMU-A | PURY-P144TKMU-A |  |  | PURY-P288TSKMU-A | Ducted Indoor Units | 274000 | 11.2 | 17.2 | 304000 | 3.39 | 216000 | 2.35 | R-410A | 22.8333
203297539 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YKMU-A | PURY-P144YKMU-A |  |  | PURY-P288YSKMU-A | Ducted Indoor Units | 274000 | 11.2 | 17.2 | 304000 | 3.39 | 216000 | 2.35 | R-410A | 22.8333
203334944 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ144XATJ* |  |  | REYQ264XATJ* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.6 | 282000 | 3.62 | 200000 | 2.22 | R-410A | 21
203334945 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* | REYQ144XATJ* |  |  | REYQ288XATJ* | Non-Ducted Indoor Units | 274000 | 11 | 21 | 294000 | 3.51 | 208000 | 2.2 | R-410A | 22.8333
203334946 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* | REYQ168XATJ* |  |  | REYQ312XATJ* | Non-Ducted Indoor Units | 296000 | 10.1 | 20.4 | 320000 | 3.56 | 214000 | 2.09 | R-410A | 24.6667
203334947 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XATJ* | REYQ168XATJ* |  |  | REYQ336XATJ* | Non-Ducted Indoor Units | 320000 | 9.9 | 20 | 338000 | 3.53 | 224000 | 2.12 | R-410A | 26.6667
203334948 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ120XATJ* | REYQ120XATJ* |  | REYQ360XATJ* | Non-Ducted Indoor Units | 342000 | 10.9 | 20 | 376000 | 3.56 | 270000 | 2.25 | R-410A | 28.5
203334961 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ144XAYD* |  |  | REYQ264XAYD* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.6 | 282000 | 3.62 | 200000 | 2.22 | R-410A | 21
203334962 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* | REYQ144XAYD* |  |  | REYQ288XAYD* | Non-Ducted Indoor Units | 274000 | 11 | 21 | 294000 | 3.51 | 208000 | 2.2 | R-410A | 22.8333
203334963 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* | REYQ168XAYD* |  |  | REYQ312XAYD* | Non-Ducted Indoor Units | 296000 | 10.1 | 20.4 | 320000 | 3.56 | 214000 | 2.09 | R-410A | 24.6667
203334964 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYD* | REYQ168XAYD* |  |  | REYQ336XAYD* | Non-Ducted Indoor Units | 320000 | 9.9 | 20 | 338000 | 3.53 | 224000 | 2.12 | R-410A | 26.6667
203334965 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ120XAYD* | REYQ120XAYD* |  | REYQ360XAYD* | Non-Ducted Indoor Units | 342000 | 10.9 | 20 | 376000 | 3.56 | 270000 | 2.25 | R-410A | 28.5
203334978 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ144XAYC* |  |  | REYQ264XAYC* | Non-Ducted Indoor Units | 252000 | 11.2 | 21.6 | 282000 | 3.62 | 200000 | 2.22 | R-410A | 21
203334979 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* | REYQ144XAYC* |  |  | REYQ288XAYC* | Non-Ducted Indoor Units | 274000 | 11 | 21 | 294000 | 3.51 | 208000 | 2.2 | R-410A | 22.8333
203334980 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* | REYQ168XAYC* |  |  | REYQ312XAYC* | Non-Ducted Indoor Units | 296000 | 10.1 | 20.4 | 320000 | 3.56 | 214000 | 2.09 | R-410A | 24.6667
203334981 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYC* | REYQ168XAYC* |  |  | REYQ336XAYC* | Non-Ducted Indoor Units | 320000 | 9.9 | 20 | 338000 | 3.53 | 224000 | 2.12 | R-410A | 26.6667
203334982 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ120XAYC* | REYQ120XAYC* |  | REYQ360XAYC* | Non-Ducted Indoor Units | 342000 | 10.9 | 20 | 376000 | 3.56 | 270000 | 2.25 | R-410A | 28.5
203364252 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ144XATJ* |  |  | REYQ264XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.8 | 282000 | 3.41 | 200000 | 2.14 | R-410A | 21
203364253 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* | REYQ144XATJ* |  |  | REYQ288XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.65 | 19.45 | 294000 | 3.35 | 208000 | 2.13 | R-410A | 22.8333
203364254 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XATJ* | REYQ168XATJ* |  |  | REYQ312XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10 | 19.2 | 320000 | 3.38 | 214000 | 2.07 | R-410A | 24.6667
203364255 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XATJ* | REYQ168XATJ* |  |  | REYQ336XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.7 | 18.65 | 338000 | 3.36 | 224000 | 2.08 | R-410A | 26.6667
203364256 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XATJ* | REYQ120XATJ* | REYQ120XATJ* |  | REYQ360XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.75 | 19.4 | 376000 | 3.38 | 270000 | 2.17 | R-410A | 28.5
203364269 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ144XAYD* |  |  | REYQ264XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.8 | 282000 | 3.41 | 200000 | 2.14 | R-410A | 21
203364270 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* | REYQ144XAYD* |  |  | REYQ288XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.65 | 19.45 | 294000 | 3.35 | 208000 | 2.13 | R-410A | 22.8333
203364271 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYD* | REYQ168XAYD* |  |  | REYQ312XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10 | 19.2 | 320000 | 3.38 | 214000 | 2.07 | R-410A | 24.6667
203364272 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYD* | REYQ168XAYD* |  |  | REYQ336XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.7 | 18.65 | 338000 | 3.36 | 224000 | 2.08 | R-410A | 26.6667
203364273 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYD* | REYQ120XAYD* | REYQ120XAYD* |  | REYQ360XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.75 | 19.4 | 376000 | 3.38 | 270000 | 2.17 | R-410A | 28.5
203364286 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ144XAYC* |  |  | REYQ264XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.8 | 282000 | 3.41 | 200000 | 2.14 | R-410A | 21
203364287 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* | REYQ144XAYC* |  |  | REYQ288XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.65 | 19.45 | 294000 | 3.35 | 208000 | 2.13 | R-410A | 22.8333
203364288 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144XAYC* | REYQ168XAYC* |  |  | REYQ312XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10 | 19.2 | 320000 | 3.38 | 214000 | 2.07 | R-410A | 24.6667
203364289 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168XAYC* | REYQ168XAYC* |  |  | REYQ336XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.7 | 18.65 | 338000 | 3.36 | 224000 | 2.08 | R-410A | 26.6667
203364290 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120XAYC* | REYQ120XAYC* | REYQ120XAYC* |  | REYQ360XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.75 | 19.4 | 376000 | 3.38 | 270000 | 2.17 | R-410A | 28.5
204572228 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM192HXVAFH |  |  | AM264JXVAFH | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
204572229 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH | AM144FXVAFH |  |  | AM288JXVAFH | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
204572243 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM192HXVAJH |  |  | AM264JXVAJH | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
204572244 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM144FXVAJH |  |  | AM288JXVAJH | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
204572258 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM192HXVAFR |  |  | AM264JXVAFR | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
204572259 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR | AM144FXVAFR |  |  | AM288JXVAFR | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
204572273 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM192HXVAJR |  |  | AM264JXVAJR | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
204572274 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM144FXVAJR |  |  | AM288JXVAJR | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
204572288 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM264KXVTFH | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
204572289 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM288KXVTFH | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
204572296 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM264KXVTJH | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
204572297 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM288KXVTJH | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
204572304 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM264KXVTFR | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
204572305 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM288KXVTFR | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
204572312 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM264KXVTJR | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
204572313 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM288KXVTJR | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
205000514 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAFR | AM192HXVAFR |  |  | AM360JXVAFR | Non-Ducted Indoor Units | 344000 | 10.3 | 23 | 386000 | 3.45 | 250000 | 2.49 | R-410A | 28.6667
205000548 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAFH | AM192HXVAFH |  |  | AM360JXVAFH | Non-Ducted Indoor Units | 344000 | 10.3 | 23 | 386000 | 3.45 | 250000 | 2.49 | R-410A | 28.6667
205000549 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAJH | AM192HXVAJH |  |  | AM360JXVAJH | Non-Ducted Indoor Units | 344000 | 10.3 | 23 | 386000 | 3.45 | 250000 | 2.49 | R-410A | 28.6667
205000550 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAJR | AM192HXVAJR |  |  | AM360JXVAJR | Non-Ducted Indoor Units | 344000 | 10.3 | 23 | 386000 | 3.45 | 250000 | 2.49 | R-410A | 28.6667
205234703 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ144XATJ* |  |  | RXYQ264XATJ* | Non-Ducted Indoor Units | 252000 | 10.3 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 21
205234704 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* | RXYQ144XATJ* |  |  | RXYQ288XATJ* | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
205234705 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* | RXYQ168XATJ* |  |  | RXYQ312XATJ* | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
205234707 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ120XATJ* | RXYQ120XATJ* |  | RXYQ360XATJ* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 372000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
205234710 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* | RXYQ120XAYC* |  | RXYQ360XAYC* | Non-Ducted Indoor Units | 342000 | 10.5 | 19.1 | 384000 | 3.62 | 270000 | 2.28 | R-410A | 28.5
205234711 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* | RXYQ144XAYC* |  | RXYQ384XAYC* | Non-Ducted Indoor Units | 352000 | 9.6 | 18.3 | 398000 | 3.26 | 280000 | 2.24 | R-410A | 29.3333
205234773 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ144XAYD* |  |  | RXYQ264XAYD* | Non-Ducted Indoor Units | 252000 | 10.3 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 21
205234774 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* | RXYQ144XAYD* |  |  | RXYQ288XAYD* | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
205234775 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* | RXYQ168XAYD* |  |  | RXYQ312XAYD* | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
205234777 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ120XAYD* | RXYQ120XAYD* |  | RXYQ360XAYD* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 372000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
205234788 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ144XAYC* |  |  | RXYQ264XAYC* | Non-Ducted Indoor Units | 252000 | 10.8 | 20.1 | 282000 | 3.71 | 200000 | 2.27 | R-410A | 21
205234789 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYC* | RXYQ144XAYC* |  |  | RXYQ288XAYC* | Non-Ducted Indoor Units | 274000 | 10.8 | 20.1 | 306000 | 3.48 | 216000 | 2.24 | R-410A | 22.8333
205234791 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168XAYC* | RXYQ168XAYC* |  |  | RXYQ336XAYC* | Non-Ducted Indoor Units | 308000 | 9.8 | 18.9 | 338000 | 3.6 | 228000 | 2.11 | R-410A | 25.6667
205234796 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* | RXYQ144XATJ* |  |  | RXYQ288XATJ* | Ducted Indoor Units | 274000 | 10.1 | 19.6 | 308000 | 3.3 | 200000 | 2.13 | R-410A | 22.8333
205234806 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* | RXYQ144XAYD* |  |  | RXYQ288XAYD* | Ducted Indoor Units | 274000 | 10.1 | 19.6 | 308000 | 3.3 | 200000 | 2.13 | R-410A | 22.8333
205234843 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ144XATJ* |  |  | RXYQ264XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.95 | 19.95 | 282000 | 3.28 | 186000 | 2.36 | R-410A | 21
205234844 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* | RXYQ144XATJ* |  |  | RXYQ288XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 19.85 | 308000 | 3.27 | 200000 | 2.1 | R-410A | 22.8333
205234845 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XATJ* | RXYQ168XATJ* |  |  | RXYQ312XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.7 | 19.35 | 334000 | 3.25 | 206000 | 2.26 | R-410A | 24.6667
205234847 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XATJ* | RXYQ120XATJ* | RXYQ120XATJ* |  | RXYQ360XATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.95 | 372000 | 3.33 | 250000 | 2.41 | R-410A | 28.5
205234853 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ144XAYD* |  |  | RXYQ264XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.95 | 19.95 | 282000 | 3.28 | 186000 | 2.36 | R-410A | 21
205234854 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* | RXYQ144XAYD* |  |  | RXYQ288XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 19.85 | 308000 | 3.27 | 200000 | 2.1 | R-410A | 22.8333
205234855 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYD* | RXYQ168XAYD* |  |  | RXYQ312XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.7 | 19.35 | 334000 | 3.25 | 206000 | 2.26 | R-410A | 24.6667
205234857 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYD* | RXYQ120XAYD* | RXYQ120XAYD* |  | RXYQ360XAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.95 | 372000 | 3.33 | 250000 | 2.41 | R-410A | 28.5
205234868 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ144XAYC* |  |  | RXYQ264XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.2 | 18.3 | 282000 | 3.47 | 200000 | 2.18 | R-410A | 21
205234869 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144XAYC* | RXYQ144XAYC* |  |  | RXYQ288XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 18.6 | 306000 | 3.34 | 216000 | 2.16 | R-410A | 22.8333
205234871 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168XAYC* | RXYQ168XAYC* |  |  | RXYQ336XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 308000 | 9.65 | 17.8 | 338000 | 3.4 | 228000 | 2.08 | R-410A | 25.6667
205234872 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120XAYC* | RXYQ120XAYC* | RXYQ120XAYC* |  | RXYQ360XAYC* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.1 | 384000 | 3.42 | 270000 | 2.19 | R-410A | 28.5
203376929 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P384YSNU-A | Ducted Indoor Units | 345654 | 10.05 | 19.73 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 28.8045
203376933 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P384TSNU-A | Ducted Indoor Units | 345654 | 10.05 | 19.73 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 28.8045
203376937 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP384YSNU-A | Ducted Indoor Units | 345654 | 10.55 | 21.06 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 28.8045
203376941 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP384TSNU-A | Ducted Indoor Units | 345654 | 10.55 | 21.06 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 28.8045
203378290 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P384YSNU-A | Non-Ducted Indoor Units | 345654 | 9.95 | 17.96 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 28.8045
203378291 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P384TSNU-A | Non-Ducted Indoor Units | 345654 | 9.95 | 17.96 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 28.8045
203378292 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP384YSNU-A | Non-Ducted Indoor Units | 345654 | 10.5 | 18.58 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 28.8045
203378293 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP384TSNU-A | Non-Ducted Indoor Units | 345654 | 10.5 | 18.58 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 28.8045
203378353 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3843BN40AN | Ducted Indoor Units | 345654 | 10.55 | 21.06 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 28.8045
203378354 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3844BN40AN | Ducted Indoor Units | 345654 | 10.55 | 21.06 | 410000 | 3.48 | 328000 | 2.13 | R-410A | 28.8045
203378419 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3843BN40AN | Ducted Indoor Units | 345654 | 10.05 | 19.73 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 28.8045
203378420 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3844BN40AN | Ducted Indoor Units | 345654 | 10.05 | 19.73 | 410000 | 3.39 | 262000 | 2.16 | R-410A | 28.8045
203378449 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3843BN40AN | Non-Ducted Indoor Units | 345654 | 10.5 | 18.58 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 28.8045
203378450 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3844BN40AN | Non-Ducted Indoor Units | 345654 | 10.5 | 18.58 | 410000 | 3.57 | 328000 | 2.19 | R-410A | 28.8045
203378451 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3843BN40AN | Non-Ducted Indoor Units | 345654 | 9.95 | 17.96 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 28.8045
203378452 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3844BN40AN | Non-Ducted Indoor Units | 345654 | 9.95 | 17.96 | 410000 | 3.45 | 262000 | 2.25 | R-410A | 28.8045
203381097 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144TNU-A | PUHY-EP120TNU-A | PUHY-EP120TNU-A |  | PUHY-EP384TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10.5 | 19.82 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 28.8045
203381098 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-EP144YNU-A | PUHY-EP120YNU-A | PUHY-EP120YNU-A |  | PUHY-EP384YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10.5 | 19.82 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 28.8045
203381141 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144TNU-A | PUHY-P120TNU-A | PUHY-P120TNU-A |  | PUHY-P384TSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10 | 18.85 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 28.8045
203381142 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P144YNU-A | PUHY-P120YNU-A | PUHY-P120YNU-A |  | PUHY-P384YSNU-A | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10 | 18.85 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 28.8045
203381228 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TKMU-A | PURY-P120TKMU-A |  |  | PURY-P264TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11 | 17.65 | 280000 | 3.3 | 200000 | 2.21 | R-410A | 20.8333
203381232 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YKMU-A | PURY-P120YKMU-A |  |  | PURY-P264YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11 | 17.65 | 280000 | 3.3 | 200000 | 2.21 | R-410A | 20.8333
203381237 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144TKMU-A | PURY-P144TKMU-A |  |  | PURY-P288TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.25 | 17.7 | 304000 | 3.3 | 216000 | 2.2 | R-410A | 22.8333
203381241 | 1/1/2027 | Mitsubishi Electric | HMSR-A-CB | PURY-P144YKMU-A | PURY-P144YKMU-A |  |  | PURY-P288YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.25 | 17.7 | 304000 | 3.3 | 216000 | 2.2 | R-410A | 22.8333
203381300 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1443AN40AN | TUHYE1203AN40AN | TUHYE1203AN40AN |  | TUHYE3843BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10.5 | 19.82 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 28.8045
203381301 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYE1444AN40AN | TUHYE1204AN40AN | TUHYE1204AN40AN |  | TUHYE3844BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10.5 | 19.82 | 410000 | 3.52 | 328000 | 2.16 | R-410A | 28.8045
203381344 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1443AN40AN | TUHYP1203AN40AN | TUHYP1203AN40AN |  | TUHYP3843BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10 | 18.85 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 28.8045
203381346 | 1/1/2027 | Trane / Mitsubishi Electric | HMSV-A-CB | TUHYP1444AN40AN | TUHYP1204AN40AN | TUHYP1204AN40AN |  | TUHYP3844BN40AN | Mixed Ducted and Non-Ducted Indoor Units | 345654 | 10 | 18.85 | 410000 | 3.42 | 262000 | 2.2 | R-410A | 28.8045
204442750 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM192HXVAFR |  |  | AM264JXVAFR | Non-Ducted Indoor Units | 252000 | 10.7 | 22.5 | 282000 | 3.56 | 184000 | 2.44 | R-410A | 21
204442752 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR | AM168HXVAFR |  |  | AM312JXVAFR | Non-Ducted Indoor Units | 298000 | 10.8 | 21.6 | 334000 | 3.5 | 218000 | 2.49 | R-410A | 24.8333
204442754 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192HXVAFR | AM192HXVAFR |  |  | AM384JXVAFR | Non-Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.4 | 268000 | 2.45 | R-410A | 30.5
204442765 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM192HXVAJR |  |  | AM264JXVAJR | Non-Ducted Indoor Units | 252000 | 10.7 | 22.5 | 282000 | 3.56 | 184000 | 2.44 | R-410A | 21
204442767 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM168HXVAJR |  |  | AM312JXVAJR | Non-Ducted Indoor Units | 298000 | 10.8 | 21.6 | 334000 | 3.5 | 218000 | 2.49 | R-410A | 24.8333
204442781 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM264KXVTFH | Non-Ducted Indoor Units | 252000 | 12.8 | 28.3 | 282000 | 3.7 | 282000 | 2.11 | R-410A | 21
204442782 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM288KXVTFH | Non-Ducted Indoor Units | 276000 | 12.8 | 28.1 | 308000 | 3.7 | 308000 | 2.1 | R-410A | 23
204442789 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM264KXVTJH | Non-Ducted Indoor Units | 252000 | 12.8 | 28.3 | 282000 | 3.7 | 282000 | 2.11 | R-410A | 21
204442790 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM288KXVTJH | Non-Ducted Indoor Units | 276000 | 12.8 | 28.1 | 308000 | 3.7 | 308000 | 2.1 | R-410A | 23
204442797 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM264KXVTFR | Non-Ducted Indoor Units | 252000 | 12.8 | 28.3 | 282000 | 3.7 | 282000 | 2.11 | R-410A | 21
204442769 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192HXVAJR | AM192HXVAJR |  |  | AM384JXVAJR | Non-Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.4 | 268000 | 2.45 | R-410A | 30.5
204442805 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM264KXVTJR | Non-Ducted Indoor Units | 252000 | 12.8 | 28.3 | 282000 | 3.7 | 282000 | 2.11 | R-410A | 21
205281471 | 1/1/2027 | LG | HMSR-A-CB | ARUM168BTE5 | ARUM096BTE5 |  |  | ARUM264BTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
205281473 | 1/1/2027 | LG | HMSR-A-CB | ARUM192BTE5 | ARUM096BTE5 |  |  | ARUM288BTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
205281474 | 1/1/2027 | LG | HMSR-A-CB | ARUM216BTE5 | ARUM096BTE5 |  |  | ARUM312BTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
205281479 | 1/1/2027 | LG | HMSR-A-CB | ARUM168DTE5 | ARUM096DTE5 |  |  | ARUM264DTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
205281480 | 1/1/2027 | LG | HMSR-A-CB | ARUM192DTE5 | ARUM096DTE5 |  |  | ARUM288DTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
205281481 | 1/1/2027 | LG | HMSR-A-CB | ARUM216DTE5 | ARUM096DTE5 |  |  | ARUM312DTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
204442808 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192HXVAJH | AM216KXVGJH |  |  | AM408KXVGJH | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
204442809 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM216KXVGJH | AM216KXVGJH |  |  | AM432KXVGJH | Non-Ducted Indoor Units | 416000 | 9.8 | 21 | 460000 | 3.3 | 300000 | 2.4 | R-410A | 34.6667
206799477 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM192HXVAFH |  |  | AM264JXVAFH | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
206799478 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM192HXVAFR |  |  | AM264JXVAFR | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
206799479 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM192HXVAJH |  |  | AM264JXVAJH | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
206799480 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM192HXVAJR |  |  | AM264JXVAJR | Ducted Indoor Units | 252000 | 9.8 | 19.6 | 282000 | 3.3 | 184000 | 2.35 | R-410A | 21
206799481 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM264KXVTFH | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
206799482 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM264KXVTFR | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
206799483 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM264KXVTJH | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
206799484 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM264KXVTJR | Ducted Indoor Units | 252000 | 11.3 | 20.4 | 282000 | 3.51 | 282000 | 2.1 | R-410A | 21
206799485 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH | AM144FXVAFH |  |  | AM288JXVAFH | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
206799486 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR | AM144FXVAFR |  |  | AM288JXVAFR | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
206799487 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM144FXVAJH |  |  | AM288JXVAJH | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
206799488 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM144FXVAJR |  |  | AM288JXVAJR | Ducted Indoor Units | 276000 | 9.6 | 20 | 308000 | 3.3 | 200000 | 2.45 | R-410A | 23
206799489 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTFH | AM096KXVTFH | AM096KXVTFH |  | AM288KXVTFH | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
206799490 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM288KXVTFR | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
206799491 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM096KXVTJH | AM096KXVTJH | AM096KXVTJH |  | AM288KXVTJH | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
206799492 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM288KXVTJR | Ducted Indoor Units | 276000 | 11.2 | 20.1 | 308000 | 3.5 | 308000 | 2.1 | R-410A | 23
200084161 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.7 | 22 | 282000 | 3.52 | 186000 | 2.42 | R-410A | 20.6667
200084162 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Non-Ducted Indoor Units | 248000 | 10.7 | 22 | 282000 | 3.52 | 186000 | 2.42 | R-410A | 20.6667
200084163 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Ducted Indoor Units | 248000 | 10.4 | 21 | 282000 | 3.49 | 186000 | 2.3 | R-410A | 20.6667
200084164 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Ducted Indoor Units | 248000 | 10.4 | 21 | 282000 | 3.49 | 186000 | 2.3 | R-410A | 20.6667
200084165 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.55 | 21.5 | 282000 | 3.5 | 186000 | 2.36 | R-410A | 20.6667
200084166 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA264RDS6-1 |  |  |  | 38VMA264RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.55 | 21.5 | 282000 | 3.5 | 186000 | 2.36 | R-410A | 20.6667
200084167 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA288RDS6-1 |  |  |  | 38VMA288RDS6-1 | Non-Ducted Indoor Units | 274000 | 10.4 | 21 | 298000 | 3.38 | 198000 | 2.2 | R-410A | 22.8333
200084168 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA288RDS6-1 |  |  |  | 38VMA288RDS6-1 | Non-Ducted Indoor Units | 274000 | 10.4 | 21 | 298000 | 3.38 | 198000 | 2.2 | R-410A | 22.8333
200084169 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA288RDS6-1 |  |  |  | 38VMA288RDS6-1 | Ducted Indoor Units | 274000 | 9.8 | 20.5 | 298000 | 3.42 | 198000 | 2.26 | R-410A | 22.8333
200084170 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA288RDS6-1 |  |  |  | 38VMA288RDS6-1 | Ducted Indoor Units | 274000 | 9.8 | 20.5 | 298000 | 3.42 | 198000 | 2.26 | R-410A | 22.8333
200084171 | 1/1/2027 | CARRIER | HMSR-A-CB | 38VMA288RDS6-1 |  |  |  | 38VMA288RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.1 | 20.75 | 298000 | 3.4 | 198000 | 2.23 | R-410A | 22.8333
200084172 | 1/1/2027 | BRYANT | HMSR-A-CB | 38VMA288RDS6-1 |  |  |  | 38VMA288RDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.1 | 20.75 | 298000 | 3.4 | 198000 | 2.23 | R-410A | 22.8333
201847149 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G | VPA096H4M-2G |  | VPA312H4M-2G | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201847150 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G | VPA096H4M-2G |  | VPA312H4M-2G | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201847151 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y | VPA096H4M-2Y |  | VPA312H4M-2Y | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201847152 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y | VPA096H4M-2Y |  | VPA312H4M-2Y | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201847153 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA120H4M-2G | VPA096H4M-2G |  | VPA336H4M-2G | Non-Ducted Indoor Units | 320000 | 10.7 | 19 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
201847154 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA120H4M-2G | VPA096H4M-2G |  | VPA336H4M-2G | Ducted Indoor Units | 320000 | 10.1 | 19.6 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
201847155 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA120H4M-2Y | VPA096H4M-2Y |  | VPA336H4M-2Y | Non-Ducted Indoor Units | 320000 | 10.7 | 19 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
201847156 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA120H4M-2Y | VPA096H4M-2Y |  | VPA336H4M-2Y | Ducted Indoor Units | 320000 | 10.1 | 19.6 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
201847209 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y | VRA096H4M-2Y |  | VRA312H4M-2Y | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201847210 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y | VRA096H4M-2Y |  | VRA312H4M-2Y | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201847211 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G | VRA096H4M-2G |  | VRA312H4M-2G | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201847212 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G | VRA096H4M-2G |  | VRA312H4M-2G | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201847213 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA120H4M-2Y | VRA096H4M-2Y |  | VRA336H4M-2Y | Non-Ducted Indoor Units | 320000 | 10.7 | 19.4 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
201847214 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA120H4M-2Y | VRA096H4M-2Y |  | VRA336H4M-2Y | Ducted Indoor Units | 320000 | 10.3 | 19.9 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
201847215 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA120H4M-2G | VRA096H4M-2G |  | VRA336H4M-2G | Non-Ducted Indoor Units | 320000 | 10.7 | 19.4 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
201847216 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA120H4M-2G | VRA096H4M-2G |  | VRA336H4M-2G | Ducted Indoor Units | 320000 | 10.3 | 19.9 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
201856734 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  | MV5-RC264DXN1-(A) | Non-Ducted Indoor Units | 252000 | 11.5 | 22.4 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201856735 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  | MV5-RC264DXN1-(A) | Ducted Indoor Units | 252000 | 10.7 | 20.5 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201856736 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  | MV5-RC288DXN1-(A) | Non-Ducted Indoor Units | 276000 | 10.9 | 21.2 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201856737 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC72DXN1-(A) |  | MV5-RC288DXN1-(A) | Ducted Indoor Units | 276000 | 10.3 | 18.9 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201856738 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) |  | MV5-RC312DXN1-(A) | Non-Ducted Indoor Units | 298000 | 10.3 | 20.6 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201856739 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) | MV5-RC96DXN1-(A) |  | MV5-RC312DXN1-(A) | Ducted Indoor Units | 298000 | 9.9 | 18.7 | 320000 | 3.32 | 218000 | 2.18 | R-410A | 24.8333
201856740 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) |  | MV5-RC336DXN1-(A) | Non-Ducted Indoor Units | 320000 | 10 | 19.7 | 338000 | 3.35 | 224000 | 2.17 | R-410A | 26.6667
201856741 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DXN1-(A) | MV5-RC120DXN1-(A) | MV5-RC96DXN1-(A) |  | MV5-RC336DXN1-(A) | Ducted Indoor Units | 320000 | 9.6 | 17.9 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 26.6667
201856758 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  | MV5-RC264DZN1-(A) | Non-Ducted Indoor Units | 252000 | 11.5 | 22.4 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201856759 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  | MV5-RC264DZN1-(A) | Ducted Indoor Units | 252000 | 10.7 | 20.5 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201856760 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  | MV5-RC288DZN1-(A) | Non-Ducted Indoor Units | 276000 | 10.9 | 21.2 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201856761 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC72DZN1-(A) |  | MV5-RC288DZN1-(A) | Ducted Indoor Units | 276000 | 10.3 | 18.9 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201856762 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) |  | MV5-RC312DZN1-(A) | Non-Ducted Indoor Units | 298000 | 10.3 | 20.6 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201856763 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) | MV5-RC96DZN1-(A) |  | MV5-RC312DZN1-(A) | Ducted Indoor Units | 298000 | 9.9 | 18.7 | 320000 | 3.32 | 218000 | 2.18 | R-410A | 24.8333
201856764 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) |  | MV5-RC336DZN1-(A) | Non-Ducted Indoor Units | 320000 | 10 | 19.7 | 338000 | 3.35 | 224000 | 2.17 | R-410A | 26.6667
201856765 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-RC120DZN1-(A) | MV5-RC120DZN1-(A) | MV5-RC96DZN1-(A) |  | MV5-RC336DZN1-(A) | Ducted Indoor Units | 320000 | 9.6 | 17.9 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 26.6667
201856782 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  | MV5-XC264DXN1-(A) | Non-Ducted Indoor Units | 252000 | 11.3 | 21.9 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201856783 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DXN1-(A) | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  | MV5-XC264DXN1-(A) | Ducted Indoor Units | 252000 | 10.5 | 20.3 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201856784 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  | MV5-XC288DXN1-(A) | Non-Ducted Indoor Units | 276000 | 10.7 | 20.9 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201856785 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) | MV5-XC96DXN1-(A) | MV5-XC72DXN1-(A) |  | MV5-XC288DXN1-(A) | Ducted Indoor Units | 276000 | 10.1 | 18.6 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201856786 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DXN1-(A) | MV5-XC96DXN1-(A) | MV5-XC96DXN1-(A) |  | MV5-XC312DXN1-(A) | Non-Ducted Indoor Units | 298000 | 9.8 | 20.3 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201856804 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  | MV5-XC264DZN1-(A) | Non-Ducted Indoor Units | 252000 | 11.3 | 21.9 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201856805 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC96DZN1-(A) | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  | MV5-XC264DZN1-(A) | Ducted Indoor Units | 252000 | 10.5 | 20.3 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201856806 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  | MV5-XC288DZN1-(A) | Non-Ducted Indoor Units | 276000 | 10.7 | 20.9 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201856807 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) | MV5-XC96DZN1-(A) | MV5-XC72DZN1-(A) |  | MV5-XC288DZN1-(A) | Ducted Indoor Units | 276000 | 10.1 | 18.6 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201856808 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-XC120DZN1-(A) | MV5-XC96DZN1-(A) | MV5-XC96DZN1-(A) |  | MV5-XC312DZN1-(A) | Non-Ducted Indoor Units | 298000 | 9.8 | 20.3 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201862870 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA096L4M-2Y | VRA072L4M-2Y |  | VRA264L4M-2Y | Non-Ducted Indoor Units | 252000 | 11.5 | 22.4 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201862871 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2Y | VRA096L4M-2Y | VRA072L4M-2Y |  | VRA264L4M-2Y | Ducted Indoor Units | 252000 | 10.7 | 20.5 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201862872 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y | VRA072L4M-2Y |  | VRA288L4M-2Y | Non-Ducted Indoor Units | 276000 | 10.9 | 21.2 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201862873 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y | VRA072L4M-2Y |  | VRA288L4M-2Y | Ducted Indoor Units | 276000 | 10.3 | 18.9 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201862874 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y | VRA096L4M-2Y |  | VRA312L4M-2Y | Non-Ducted Indoor Units | 298000 | 10.3 | 20.6 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201862875 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA096L4M-2Y | VRA096L4M-2Y |  | VRA312L4M-2Y | Ducted Indoor Units | 298000 | 9.9 | 18.7 | 320000 | 3.32 | 218000 | 2.18 | R-410A | 24.8333
201862876 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA120L4M-2Y | VRA096L4M-2Y |  | VRA336L4M-2Y | Non-Ducted Indoor Units | 320000 | 10 | 19.7 | 338000 | 3.35 | 224000 | 2.17 | R-410A | 26.6667
201862877 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2Y | VRA120L4M-2Y | VRA096L4M-2Y |  | VRA336L4M-2Y | Ducted Indoor Units | 320000 | 9.6 | 17.9 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 26.6667
201862894 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA096L4M-2G | VRA072L4M-2G |  | VRA264L4M-2G | Non-Ducted Indoor Units | 252000 | 11.5 | 22.4 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201862895 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA096L4M-2G | VRA096L4M-2G | VRA072L4M-2G |  | VRA264L4M-2G | Ducted Indoor Units | 252000 | 10.7 | 20.5 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201862896 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G | VRA072L4M-2G |  | VRA288L4M-2G | Non-Ducted Indoor Units | 276000 | 10.9 | 21.2 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201862897 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G | VRA072L4M-2G |  | VRA288L4M-2G | Ducted Indoor Units | 276000 | 10.3 | 18.9 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201862898 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G | VRA096L4M-2G |  | VRA312L4M-2G | Non-Ducted Indoor Units | 298000 | 10.3 | 20.6 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201862899 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA096L4M-2G | VRA096L4M-2G |  | VRA312L4M-2G | Ducted Indoor Units | 298000 | 9.9 | 18.7 | 320000 | 3.32 | 218000 | 2.18 | R-410A | 24.8333
201862900 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA120L4M-2G | VRA096L4M-2G |  | VRA336L4M-2G | Non-Ducted Indoor Units | 320000 | 10 | 19.7 | 338000 | 3.35 | 224000 | 2.17 | R-410A | 26.6667
201862901 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120L4M-2G | VRA120L4M-2G | VRA096L4M-2G |  | VRA336L4M-2G | Ducted Indoor Units | 320000 | 9.6 | 17.9 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 26.6667
201862918 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA096L4M-2Y | VPA072L4M-2Y |  | VPA264L4M-2Y | Non-Ducted Indoor Units | 252000 | 11.3 | 21.9 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201862919 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2Y | VPA096L4M-2Y | VPA072L4M-2Y |  | VPA264L4M-2Y | Ducted Indoor Units | 252000 | 10.5 | 20.3 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201862920 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y | VPA096L4M-2Y | VPA072L4M-2Y |  | VPA288L4M-2Y | Non-Ducted Indoor Units | 276000 | 10.7 | 20.9 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201862921 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y | VPA096L4M-2Y | VPA072L4M-2Y |  | VPA288L4M-2Y | Ducted Indoor Units | 276000 | 10.1 | 18.6 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201862922 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2Y | VPA096L4M-2Y | VPA096L4M-2Y |  | VPA312L4M-2Y | Non-Ducted Indoor Units | 298000 | 9.8 | 20.3 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201862940 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA096L4M-2G | VPA072L4M-2G |  | VPA264L4M-2G | Non-Ducted Indoor Units | 252000 | 11.3 | 21.9 | 282000 | 3.6 | 198000 | 2.33 | R-410A | 21
201862941 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA096L4M-2G | VPA096L4M-2G | VPA072L4M-2G |  | VPA264L4M-2G | Ducted Indoor Units | 252000 | 10.5 | 20.3 | 282000 | 3.42 | 198000 | 2.26 | R-410A | 21
201862942 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G | VPA096L4M-2G | VPA072L4M-2G |  | VPA288L4M-2G | Non-Ducted Indoor Units | 276000 | 10.7 | 20.9 | 298000 | 3.5 | 204000 | 2.32 | R-410A | 23
201862943 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G | VPA096L4M-2G | VPA072L4M-2G |  | VPA288L4M-2G | Ducted Indoor Units | 276000 | 10.1 | 18.6 | 298000 | 3.35 | 204000 | 2.19 | R-410A | 23
201862944 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120L4M-2G | VPA096L4M-2G | VPA096L4M-2G |  | VPA312L4M-2G | Non-Ducted Indoor Units | 298000 | 9.8 | 20.3 | 320000 | 3.45 | 218000 | 2.22 | R-410A | 24.8333
201863373 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X312DXN1-(A)* | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201863374 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X312DXN1-(A)* | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201863379 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X312DZN1-(A)* | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201863380 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X312DZN1-(A)* | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201863385 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R312DXN1-(A)* | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201863386 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R312DXN1-(A)* | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
201863391 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R312DZN1-(A)* | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
201863392 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R312DZN1-(A)* | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
10611545 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X312DXN1-(A) | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
10611546 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X312DXN1-(A) | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
10611547 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X336DXN1-(A) | Non-Ducted Indoor Units | 320000 | 10.7 | 19 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
10611548 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X336DXN1-(A) | Ducted Indoor Units | 320000 | 10.1 | 19.6 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
10611559 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X312DZN1-(A) | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
10611560 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X312DZN1-(A) | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
10611561 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X336DZN1-(A) | Non-Ducted Indoor Units | 320000 | 10.7 | 19 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
10611562 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X336DZN1-(A) | Ducted Indoor Units | 320000 | 10.1 | 19.6 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
10611584 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R312DXN1-(A) | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
10611585 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R312DXN1-(A) | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
10611586 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R336DXN1-(A) | Non-Ducted Indoor Units | 320000 | 10.7 | 19.4 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
10611587 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R336DXN1-(A) | Ducted Indoor Units | 320000 | 10.3 | 19.9 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
10611608 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R312DZN1-(A) | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
10611609 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R312DZN1-(A) | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
10611610 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R336DZN1-(A) | Non-Ducted Indoor Units | 320000 | 10.7 | 19.4 | 338000 | 3.27 | 224000 | 2.1 | R-410A | 26.6667
10611611 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R336DZN1-(A) | Ducted Indoor Units | 320000 | 10.3 | 19.9 | 338000 | 3.25 | 224000 | 2.15 | R-410A | 26.6667
10611628 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X312DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.65 | 20.65 | 320000 | 3.31 | 218000 | 2.22 | R-410A | 24.8333
10611629 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DXN1-(A) | MV5-X120DXN1-(A) | MV5-X96DXN1-(A) |  | MV5-X336DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.4 | 19.3 | 338000 | 3.26 | 224000 | 2.12 | R-410A | 26.6667
10611643 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X312DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.65 | 20.65 | 320000 | 3.31 | 218000 | 2.22 | R-410A | 24.8333
10611644 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-X120DZN1-(A) | MV5-X120DZN1-(A) | MV5-X96DZN1-(A) |  | MV5-X336DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.4 | 19.3 | 338000 | 3.26 | 224000 | 2.12 | R-410A | 26.6667
10612360 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R312DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.8 | 21 | 320000 | 3.31 | 218000 | 2.22 | R-410A | 24.8333
10612361 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DXN1-(A) | MV5-R120DXN1-(A) | MV5-R96DXN1-(A) |  | MV5-R336DXN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.65 | 338000 | 3.26 | 224000 | 2.12 | R-410A | 26.6667
10612372 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R312DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.8 | 21 | 320000 | 3.31 | 218000 | 2.22 | R-410A | 24.8333
10612373 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-R120DZN1-(A) | MV5-R120DZN1-(A) | MV5-R96DZN1-(A) |  | MV5-R336DZN1-(A) | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 19.65 | 338000 | 3.26 | 224000 | 2.12 | R-410A | 26.6667
10612415 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
10612416 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
10612417 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
10612418 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Ducted Indoor Units | 276000 | 11.3 | 20 | 308000 | 3.81 | 216000 | 2.88 | R-410A | 23
10612419 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
10612420 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Ducted Indoor Units | 276000 | 11.3 | 20 | 308000 | 3.81 | 216000 | 2.88 | R-410A | 23
10612421 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
10612422 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Ducted Indoor Units | 276000 | 11.2 | 19.6 | 308000 | 3.76 | 216000 | 2.8 | R-410A | 23
10612423 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
10612424 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Ducted Indoor Units | 276000 | 11.2 | 19.6 | 308000 | 3.76 | 216000 | 2.8 | R-410A | 23
10612425 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
10612426 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Ducted Indoor Units | 298000 | 10.8 | 19.7 | 334000 | 3.66 | 236000 | 2.72 | R-410A | 24.8333
10612427 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
10612428 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Ducted Indoor Units | 298000 | 10.8 | 19.7 | 334000 | 3.66 | 236000 | 2.72 | R-410A | 24.8333
10612429 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
10612430 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Ducted Indoor Units | 320000 | 10.4 | 19.6 | 360000 | 3.49 | 268000 | 2.57 | R-410A | 26.6667
10612431 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
10612432 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Ducted Indoor Units | 320000 | 10.4 | 19.6 | 360000 | 3.49 | 268000 | 2.57 | R-410A | 26.6667
10612433 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 384000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
10612434 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Ducted Indoor Units | 342000 | 11.8 | 20.3 | 384000 | 3.66 | 284000 | 2.72 | R-410A | 28.5
10612435 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 384000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
10612436 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Ducted Indoor Units | 342000 | 11.8 | 20.3 | 384000 | 3.66 | 284000 | 2.72 | R-410A | 28.5
10612487 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Ducted Indoor Units | 252000 | 12 | 20.4 | 282000 | 3.9 | 200000 | 2.88 | R-410A | 21
10612488 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Ducted Indoor Units | 252000 | 12 | 20.4 | 282000 | 3.9 | 200000 | 2.88 | R-410A | 21
10612489 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.7 | 21.6 | 282000 | 3.77 | 200000 | 2.77 | R-410A | 21
10612490 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 21.8 | 282000 | 3.43 | 200000 | 2.41 | R-410A | 21
10612491 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 21.8 | 282000 | 3.43 | 200000 | 2.41 | R-410A | 21
10612492 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.2 | 21.25 | 308000 | 3.7 | 216000 | 2.76 | R-410A | 23
10612493 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.2 | 21.25 | 308000 | 3.7 | 216000 | 2.76 | R-410A | 23
10612494 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 20.9 | 308000 | 3.63 | 216000 | 2.69 | R-410A | 23
10612495 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 20.9 | 308000 | 3.63 | 216000 | 2.69 | R-410A | 23
10612496 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 21.5 | 308000 | 3.45 | 216000 | 2.43 | R-410A | 23
10612497 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.05 | 21.5 | 308000 | 3.45 | 216000 | 2.43 | R-410A | 23
10612498 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.05 | 21.05 | 308000 | 3.36 | 216000 | 2.33 | R-410A | 23
10612499 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.05 | 21.05 | 308000 | 3.36 | 216000 | 2.33 | R-410A | 23
10612500 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.54 | 236000 | 2.66 | R-410A | 24.8333
10612501 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.54 | 236000 | 2.66 | R-410A | 24.8333
10612502 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 20.9 | 334000 | 3.29 | 236000 | 2.36 | R-410A | 24.8333
10612503 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.15 | 20.9 | 334000 | 3.29 | 236000 | 2.36 | R-410A | 24.8333
10612504 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.35 | 20.8 | 360000 | 3.42 | 268000 | 2.51 | R-410A | 26.6667
10612505 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.35 | 20.8 | 360000 | 3.42 | 268000 | 2.51 | R-410A | 26.6667
10612506 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 22.3 | 360000 | 3.36 | 268000 | 2.39 | R-410A | 26.6667
10612507 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 22.3 | 360000 | 3.36 | 268000 | 2.39 | R-410A | 26.6667
10612510 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.7 | 21.35 | 384000 | 3.59 | 284000 | 2.65 | R-410A | 28.5
10612511 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.7 | 21.35 | 384000 | 3.59 | 284000 | 2.65 | R-410A | 28.5
10612512 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.6 | 21.75 | 386000 | 3.33 | 284000 | 2.31 | R-410A | 28.5
10612513 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 9.6 | 21.75 | 386000 | 3.33 | 284000 | 2.31 | R-410A | 28.5
10612514 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.8 | 20.8 | 410000 | 3.47 | 294000 | 2.59 | R-410A | 30.5
10612515 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3846FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 21.25 | 412000 | 3.25 | 294000 | 2.26 | R-410A | 30.5
10612516 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3846FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.6 | 21.25 | 412000 | 3.25 | 294000 | 2.26 | R-410A | 30.5
10612517 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.7 | 20.5 | 434000 | 3.37 | 310000 | 2.53 | R-410A | 32.5
10612518 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.4 | 20.15 | 434000 | 3.31 | 310000 | 2.51 | R-410A | 32.5
10612521 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.1 | 20.2 | 460000 | 3.3 | 328000 | 2.5 | R-410A | 34.1667
10612598 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.7 | 21.6 | 282000 | 3.77 | 200000 | 2.77 | R-410A | 21
10612599 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Non-Ducted Indoor Units | 252000 | 10.9 | 23.1 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
10612600 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Ducted Indoor Units | 252000 | 10.9 | 20.5 | 282000 | 3.46 | 200000 | 2.37 | R-410A | 21
10612601 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Non-Ducted Indoor Units | 252000 | 10.9 | 23.1 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
10612602 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Ducted Indoor Units | 252000 | 10.9 | 20.5 | 282000 | 3.46 | 200000 | 2.37 | R-410A | 21
10612603 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.8 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
10612604 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Ducted Indoor Units | 276000 | 11 | 20.2 | 308000 | 3.46 | 216000 | 2.37 | R-410A | 23
10612605 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.8 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
10612606 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Ducted Indoor Units | 276000 | 11 | 20.2 | 308000 | 3.46 | 216000 | 2.37 | R-410A | 23
10612607 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Non-Ducted Indoor Units | 276000 | 10.3 | 22.4 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
10612608 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Ducted Indoor Units | 276000 | 9.8 | 19.7 | 308000 | 3.37 | 216000 | 2.32 | R-410A | 23
10612609 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Non-Ducted Indoor Units | 276000 | 10.3 | 22.4 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
10612610 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Ducted Indoor Units | 276000 | 9.8 | 19.7 | 308000 | 3.37 | 216000 | 2.32 | R-410A | 23
10612611 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Non-Ducted Indoor Units | 298000 | 10.3 | 22.1 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
10612612 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Ducted Indoor Units | 298000 | 10 | 19.7 | 334000 | 3.29 | 236000 | 2.33 | R-410A | 24.8333
10612613 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Non-Ducted Indoor Units | 298000 | 10.3 | 22.1 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
10612614 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Ducted Indoor Units | 298000 | 10 | 19.7 | 334000 | 3.29 | 236000 | 2.33 | R-410A | 24.8333
10612615 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.7 | 23.9 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
10612616 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Ducted Indoor Units | 320000 | 10.2 | 20.7 | 360000 | 3.32 | 268000 | 2.38 | R-410A | 26.6667
10612617 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.7 | 23.9 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
10612618 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Ducted Indoor Units | 320000 | 10.2 | 20.7 | 360000 | 3.32 | 268000 | 2.38 | R-410A | 26.6667
10612619 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1686FT6P-UL |  |  | MMY-AP336S6FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.1 | 21.9 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
10612621 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1686FT9P-UL |  |  | MMY-AP336S6FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.1 | 21.9 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
10612623 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Non-Ducted Indoor Units | 342000 | 9.7 | 23.3 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
10612625 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Non-Ducted Indoor Units | 342000 | 9.7 | 23.3 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
10612627 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
10612628 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Ducted Indoor Units | 366000 | 11 | 19.8 | 410000 | 3.55 | 294000 | 2.63 | R-410A | 30.5
10612629 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
10612630 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Ducted Indoor Units | 366000 | 11 | 19.8 | 410000 | 3.55 | 294000 | 2.63 | R-410A | 30.5
10612635 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 435000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
10612636 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Ducted Indoor Units | 390000 | 11 | 19.6 | 435000 | 3.37 | 310000 | 2.57 | R-410A | 32.5
10612637 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 435000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
10612638 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Ducted Indoor Units | 390000 | 11 | 19.6 | 435000 | 3.37 | 310000 | 2.57 | R-410A | 32.5
10612639 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 435000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
10612640 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Ducted Indoor Units | 390000 | 10.6 | 19.3 | 435000 | 3.32 | 310000 | 2.55 | R-410A | 32.5
10612641 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 435000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
10612642 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Ducted Indoor Units | 390000 | 10.6 | 19.3 | 435000 | 3.32 | 310000 | 2.55 | R-410A | 32.5
10612647 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
10612648 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Ducted Indoor Units | 410000 | 10.2 | 19.1 | 460000 | 3.32 | 328000 | 2.52 | R-410A | 34.1667
10612649 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
10612650 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Ducted Indoor Units | 410000 | 10.2 | 19.1 | 460000 | 3.32 | 328000 | 2.52 | R-410A | 34.1667
10612656 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4566HT6P-UL | Ducted Indoor Units | 430000 | 9.9 | 19.3 | 485000 | 3.26 | 350000 | 2.5 | R-410A | 35.8333
10612658 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4566HT9P-UL | Ducted Indoor Units | 430000 | 9.9 | 19.3 | 485000 | 3.26 | 350000 | 2.5 | R-410A | 35.8333
10612665 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.8 | 20.8 | 410000 | 3.47 | 294000 | 2.59 | R-410A | 30.5
10612666 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.7 | 20.5 | 434000 | 3.37 | 310000 | 2.53 | R-410A | 32.5
10612667 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1206HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.4 | 20.15 | 434000 | 3.31 | 310000 | 2.51 | R-410A | 32.5
10612668 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT6P-UL | MMY-MAP1446HT6P-UL | MMY-MAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.1 | 20.2 | 460000 | 3.3 | 328000 | 2.5 | R-410A | 34.1667
201978080 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A | PUHY-P72TKMU-A |  | PUHY-P264TSKMU-A | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
201978081 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  | PUHY-P264YSKMU-A | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
201978082 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  | PUHY-P288TSKMU-A | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
201978083 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  | PUHY-P288YSKMU-A | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
201978084 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  | PUHY-P312TSKMU-A | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
201978085 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  | PUHY-P312YSKMU-A | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
201978086 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  | PUHY-P336TSKMU-A | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
201978087 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  | PUHY-P336YSKMU-A | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
201981536 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  | PUHY-P312YSKMU-A | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
201981537 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  | PUHY-P336YSKMU-A | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
201981538 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P120YKMU-A |  | PUHY-P360YSKMU-A | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
201982846 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  | PUHY-P312TSKMU-A | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
201982847 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  | PUHY-P336TSKMU-A | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
201982848 | 1/1/2027 | Mitsubishi Electric | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P120TKMU-A |  | PUHY-P360TSKMU-A | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
201992870 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* | RXYQ144TAYC* |  | RXYQ384TAYC* | Non-Ducted Indoor Units | 352000 | 9.6 | 18.3 | 398000 | 3.26 | 280000 | 2.24 | R-410A | 29.3333
201992876 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ144TAYC* |  |  | RXYQ264TAYC* | Non-Ducted Indoor Units | 252000 | 10.8 | 20.1 | 282000 | 3.71 | 200000 | 2.27 | R-410A | 21
201992877 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYC* | RXYQ144TAYC* |  |  | RXYQ288TAYC* | Non-Ducted Indoor Units | 274000 | 10.8 | 20.1 | 306000 | 3.48 | 216000 | 2.24 | R-410A | 22.8333
202016263 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168TAYC* | RXYQ168TAYC* |  |  | RXYQ336TAYC* | Non-Ducted Indoor Units | 308000 | 9.8 | 18.9 | 338000 | 3.6 | 228000 | 2.11 | R-410A | 25.6667
202016265 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* | RXYQ120TAYC* |  | RXYQ360TAYC* | Non-Ducted Indoor Units | 342000 | 10.5 | 19.1 | 384000 | 3.62 | 270000 | 2.28 | R-410A | 28.5
202022807 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ144TAYC* |  |  | RXYQ264TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.2 | 18.3 | 282000 | 3.47 | 200000 | 2.18 | R-410A | 21
202022808 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYC* | RXYQ144TAYC* |  |  | RXYQ288TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 18.6 | 306000 | 3.34 | 216000 | 2.16 | R-410A | 22.8333
202022810 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ168TAYC* | RXYQ168TAYC* |  |  | RXYQ336TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 308000 | 9.65 | 17.8 | 338000 | 3.4 | 228000 | 2.08 | R-410A | 25.6667
202022811 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYC* | RXYQ120TAYC* | RXYQ120TAYC* |  | RXYQ360TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.1 | 384000 | 3.42 | 270000 | 2.19 | R-410A | 28.5
202095846 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y | VPA096H4M-2Y |  | VPA312H4M-2Y | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
202095847 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2Y | VPA096H4M-2Y | VPA096H4M-2Y |  | VPA312H4M-2Y | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
202095848 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G | VPA096H4M-2G |  | VPA312H4M-2G | Non-Ducted Indoor Units | 298000 | 10.7 | 20.4 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
202095849 | 1/1/2027 | LENNOX | HMSV-A-CB | VPA120H4M-2G | VPA096H4M-2G | VPA096H4M-2G |  | VPA312H4M-2G | Ducted Indoor Units | 298000 | 10.6 | 20.9 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
202095850 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y | VRA096H4M-2Y |  | VRA312H4M-2Y | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
202095851 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2Y | VRA096H4M-2Y | VRA096H4M-2Y |  | VRA312H4M-2Y | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
202095852 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G | VRA096H4M-2G |  | VRA312H4M-2G | Non-Ducted Indoor Units | 298000 | 10.9 | 20.8 | 320000 | 3.32 | 218000 | 2.2 | R-410A | 24.8333
202095853 | 1/1/2027 | LENNOX | HMSR-A-CB | VRA120H4M-2G | VRA096H4M-2G | VRA096H4M-2G |  | VRA312H4M-2G | Ducted Indoor Units | 298000 | 10.7 | 21.2 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 24.8333
202606862 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
202606863 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
202606864 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
202606865 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
202606866 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
202606867 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
202606868 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
202606869 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
202606870 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
202606871 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
202606872 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
202606873 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
202606874 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S |  | TVAHP288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
202606875 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S |  | HVAHP288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
202606876 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S |  | YVAHP288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
202606877 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP096B41S | TVAHP072B41S |  | TVAHP288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
202606878 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP096B41S | HVAHP072B41S |  | HVAHP288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
202606879 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP096B41S | YVAHP072B41S |  | YVAHP288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
202606880 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S |  | TVAHR288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
202606881 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S |  | HVAHR288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
202606882 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S |  | YVAHR288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
202606883 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR096B41S | TVAHR072B41S |  | TVAHR288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
202606884 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR096B41S | HVAHR072B41S |  | HVAHR288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
202606885 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR096B41S | YVAHR072B41S |  | YVAHR288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
202607634 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
202607635 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
202607636 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
202607637 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
202607638 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
202607639 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
202607640 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
202607641 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
202607642 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
202607643 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
202607644 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
202607645 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
202607646 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607647 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607648 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607649 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607650 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607651 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607652 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607653 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607654 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607655 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607656 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607657 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
202607658 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607659 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607660 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607661 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607662 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607663 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607664 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607665 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607666 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607667 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607668 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607669 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
202607670 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S |  | TVAHP288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
202607671 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S |  | HVAHP288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
202607672 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S |  | YVAHP288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
202607676 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S |  | TVAHR288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
202607677 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S |  | HVAHR288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
202607678 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S |  | YVAHR288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
202607682 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
202607683 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
202607684 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
202607685 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
202607686 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
202607687 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
202607688 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S |  |  | TVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607689 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S |  |  | HVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607690 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S |  |  | YVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607691 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S |  |  | TVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607692 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S |  |  | HVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607693 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S |  |  | YVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607694 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S |  |  | TVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607695 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S |  |  | HVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607696 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S |  |  | YVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607697 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S |  |  | TVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607698 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S |  |  | HVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607699 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S |  |  | YVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
202607712 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP072B31S |  | TVAHP312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
202607713 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP072B31S |  | HVAHP312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
202607714 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP072B31S |  | YVAHP312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
202607718 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR072B31S |  | TVAHR312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
202607719 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR072B31S |  | HVAHR312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
202607720 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR072B31S |  | YVAHR312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
202607724 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP072B31S |  | TVAHP312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
202607725 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP072B31S |  | HVAHP312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
202607726 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP072B31S |  | YVAHP312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
202607730 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR072B31S |  | TVAHR312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
202607731 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR072B31S |  | HVAHR312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
202607732 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR072B31S |  | YVAHR312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
202607736 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S | TVAHP144B32S |  |  | TVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607737 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S | HVAHP144B32S |  |  | HVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607738 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S | YVAHP144B32S |  |  | YVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607739 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S | TVAHP144B42S |  |  | TVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607740 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S | HVAHP144B42S |  |  | HVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607741 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S | YVAHP144B42S |  |  | YVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607742 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S | TVAHR144B32S |  |  | TVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607743 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S | HVAHR144B32S |  |  | HVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607744 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S | YVAHR144B32S |  |  | YVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607745 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S | TVAHR144B42S |  |  | TVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607746 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S | HVAHR144B42S |  |  | HVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607747 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S | YVAHR144B42S |  |  | YVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
202607760 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
202607761 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
202607762 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
202607763 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
202607764 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
202607765 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
202607766 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
202607767 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
202607768 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
202607769 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
202607770 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
202607771 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
202607772 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
202607773 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
202607774 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
202607775 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
202607776 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
202607777 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
202607778 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
202607779 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
202607780 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
202607781 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
202607782 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
202607783 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
202607784 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP096B31S |  | TVAHP336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
202607785 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP096B31S |  | HVAHP336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
202607786 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP096B31S |  | YVAHP336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
202607787 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP096B41S |  | TVAHP336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
202607788 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP096B41S |  | HVAHP336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
202607789 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP096B41S |  | YVAHP336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
202607790 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR096B31S |  | TVAHR336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
202607791 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR096B31S |  | HVAHR336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
202607792 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR096B31S |  | YVAHR336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
202607793 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR096B41S |  | TVAHR336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
202607794 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR096B41S |  | HVAHR336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
202607795 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR096B41S |  | YVAHR336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
202607796 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP096B31S |  | TVAHP336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
202607797 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP096B31S |  | HVAHP336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
202607798 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP096B31S |  | YVAHP336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
202607799 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP096B41S |  | TVAHP336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
202607800 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP096B41S |  | HVAHP336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
202607801 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP096B41S |  | YVAHP336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
202607802 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR096B31S |  | TVAHR336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
202607803 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR096B31S |  | HVAHR336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
202607804 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR096B31S |  | YVAHR336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
202607805 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR096B41S |  | TVAHR336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
202607806 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR096B41S |  | HVAHR336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
202607807 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR096B41S |  | YVAHR336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
202607808 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S | TVAHP144B32S |  |  | TVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607809 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S | HVAHP144B32S |  |  | HVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607810 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S | YVAHP144B32S |  |  | YVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607811 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S | TVAHP144B42S |  |  | TVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607812 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S | HVAHP144B42S |  |  | HVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607813 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S | YVAHP144B42S |  |  | YVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607814 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S | TVAHR144B32S |  |  | TVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607815 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S | HVAHR144B32S |  |  | HVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607816 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S | YVAHR144B32S |  |  | YVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607817 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S | TVAHR144B42S |  |  | TVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607818 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S | HVAHR144B42S |  |  | HVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607819 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S | YVAHR144B42S |  |  | YVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
202607832 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
202607833 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
202607834 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
202607835 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
202607836 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
202607837 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
202607838 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
202607839 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
202607840 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
202607841 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
202607842 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
202607843 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
202607856 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP120B31S |  | TVAHP360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
202607857 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP120B31S |  | HVAHP360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
202607858 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP120B31S |  | YVAHP360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
202607859 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP120B41S |  | TVAHP360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
202607860 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP120B41S |  | HVAHP360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
202607861 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP120B41S |  | YVAHP360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
202607862 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR120B31S |  | TVAHR360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
202607863 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR120B31S |  | HVAHR360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
202607864 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR120B31S |  | YVAHR360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
202607865 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR120B41S |  | TVAHR360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
202607866 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR120B41S |  | HVAHR360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
202607867 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR120B41S |  | YVAHR360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
202608148 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608149 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608150 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608151 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608152 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608153 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608154 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608155 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608156 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608157 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608158 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608159 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
202608172 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202608173 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202608174 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202608175 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202608176 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202608177 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
202608178 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S |  |  | TVAHP288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608179 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S |  |  | HVAHP288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608180 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S |  |  | YVAHP288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608181 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S |  |  | TVAHP288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608182 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S |  |  | HVAHP288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608183 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S |  |  | YVAHP288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608184 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S |  |  | TVAHR288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608185 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S |  |  | HVAHR288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608186 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S |  |  | YVAHR288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608187 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S |  |  | TVAHR288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608188 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S |  |  | HVAHR288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608189 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S |  |  | YVAHR288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
202608202 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S | TVAHP144B32S |  |  | TVAHP312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608203 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S | HVAHP144B32S |  |  | HVAHP312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608204 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S | YVAHP144B32S |  |  | YVAHP312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608205 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S | TVAHP144B42S |  |  | TVAHP312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608206 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S | HVAHP144B42S |  |  | HVAHP312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608207 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S | YVAHP144B42S |  |  | YVAHP312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608208 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S | TVAHR144B32S |  |  | TVAHR312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608209 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S | HVAHR144B32S |  |  | HVAHR312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608210 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S | YVAHR144B32S |  |  | YVAHR312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608211 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S | TVAHR144B42S |  |  | TVAHR312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608212 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S | HVAHR144B42S |  |  | HVAHR312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608213 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S | YVAHR144B42S |  |  | YVAHR312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
202608238 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S | TVAHP144B32S |  |  | TVAHP336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608239 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S | HVAHP144B32S |  |  | HVAHP336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608240 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S | YVAHP144B32S |  |  | YVAHP336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608241 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S | TVAHP144B42S |  |  | TVAHP336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608242 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S | HVAHP144B42S |  |  | HVAHP336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608243 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S | YVAHP144B42S |  |  | YVAHP336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608244 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S | TVAHR144B32S |  |  | TVAHR336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608245 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S | HVAHR144B32S |  |  | HVAHR336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608246 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S | YVAHR144B32S |  |  | YVAHR336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608247 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S | TVAHR144B42S |  |  | TVAHR336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608248 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S | HVAHR144B42S |  |  | HVAHR336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
202608249 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S | YVAHR144B42S |  |  | YVAHR336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
203906821 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906822 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906823 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906824 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906825 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906826 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906827 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906828 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906829 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906830 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906831 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906832 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
203906833 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906835 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906836 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906837 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906838 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906839 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906840 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906841 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906842 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906843 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906844 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906845 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
203906846 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203906847 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203906848 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203906849 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203906850 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203906851 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203906852 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S |  |  | TVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906854 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S |  |  | HVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906855 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S |  |  | YVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906856 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S |  |  | TVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906857 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S |  |  | HVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906858 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S |  |  | YVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906859 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S |  |  | TVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906860 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S |  |  | HVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906861 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S |  |  | YVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906862 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S |  |  | TVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906863 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S |  |  | HVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906864 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S |  |  | YVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
203906878 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S | TVAHP144B32S |  |  | TVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906879 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S | HVAHP144B32S |  |  | HVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906880 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S | YVAHP144B32S |  |  | YVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906881 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S | TVAHP144B42S |  |  | TVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906882 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S | HVAHP144B42S |  |  | HVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906883 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S | YVAHP144B42S |  |  | YVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906884 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S | TVAHR144B32S |  |  | TVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906885 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S | HVAHR144B32S |  |  | HVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906887 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S | YVAHR144B32S |  |  | YVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906888 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S | TVAHR144B42S |  |  | TVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906889 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S | HVAHR144B42S |  |  | HVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906890 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S | YVAHR144B42S |  |  | YVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
203906903 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S | TVAHP144B32S |  |  | TVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906904 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S | HVAHP144B32S |  |  | HVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906905 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S | YVAHP144B32S |  |  | YVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906906 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S | TVAHP144B42S |  |  | TVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906907 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S | HVAHP144B42S |  |  | HVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906909 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S | YVAHP144B42S |  |  | YVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906910 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S | TVAHR144B32S |  |  | TVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906911 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S | HVAHR144B32S |  |  | HVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906912 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S | YVAHR144B32S |  |  | YVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906913 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S | TVAHR144B42S |  |  | TVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906914 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S | HVAHR144B42S |  |  | HVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203906915 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S | YVAHR144B42S |  |  | YVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
203994166 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994167 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994168 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994169 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994170 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994171 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
203994694 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
203994695 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
203994696 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
203994697 | 1/1/2027 | JOHNSON CONTROLS-HITACHI AIR CONDITIONING | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
203994698 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
203994699 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
204268364 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR120B52S |  |  | TVAHR264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268371 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR120B52S | TVAHR120B52S |  | TVAHR384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268384 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR120B52S |  |  | HVAHR264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268389 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR120B52S | HVAHR120B52S |  | HVAHR384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268400 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR120B52S |  |  | YVAHR264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268405 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR120B52S | YVAHR120B52S |  | YVAHR384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268416 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR120B52S |  |  | TVAHR264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268417 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR144B52S |  |  | TVAHR288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268418 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B52S | TVAHR144B52S |  |  | TVAHR312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204268419 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B52S | TVAHR144B52S |  |  | TVAHR336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204268423 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR144B52S | TVAHR144B52S |  | TVAHR432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204268432 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR120B52S |  |  | HVAHR264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268433 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR144B52S |  |  | HVAHR288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268434 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S | HVAHR144B52S |  |  | HVAHR312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204268435 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B52S | HVAHR144B52S |  |  | HVAHR336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204268439 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR144B52S | HVAHR144B52S |  | HVAHR432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204268456 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR120B52S |  |  | YVAHR264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268458 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR144B52S |  |  | YVAHR288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268460 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S | YVAHR144B52S |  |  | YVAHR312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204268462 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B52S | YVAHR144B52S |  |  | YVAHR336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204268470 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR144B52S | YVAHR144B52S |  | YVAHR432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204268481 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP120B52S |  |  | TVAHP264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268489 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP120B52S | TVAHP120B52S |  | TVAHP384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268513 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP120B52S |  |  | HVAHP264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268525 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP120B52S | HVAHP120B52S |  | HVAHP384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268545 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP120B52S |  |  | YVAHP264B52S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
204268553 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP120B52S | YVAHP120B52S |  | YVAHP384B52S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
204268569 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP120B52S |  |  | TVAHP264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268570 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP144B52S |  |  | TVAHP288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268572 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B52S | TVAHP144B52S |  |  | TVAHP312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204268574 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B52S | TVAHP144B52S |  |  | TVAHP336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204268579 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP144B52S | TVAHP144B52S |  | TVAHP432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204268588 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP120B52S |  |  | HVAHP264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268589 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP144B52S |  |  | HVAHP288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268590 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S | HVAHP144B52S |  |  | HVAHP312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204268591 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B52S | HVAHP144B52S |  |  | HVAHP336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204268595 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP144B52S | HVAHP144B52S |  | HVAHP432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204268604 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP120B52S |  |  | YVAHP264B52S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
204268606 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP144B52S |  |  | YVAHP288B52S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
204268607 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S | YVAHP144B52S |  |  | YVAHP312B52S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
204268609 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B52S | YVAHP144B52S |  |  | YVAHP336B52S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
204268616 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP144B52S | YVAHP144B52S |  | YVAHP432B52S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
204269032 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR120B52S |  |  | TVAHR264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269033 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B52S | TVAHR144B52S |  |  | TVAHR288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204269034 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B52S | TVAHR144B52S |  |  | TVAHR312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269035 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B52S | TVAHR144B52S |  |  | TVAHR336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204269048 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR120B52S |  |  | HVAHR264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269049 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B52S | HVAHR144B52S |  |  | HVAHR288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204269050 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B52S | HVAHR144B52S |  |  | HVAHR312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269051 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B52S | HVAHR144B52S |  |  | HVAHR336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204269064 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR120B52S |  |  | YVAHR264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269065 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B52S | YVAHR144B52S |  |  | YVAHR288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204269066 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B52S | YVAHR144B52S |  |  | YVAHR312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269067 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B52S | YVAHR144B52S |  |  | YVAHR336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204269080 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP120B52S |  |  | TVAHP264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269081 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B52S | TVAHP144B52S |  |  | TVAHP288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204269082 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B52S | TVAHP144B52S |  |  | TVAHP312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269083 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B52S | TVAHP144B52S |  |  | TVAHP336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204269096 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP120B52S |  |  | HVAHP264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269097 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B52S | HVAHP144B52S |  |  | HVAHP288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204269098 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B52S | HVAHP144B52S |  |  | HVAHP312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269099 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B52S | HVAHP144B52S |  |  | HVAHP336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204269112 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP120B52S |  |  | YVAHP264B52S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
204269113 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B52S | YVAHP144B52S |  |  | YVAHP288B52S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
204269114 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B52S | YVAHP144B52S |  |  | YVAHP312B52S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
204269115 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B52S | YVAHP144B52S |  |  | YVAHP336B52S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
204442719 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM192HXVAFH |  |  | AM264JXVAFH | Non-Ducted Indoor Units | 252000 | 10.7 | 22.5 | 282000 | 3.56 | 184000 | 2.44 | R-410A | 21
204442720 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH | AM144FXVAFH |  |  | AM288JXVAFH | Non-Ducted Indoor Units | 276000 | 11 | 22.6 | 308000 | 3.54 | 200000 | 2.46 | R-410A | 23
204442721 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH | AM168HXVAFH |  |  | AM312JXVAFH | Non-Ducted Indoor Units | 298000 | 10.8 | 21.6 | 334000 | 3.5 | 218000 | 2.49 | R-410A | 24.8333
204442722 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAFH | AM168HXVAFH |  |  | AM336JXVAFH | Non-Ducted Indoor Units | 320000 | 10.6 | 21.5 | 360000 | 3.46 | 234000 | 2.49 | R-410A | 26.6667
204442723 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192HXVAFH | AM192HXVAFH |  |  | AM384JXVAFH | Non-Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.4 | 268000 | 2.45 | R-410A | 30.5
204442724 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM144FXVAFH | AM192HXVAFH |  | AM408JXVAFH | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
204442734 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM192HXVAJH |  |  | AM264JXVAJH | Non-Ducted Indoor Units | 252000 | 10.7 | 22.5 | 282000 | 3.56 | 184000 | 2.44 | R-410A | 21
204442735 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM144FXVAJH |  |  | AM288JXVAJH | Non-Ducted Indoor Units | 276000 | 11 | 22.6 | 308000 | 3.54 | 200000 | 2.46 | R-410A | 23
204442736 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM168HXVAJH |  |  | AM312JXVAJH | Non-Ducted Indoor Units | 298000 | 10.8 | 21.6 | 334000 | 3.5 | 218000 | 2.49 | R-410A | 24.8333
204442737 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM168HXVAJH | AM168HXVAJH |  |  | AM336JXVAJH | Non-Ducted Indoor Units | 320000 | 10.6 | 21.5 | 360000 | 3.46 | 234000 | 2.49 | R-410A | 26.6667
204442738 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM192HXVAJH | AM192HXVAJH |  |  | AM384JXVAJH | Non-Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.4 | 268000 | 2.45 | R-410A | 30.5
204442739 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM144FXVAJH | AM192HXVAJH |  | AM408JXVAJH | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
9363504 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.7 | 19 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
9363505 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 10.6 | 19.2 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
9363506 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 10.65 | 19.1 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
9363507 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.7 | 19 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
10032811 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) |  | GMV-264WM/B-F(U) | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10035095 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) |  | GMV-288WM/B-F(U) | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
10255984 | 1/1/2027 | INNOVAIR | HMSV-A-CB | VEP072C432Y | VEP096C432Y | VEP096C432Y |  | VEP264C432Y | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10257462 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP096C432Y |  | VEP288C432Y | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
10257465 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y | VEP096C432Y | VEP096C432Y |  | VEP264C432Y | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10267488 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-288WM/B-U(U) | Non-Ducted Indoor Units | 274000 | 10.2 | 20.5 | 308000 | 3.3 | 200000 | 2.2 | R-410A | 22.8333
10267489 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-288WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.35 | 20.25 | 308000 | 3.27 | 200000 | 2.2 | R-410A | 22.8333
10267485 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-264WM/B-U(U) | Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.35 | 186000 | 2.2 | R-410A | 20.8333
10267486 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-264WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.32 | 186000 | 2.2 | R-410A | 20.8333
10267492 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-312WM/B-U(U) | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.35 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10323542 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10323547 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S | TVAHR120B32S |  | TVAHR384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10323558 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10323563 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S | HVAHR120B32S |  | HVAHR384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10323574 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10323579 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S | YVAHR120B32S |  | YVAHR384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10323590 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10323595 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S | TVAHR120B42S |  | TVAHR384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10323606 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10323611 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S | HVAHR120B42S |  | HVAHR384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10323622 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10323627 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S | YVAHR120B42S |  | YVAHR384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10323638 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10323639 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S |  |  | TVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10323640 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S | TVAHR144B32S |  |  | TVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10323641 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S | TVAHR144B32S |  |  | TVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10323645 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S | TVAHR144B32S |  | TVAHR432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10323654 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10323655 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S |  |  | HVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10323656 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S | HVAHR144B32S |  |  | HVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10323657 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S | HVAHR144B32S |  |  | HVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10323661 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S | HVAHR144B32S |  | HVAHR432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10323670 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10323671 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S |  |  | YVAHR288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10323672 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S | YVAHR144B32S |  |  | YVAHR312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10323673 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S | YVAHR144B32S |  |  | YVAHR336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10323677 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S | YVAHR144B32S |  | YVAHR432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10323686 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10323687 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S |  |  | TVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10323688 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S | TVAHR144B42S |  |  | TVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10323689 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S | TVAHR144B42S |  |  | TVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10323693 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S | TVAHR144B42S |  | TVAHR432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10323702 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10323703 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S |  |  | HVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10323704 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S | HVAHR144B42S |  |  | HVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10323705 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S | HVAHR144B42S |  |  | HVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10323709 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S | HVAHR144B42S |  | HVAHR432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10323718 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10323719 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S |  |  | YVAHR288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10323720 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S | YVAHR144B42S |  |  | YVAHR312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10323721 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S | YVAHR144B42S |  |  | YVAHR336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10323725 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S | YVAHR144B42S |  | YVAHR432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10323736 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR120B42S |  |  | TVAHR264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10323737 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B42S | TVAHR144B42S |  |  | TVAHR288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10323738 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B42S | TVAHR144B42S |  |  | TVAHR312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10323739 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B42S | TVAHR144B42S |  |  | TVAHR336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10323752 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR120B42S |  |  | HVAHR264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10323753 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B42S | HVAHR144B42S |  |  | HVAHR288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10323754 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B42S | HVAHR144B42S |  |  | HVAHR312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10323755 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B42S | HVAHR144B42S |  |  | HVAHR336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10323768 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR120B42S |  |  | YVAHR264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10323769 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B42S | YVAHR144B42S |  |  | YVAHR288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10323770 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B42S | YVAHR144B42S |  |  | YVAHR312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10323771 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B42S | YVAHR144B42S |  |  | YVAHR336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10323785 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR120B32S |  |  | TVAHR264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10323786 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR144B32S | TVAHR144B32S |  |  | TVAHR288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10323787 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR168B32S | TVAHR144B32S |  |  | TVAHR312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10323788 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR192B32S | TVAHR144B32S |  |  | TVAHR336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10323801 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR120B32S |  |  | HVAHR264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10323802 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR144B32S | HVAHR144B32S |  |  | HVAHR288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10323803 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR168B32S | HVAHR144B32S |  |  | HVAHR312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10323804 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR192B32S | HVAHR144B32S |  |  | HVAHR336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10323817 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR120B32S |  |  | YVAHR264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10323818 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR144B32S | YVAHR144B32S |  |  | YVAHR288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10323819 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR168B32S | YVAHR144B32S |  |  | YVAHR312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10323820 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR192B32S | YVAHR144B32S |  |  | YVAHR336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10103116 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ144TAYC* |  |  | REYQ264TAYC* | Non-Ducted Indoor Units | 252000 | 11.2 | 20.5 | 282000 | 3.62 | 200000 | 2.22 | R-410A | 21
10103117 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* | REYQ144TAYC* |  |  | REYQ288TAYC* | Non-Ducted Indoor Units | 274000 | 11 | 20.3 | 294000 | 3.51 | 208000 | 2.2 | R-410A | 22.8333
10103118 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* | REYQ168TAYC* |  |  | REYQ312TAYC* | Non-Ducted Indoor Units | 296000 | 10.1 | 19.4 | 320000 | 3.56 | 214000 | 2.09 | R-410A | 24.6667
10103119 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TAYC* | REYQ168TAYC* |  |  | REYQ336TAYC* | Non-Ducted Indoor Units | 320000 | 9.8 | 19 | 338000 | 3.53 | 224000 | 2.12 | R-410A | 26.6667
10103120 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ120TAYC* | REYQ120TAYC* |  | REYQ360TAYC* | Non-Ducted Indoor Units | 342000 | 10.8 | 19.6 | 384000 | 3.56 | 270000 | 2.25 | R-410A | 28.5
10103157 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ144TAYC* |  |  | REYQ264TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.7 | 18.75 | 282000 | 3.41 | 200000 | 2.14 | R-410A | 21
10103158 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* | REYQ144TAYC* |  |  | REYQ288TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.65 | 18.85 | 294000 | 3.35 | 208000 | 2.13 | R-410A | 22.8333
10103159 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYC* | REYQ168TAYC* |  |  | REYQ312TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.9 | 18.2 | 320000 | 3.38 | 214000 | 2.07 | R-410A | 24.6667
10103160 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TAYC* | REYQ168TAYC* |  |  | REYQ336TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 17.9 | 338000 | 3.36 | 224000 | 2.08 | R-410A | 26.6667
10103161 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYC* | REYQ120TAYC* | REYQ120TAYC* |  | REYQ360TAYC* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.65 | 18.6 | 384000 | 3.38 | 270000 | 2.17 | R-410A | 28.5
10206684 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10206698 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10206712 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10206726 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10206740 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10206754 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Non-Ducted Indoor Units | 252000 | 10 | 21.1 | 282000 | 3.7 | 200000 | 2.26 | R-410A | 21
10206768 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10206769 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S |  |  | TVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10206770 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S | TVAHP144B32S |  |  | TVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10206771 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S | TVAHP144B32S |  |  | TVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10206773 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S | TVAHP144B32S |  | TVAHP432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10206782 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10206783 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S |  |  | HVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10206784 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S | HVAHP144B32S |  |  | HVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10206785 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S | HVAHP144B32S |  |  | HVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10206787 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S | HVAHP144B32S |  | HVAHP432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10206796 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10206797 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S |  |  | YVAHP288B32S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10206798 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S | YVAHP144B32S |  |  | YVAHP312B32S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10206799 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S | YVAHP144B32S |  |  | YVAHP336B32S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10206801 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S | YVAHP144B32S |  | YVAHP432B32S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10206810 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10206811 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S |  |  | TVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10206812 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S | TVAHP144B42S |  |  | TVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10206813 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S | TVAHP144B42S |  |  | TVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10206815 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S | TVAHP144B42S |  | TVAHP432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10206824 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10206825 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S |  |  | HVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10206826 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S | HVAHP144B42S |  |  | HVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10206827 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S | HVAHP144B42S |  |  | HVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10206829 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S | HVAHP144B42S |  | HVAHP432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10206838 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Ducted Indoor Units | 252000 | 10.5 | 20.8 | 282000 | 3.56 | 200000 | 2.26 | R-410A | 21
10206839 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S |  |  | YVAHP288B42S | Ducted Indoor Units | 276000 | 9.9 | 20.7 | 308000 | 3.42 | 214000 | 2.24 | R-410A | 23
10206840 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S | YVAHP144B42S |  |  | YVAHP312B42S | Ducted Indoor Units | 298000 | 10 | 19.5 | 334000 | 3.31 | 232000 | 2.12 | R-410A | 24.8333
10206841 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S | YVAHP144B42S |  |  | YVAHP336B42S | Ducted Indoor Units | 320000 | 9.8 | 19.1 | 360000 | 3.32 | 250000 | 2.25 | R-410A | 26.6667
10206843 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S | YVAHP144B42S |  | YVAHP432B42S | Ducted Indoor Units | 400000 | 9.6 | 19 | 460000 | 3.35 | 300000 | 2.19 | R-410A | 33.3333
10207486 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S | TVAHP120B32S |  | TVAHP384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10207488 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S | HVAHP120B32S |  | HVAHP384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10207490 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S | YVAHP120B32S |  | YVAHP384B32S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10207492 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S | TVAHP120B42S |  | TVAHP384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10207494 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S | HVAHP120B42S |  | HVAHP384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10207496 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S | YVAHP120B42S |  | YVAHP384B42S | Non-Ducted Indoor Units | 366000 | 9.6 | 19.6 | 410000 | 3.37 | 276000 | 2.2 | R-410A | 30.5
10207518 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP120B32S |  |  | TVAHP264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10207519 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B32S | TVAHP144B32S |  |  | TVAHP288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10207520 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B32S | TVAHP144B32S |  |  | TVAHP312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10207521 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B32S | TVAHP144B32S |  |  | TVAHP336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10207532 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP120B32S |  |  | HVAHP264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10207533 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B32S | HVAHP144B32S |  |  | HVAHP288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10207534 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B32S | HVAHP144B32S |  |  | HVAHP312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10207535 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B32S | HVAHP144B32S |  |  | HVAHP336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10207546 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP120B32S |  |  | YVAHP264B32S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10207547 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B32S | YVAHP144B32S |  |  | YVAHP288B32S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10207548 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B32S | YVAHP144B32S |  |  | YVAHP312B32S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10207549 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B32S | YVAHP144B32S |  |  | YVAHP336B32S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10207560 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP120B42S |  |  | TVAHP264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10207561 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP144B42S | TVAHP144B42S |  |  | TVAHP288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10207562 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP168B42S | TVAHP144B42S |  |  | TVAHP312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10207563 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP192B42S | TVAHP144B42S |  |  | TVAHP336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10207574 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP120B42S |  |  | HVAHP264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10207575 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP144B42S | HVAHP144B42S |  |  | HVAHP288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10207576 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP168B42S | HVAHP144B42S |  |  | HVAHP312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10207577 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP192B42S | HVAHP144B42S |  |  | HVAHP336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10207588 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP120B42S |  |  | YVAHP264B42S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.25 | 20.95 | 282000 | 3.63 | 200000 | 2.26 | R-410A | 21
10207589 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP144B42S | YVAHP144B42S |  |  | YVAHP288B42S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.7 | 20.05 | 308000 | 3.42 | 214000 | 2.22 | R-410A | 23
10207590 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP168B42S | YVAHP144B42S |  |  | YVAHP312B42S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.85 | 19.9 | 334000 | 3.34 | 232000 | 2.08 | R-410A | 24.8333
10207591 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP192B42S | YVAHP144B42S |  |  | YVAHP336B42S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.65 | 19.95 | 360000 | 3.29 | 250000 | 2.28 | R-410A | 26.6667
10208208 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DZN1 |  |  |  | MV5-2R264DZN1 | Ducted Indoor Units | 248000 | 10.4 | 21 | 282000 | 3.49 | 186000 | 2.3 | R-410A | 20.6667
10208209 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R288DZN1 |  |  |  | MV5-2R288DZN1 | Ducted Indoor Units | 274000 | 9.8 | 20.5 | 298000 | 3.42 | 198000 | 2.26 | R-410A | 22.8333
10208213 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DZN1 |  |  |  | MV5-2R264DZN1 | Non-Ducted Indoor Units | 248000 | 10.7 | 22 | 282000 | 3.52 | 186000 | 2.42 | R-410A | 20.6667
10208214 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R288DZN1 |  |  |  | MV5-2R288DZN1 | Non-Ducted Indoor Units | 274000 | 10.4 | 21 | 298000 | 3.38 | 198000 | 2.2 | R-410A | 22.8333
10208473 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DXN1 |  |  |  | MV5-2R264DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.55 | 21.5 | 282000 | 3.5 | 186000 | 2.36 | R-410A | 20.6667
10208474 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R288DXN1 |  |  |  | MV5-2R288DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.1 | 20.75 | 298000 | 3.4 | 198000 | 2.23 | R-410A | 22.8333
10208478 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R264DZN1 |  |  |  | MV5-2R264DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 248000 | 10.55 | 21.5 | 282000 | 3.5 | 186000 | 2.36 | R-410A | 20.6667
10208479 | 1/1/2027 | MIDEA | HMSR-A-CB | MV5-2R288DZN1 |  |  |  | MV5-2R288DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.1 | 20.75 | 298000 | 3.4 | 198000 | 2.23 | R-410A | 22.8333
9363483 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA144HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA264HDS5-1 | Non-Ducted Indoor Units | 246000 | 9.7 | 19 | 270000 | 3.27 | 178000 | 2.15 | R-410A | 20.5
9363486 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA144HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA264HDS6-1 | Non-Ducted Indoor Units | 246000 | 9.7 | 19 | 270000 | 3.27 | 178000 | 2.15 | R-410A | 20.5
9363494 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.6 | 20.5 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
9363496 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.85 | 20.25 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
9363497 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 11.1 | 20 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
9363498 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.6 | 20.5 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
9363499 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.85 | 20.25 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
9363500 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 11.1 | 20 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
9363501 | 1/1/2027 | BRYANT | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 10.6 | 19.2 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
9302774 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Non-Ducted Indoor Units | 304000 | 10.7 | 19 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
9302775 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Ducted Indoor Units | 304000 | 10.6 | 19.2 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
9302776 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 10.65 | 19.1 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
9302777 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA120HDS6-1 | 38VMA096HDS6-1 |  | 38VMA336HDS6-1 | Non-Ducted Indoor Units | 304000 | 10.7 | 19 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
9989800 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TATJ* | REYQ144TATJ* |  |  | REYQ264TATJ* | Non-Ducted Indoor Units | 252000 | 11.6 | 21.6 | 274000 | 3.55 | 196000 | 2.33 | R-410A | 21
9989801 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TATJ* | REYQ144TATJ* |  |  | REYQ288TATJ* | Non-Ducted Indoor Units | 274000 | 11.4 | 21 | 288000 | 3.51 | 210000 | 2.41 | R-410A | 22.8333
9989802 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TATJ* | REYQ168TATJ* |  |  | REYQ312TATJ* | Non-Ducted Indoor Units | 296000 | 11 | 20.2 | 306000 | 3.57 | 230000 | 2.35 | R-410A | 24.6667
9989803 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TATJ* | REYQ168TATJ* |  |  | REYQ336TATJ* | Non-Ducted Indoor Units | 320000 | 10.3 | 19 | 316000 | 3.53 | 244000 | 2.18 | R-410A | 26.6667
9989804 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TATJ* | REYQ120TATJ* | REYQ120TATJ* |  | REYQ360TATJ* | Non-Ducted Indoor Units | 342000 | 10.8 | 19.6 | 376000 | 3.52 | 258000 | 2.28 | R-410A | 28.5
9989810 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYD* | REYQ144TAYD* |  |  | REYQ264TAYD* | Non-Ducted Indoor Units | 252000 | 11.6 | 21.6 | 274000 | 3.55 | 196000 | 2.33 | R-410A | 21
9989811 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYD* | REYQ144TAYD* |  |  | REYQ288TAYD* | Non-Ducted Indoor Units | 274000 | 11.4 | 21 | 288000 | 3.51 | 210000 | 2.41 | R-410A | 22.8333
9989812 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYD* | REYQ168TAYD* |  |  | REYQ312TAYD* | Non-Ducted Indoor Units | 296000 | 11 | 20.2 | 306000 | 3.57 | 230000 | 2.35 | R-410A | 24.6667
9989813 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TAYD* | REYQ168TAYD* |  |  | REYQ336TAYD* | Non-Ducted Indoor Units | 320000 | 10.3 | 19 | 316000 | 3.53 | 244000 | 2.18 | R-410A | 26.6667
9989814 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYD* | REYQ120TAYD* | REYQ120TAYD* |  | REYQ360TAYD* | Non-Ducted Indoor Units | 342000 | 10.8 | 19.6 | 376000 | 3.52 | 258000 | 2.28 | R-410A | 28.5
9989855 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TATJ* | REYQ144TATJ* |  |  | REYQ264TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.1 | 274000 | 3.37 | 196000 | 2.2 | R-410A | 21
9989856 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYD* | REYQ144TAYD* |  |  | REYQ264TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11 | 20.1 | 274000 | 3.37 | 196000 | 2.2 | R-410A | 21
9989857 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TATJ* | REYQ144TATJ* |  |  | REYQ288TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 19.45 | 288000 | 3.35 | 210000 | 2.27 | R-410A | 22.8333
9989858 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYD* | REYQ144TAYD* |  |  | REYQ288TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.85 | 19.45 | 288000 | 3.35 | 210000 | 2.27 | R-410A | 22.8333
9989859 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TATJ* | REYQ168TATJ* |  |  | REYQ312TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.5 | 19.1 | 306000 | 3.38 | 230000 | 2.22 | R-410A | 24.6667
9989860 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TAYD* | REYQ168TAYD* |  |  | REYQ312TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.5 | 19.1 | 306000 | 3.38 | 230000 | 2.22 | R-410A | 24.6667
9989861 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TATJ* | REYQ168TATJ* |  |  | REYQ336TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.95 | 18.15 | 316000 | 3.36 | 244000 | 2.11 | R-410A | 26.6667
9989862 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TAYD* | REYQ168TAYD* |  |  | REYQ336TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 9.95 | 18.15 | 316000 | 3.36 | 244000 | 2.11 | R-410A | 26.6667
9989863 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TATJ* | REYQ120TATJ* | REYQ120TATJ* |  | REYQ360TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.75 | 19.2 | 376000 | 3.39 | 258000 | 2.16 | R-410A | 28.5
9989864 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TAYD* | REYQ120TAYD* | REYQ120TAYD* |  | REYQ360TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.75 | 19.2 | 376000 | 3.39 | 258000 | 2.16 | R-410A | 28.5
9990037 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ144TATJ* |  |  | RXYQ264TATJ* | Non-Ducted Indoor Units | 252000 | 10.3 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 21
9990038 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* | RXYQ144TATJ* |  |  | RXYQ288TATJ* | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
9990039 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* | RXYQ168TATJ* |  |  | RXYQ312TATJ* | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
9990041 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* | RXYQ120TATJ* |  | RXYQ360TATJ* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 372000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
9990054 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ144TAYD* |  |  | RXYQ264TAYD* | Non-Ducted Indoor Units | 252000 | 10.3 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 21
9990055 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* | RXYQ144TAYD* |  |  | RXYQ288TAYD* | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
9990056 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* | RXYQ168TAYD* |  |  | RXYQ312TAYD* | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
9990058 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ120TAYD* | RXYQ120TAYD* |  | RXYQ360TAYD* | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 372000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
9990075 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* | RXYQ144TATJ* |  |  | RXYQ288TATJ* | Ducted Indoor Units | 274000 | 10.1 | 19.6 | 308000 | 3.3 | 200000 | 2.13 | R-410A | 22.8333
9990076 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* | RXYQ144TAYD* |  |  | RXYQ288TAYD* | Ducted Indoor Units | 274000 | 10.1 | 19.6 | 308000 | 3.3 | 200000 | 2.13 | R-410A | 22.8333
9990103 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ144TATJ* |  |  | RXYQ264TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.95 | 19.95 | 282000 | 3.28 | 186000 | 2.36 | R-410A | 21
9990104 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ144TAYD* |  |  | RXYQ264TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 9.95 | 19.95 | 282000 | 3.28 | 186000 | 2.36 | R-410A | 21
9990105 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* | RXYQ144TATJ* |  |  | RXYQ288TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 19.85 | 308000 | 3.27 | 200000 | 2.1 | R-410A | 22.8333
9990106 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* | RXYQ144TAYD* |  |  | RXYQ288TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.3 | 19.85 | 308000 | 3.27 | 200000 | 2.1 | R-410A | 22.8333
9990107 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TATJ* | RXYQ168TATJ* |  |  | RXYQ312TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.7 | 19.35 | 334000 | 3.25 | 206000 | 2.26 | R-410A | 24.6667
9990108 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TAYD* | RXYQ168TAYD* |  |  | RXYQ312TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.7 | 19.35 | 334000 | 3.25 | 206000 | 2.26 | R-410A | 24.6667
9990111 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TATJ* | RXYQ120TATJ* | RXYQ120TATJ* |  | RXYQ360TATJ* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.95 | 372000 | 3.33 | 250000 | 2.41 | R-410A | 28.5
9990112 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TAYD* | RXYQ120TAYD* | RXYQ120TAYD* |  | RXYQ360TAYD* | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.05 | 18.95 | 372000 | 3.33 | 250000 | 2.41 | R-410A | 28.5
9990307 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA72RLBV1 |  | AOUA264RLBVG1 | Ducted Indoor Units | 252000 | 10.9 | 20.1 | 282000 | 3.4 | 194000 | 2.27 | R-410A | 21
9990308 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA96RLBV1 |  | AOUA288RLBVG1 | Ducted Indoor Units | 274000 | 10.6 | 20.1 | 308000 | 3.31 | 210000 | 2.27 | R-410A | 22.8333
9990314 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA72RLBV1 |  | AOUA264RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 20.45 | 282000 | 3.42 | 194000 | 2.28 | R-410A | 21
9990315 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLBV1 | AOUA96RLBV1 | AOUA96RLBV1 |  | AOUA288RLBVG1 | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 20.45 | 308000 | 3.33 | 210000 | 2.28 | R-410A | 22.8333
9302756 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA144HDS5-1 | 38VMA120HDS5-1 |  |  | 38VMA264HDS5-1 | Non-Ducted Indoor Units | 246000 | 9.7 | 19 | 270000 | 3.27 | 178000 | 2.15 | R-410A | 20.5
9302759 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA144HDS6-1 | 38VMA120HDS6-1 |  |  | 38VMA264HDS6-1 | Non-Ducted Indoor Units | 246000 | 9.7 | 19 | 270000 | 3.27 | 178000 | 2.15 | R-410A | 20.5
9302766 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Ducted Indoor Units | 284000 | 10.6 | 20.5 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
9302767 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.85 | 20.25 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
9302768 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA096HDS5-1 | 38VMA096HDS5-1 |  | 38VMA312HDS5-1 | Non-Ducted Indoor Units | 284000 | 11.1 | 20 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
9302769 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Ducted Indoor Units | 284000 | 10.6 | 20.5 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
9302770 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.85 | 20.25 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
9302771 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS6-1 | 38VMA096HDS6-1 | 38VMA096HDS6-1 |  | 38VMA312HDS6-1 | Non-Ducted Indoor Units | 284000 | 11.1 | 20 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
9302772 | 1/1/2027 | CARRIER | HMSV-A-CB | 38VMA120HDS5-1 | 38VMA120HDS5-1 | 38VMA096HDS5-1 |  | 38VMA336HDS5-1 | Ducted Indoor Units | 304000 | 10.6 | 19.2 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
8657034 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P96ZKMU-A |  | PUHY-P336ZSKMU-A | Non-Ducted Indoor Units | 320000 | 12.5 | 22.6 | 360000 | 3.42 | 268000 | 2.13 | R-410A | 26.6667
8657028 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P72ZKMU-A | PUHY-P72ZKMU-A |  | PUHY-P264ZSKMU-A | Non-Ducted Indoor Units | 252000 | 12.9 | 23.5 | 280000 | 3.62 | 200000 | 2.16 | R-410A | 21
8657030 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P96ZKMU-A | PUHY-P72ZKMU-A |  | PUHY-P288ZSKMU-A | Non-Ducted Indoor Units | 274000 | 12.8 | 23.5 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
8657032 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P72ZKMU-A |  | PUHY-P312ZSKMU-A | Non-Ducted Indoor Units | 296000 | 12.7 | 22.7 | 334000 | 3.59 | 236000 | 2.22 | R-410A | 24.6667
9122314 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 | MV5-H96DZN1 |  | MV5-H312DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.85 | 20.25 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
9122315 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 | MV5-H96DZN1 |  | MV5-H336DZN1 | Mixed Ducted and Non-Ducted Indoor Units | 304000 | 10.65 | 19.1 | 338000 | 3.28 | 224000 | 2.18 | R-410A | 25.3333
9122957 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Non-Ducted Indoor Units | 252000 | 11.2 | 23.8 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
9122958 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Non-Ducted Indoor Units | 276000 | 11.4 | 23.5 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
9122959 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Non-Ducted Indoor Units | 276000 | 10.6 | 23 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
9122960 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Non-Ducted Indoor Units | 298000 | 10.6 | 22.7 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
9122961 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Non-Ducted Indoor Units | 320000 | 11 | 24.6 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
9122962 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1686FT6P-UL |  |  | MMY-AP336S6FT6P-UL | Non-Ducted Indoor Units | 320000 | 10.4 | 22.5 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
9122963 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Non-Ducted Indoor Units | 342000 | 10 | 24 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
9122998 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Ducted Indoor Units | 252000 | 11.4 | 22.5 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
9122999 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Non-Ducted Indoor Units | 252000 | 11.2 | 23.8 | 282000 | 3.4 | 200000 | 2.45 | R-410A | 21
9123000 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Ducted Indoor Units | 252000 | 11.4 | 22.5 | 282000 | 3.5 | 200000 | 2.4 | R-410A | 21
9123001 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Ducted Indoor Units | 276000 | 11.5 | 22 | 308000 | 3.5 | 216000 | 2.4 | R-410A | 23
9123002 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Non-Ducted Indoor Units | 276000 | 11.4 | 23.5 | 308000 | 3.45 | 216000 | 2.5 | R-410A | 23
9123003 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Ducted Indoor Units | 276000 | 11.5 | 22 | 308000 | 3.5 | 216000 | 2.4 | R-410A | 23
9123004 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Ducted Indoor Units | 276000 | 10.3 | 21.5 | 308000 | 3.4 | 216000 | 2.35 | R-410A | 23
9123005 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Non-Ducted Indoor Units | 276000 | 10.6 | 23 | 308000 | 3.35 | 216000 | 2.35 | R-410A | 23
9123006 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Ducted Indoor Units | 276000 | 10.3 | 21.5 | 308000 | 3.4 | 216000 | 2.35 | R-410A | 23
9123007 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Ducted Indoor Units | 298000 | 10.5 | 21.5 | 334000 | 3.32 | 236000 | 2.35 | R-410A | 24.8333
9123008 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Non-Ducted Indoor Units | 298000 | 10.6 | 22.7 | 334000 | 3.3 | 236000 | 2.4 | R-410A | 24.8333
9123009 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Ducted Indoor Units | 298000 | 10.5 | 21.5 | 334000 | 3.32 | 236000 | 2.35 | R-410A | 24.8333
9123010 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Ducted Indoor Units | 320000 | 10.7 | 22.5 | 360000 | 3.35 | 268000 | 2.4 | R-410A | 26.6667
9123011 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Non-Ducted Indoor Units | 320000 | 11 | 24.6 | 360000 | 3.4 | 268000 | 2.4 | R-410A | 26.6667
9123012 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Ducted Indoor Units | 320000 | 10.7 | 22.5 | 360000 | 3.35 | 268000 | 2.4 | R-410A | 26.6667
9123014 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1686FT9P-UL |  |  | MMY-AP336S6FT9P-UL | Non-Ducted Indoor Units | 320000 | 10.4 | 22.5 | 360000 | 3.25 | 268000 | 2.28 | R-410A | 26.6667
9123016 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Ducted Indoor Units | 342000 | 10 | 22 | 386000 | 3.4 | 284000 | 2.3 | R-410A | 28.5
9123017 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Non-Ducted Indoor Units | 342000 | 10 | 24 | 386000 | 3.3 | 284000 | 2.35 | R-410A | 28.5
9123018 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Ducted Indoor Units | 342000 | 10 | 22 | 386000 | 3.4 | 284000 | 2.3 | R-410A | 28.5
9123019 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3846FT6P-UL | Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.3 | 294000 | 2.2 | R-410A | 30.5
9123021 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3846FT9P-UL | Ducted Indoor Units | 366000 | 10 | 21.5 | 410000 | 3.3 | 294000 | 2.2 | R-410A | 30.5
9123022 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP4086FT6P-UL | Ducted Indoor Units | 390000 | 9.9 | 21 | 435000 | 3.3 | 310000 | 2.31 | R-410A | 32.5
9123024 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP4086FT9P-UL | Ducted Indoor Units | 390000 | 9.9 | 21 | 435000 | 3.3 | 310000 | 2.31 | R-410A | 32.5
9123025 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  | MMY-AP4326FT6P-UL | Ducted Indoor Units | 410000 | 9.7 | 20.5 | 460000 | 3.25 | 328000 | 2.3 | R-410A | 34.1667
9123027 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  | MMY-AP4326FT9P-UL | Ducted Indoor Units | 410000 | 9.7 | 20.5 | 460000 | 3.25 | 328000 | 2.3 | R-410A | 34.1667
9123051 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP2646FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.3 | 23.15 | 282000 | 3.45 | 200000 | 2.42 | R-410A | 21
9123052 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP2646FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.3 | 23.15 | 282000 | 3.45 | 200000 | 2.42 | R-410A | 21
9123053 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP2886FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.45 | 22.75 | 308000 | 3.47 | 216000 | 2.45 | R-410A | 23
9123054 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP2886FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.45 | 22.75 | 308000 | 3.47 | 216000 | 2.45 | R-410A | 23
9123055 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1206FT6P-UL |  |  | MMY-AP288S6FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.45 | 22.25 | 308000 | 3.37 | 216000 | 2.35 | R-410A | 23
9123056 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1206FT9P-UL |  |  | MMY-AP288S6FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.45 | 22.25 | 308000 | 3.37 | 216000 | 2.35 | R-410A | 23
9123057 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT6P-UL | MMY-MAP1446FT6P-UL |  |  | MMY-AP3126FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 22.1 | 334000 | 3.31 | 236000 | 2.37 | R-410A | 24.8333
9123058 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1686FT9P-UL | MMY-MAP1446FT9P-UL |  |  | MMY-AP3126FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.55 | 22.1 | 334000 | 3.31 | 236000 | 2.37 | R-410A | 24.8333
9123059 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP0966FT6P-UL |  | MMY-AP3366FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.85 | 23.55 | 360000 | 3.37 | 268000 | 2.4 | R-410A | 26.6667
9123060 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP0966FT9P-UL |  | MMY-AP3366FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.85 | 23.55 | 360000 | 3.37 | 268000 | 2.4 | R-410A | 26.6667
9123063 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3606FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10 | 23 | 386000 | 3.35 | 284000 | 2.32 | R-410A | 28.5
9123064 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3606FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10 | 23 | 386000 | 3.35 | 284000 | 2.32 | R-410A | 28.5
9123065 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP3846FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10 | 22.45 | 410000 | 3.27 | 294000 | 2.27 | R-410A | 30.5
9123066 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP3846FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10 | 22.45 | 410000 | 3.27 | 294000 | 2.27 | R-410A | 30.5
9123067 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT6P-UL | MMY-MAP1446FT6P-UL | MMY-MAP1206FT6P-UL |  | MMY-AP4086FT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.9 | 21.75 | 434000 | 3.26 | 310000 | 2.33 | R-410A | 32.5
9123068 | 1/1/2027 | TOSHIBA CARRIER | HMSR-A-CB | MMY-MAP1446FT9P-UL | MMY-MAP1446FT9P-UL | MMY-MAP1206FT9P-UL |  | MMY-AP4086FT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.9 | 21.75 | 434000 | 3.26 | 310000 | 2.33 | R-410A | 32.5
9121946 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H144DXN1 | MV5-H120DXN1 |  |  | MV5-H264DXN1 | Non-Ducted Indoor Units | 246000 | 9.7 | 19 | 270000 | 3.27 | 178000 | 2.15 | R-410A | 20.5
9121957 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H144DZN1 | MV5-H120DZN1 |  |  | MV5-H264DZN1 | Non-Ducted Indoor Units | 246000 | 9.7 | 19 | 270000 | 3.27 | 178000 | 2.15 | R-410A | 20.5
9121971 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 | MV5-H96DXN1 |  | MV5-H312DXN1 | Non-Ducted Indoor Units | 284000 | 11.1 | 20 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
9121972 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 | MV5-H96DXN1 |  | MV5-H312DXN1 | Ducted Indoor Units | 284000 | 10.6 | 20.5 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
9121973 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 | MV5-H96DXN1 |  | MV5-H336DXN1 | Non-Ducted Indoor Units | 304000 | 10.7 | 19 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
9121974 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H120DXN1 | MV5-H96DXN1 |  | MV5-H336DXN1 | Ducted Indoor Units | 304000 | 10.6 | 19.2 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
9121992 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 | MV5-H96DZN1 |  | MV5-H312DZN1 | Non-Ducted Indoor Units | 284000 | 11.1 | 20 | 320000 | 3.43 | 218000 | 2.3 | R-410A | 23.6667
9121993 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H96DZN1 | MV5-H96DZN1 |  | MV5-H312DZN1 | Ducted Indoor Units | 284000 | 10.6 | 20.5 | 320000 | 3.3 | 218000 | 2.24 | R-410A | 23.6667
9121994 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 | MV5-H96DZN1 |  | MV5-H336DZN1 | Non-Ducted Indoor Units | 304000 | 10.7 | 19 | 338000 | 3.31 | 224000 | 2.2 | R-410A | 25.3333
9121995 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DZN1 | MV5-H120DZN1 | MV5-H96DZN1 |  | MV5-H336DZN1 | Ducted Indoor Units | 304000 | 10.6 | 19.2 | 338000 | 3.25 | 224000 | 2.17 | R-410A | 25.3333
9122298 | 1/1/2027 | MIDEA | HMSV-A-CB | MV5-H120DXN1 | MV5-H96DXN1 | MV5-H96DXN1 |  | MV5-H312DXN1 | Mixed Ducted and Non-Ducted Indoor Units | 284000 | 10.85 | 20.25 | 320000 | 3.36 | 218000 | 2.27 | R-410A | 23.6667
9045762 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
9045764 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
9045786 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
9045788 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
9045810 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
9045812 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Non-Ducted Indoor Units | 276000 | 9.9 | 17.7 | 308000 | 3.57 | 260000 | 2.26 | R-410A | 23
9056984 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31CW | TVAHP096B31CW | TVAHP096B31CW |  | TVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
9056985 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41CW | TVAHP096B41CW | TVAHP096B41CW |  | TVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
9056996 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31CW | HVAHP096B31CW | HVAHP096B31CW |  | HVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
9056997 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41CW | HVAHP096B41CW | HVAHP096B41CW |  | HVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
9057008 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31CW | YVAHP096B31CW | YVAHP096B31CW |  | YVAHP288B31CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
9057009 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41CW | YVAHP096B41CW | YVAHP096B41CW |  | YVAHP288B41CW | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.75 | 16.4 | 308000 | 3.51 | 260000 | 2.25 | R-410A | 23
9085416 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
9085417 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Ducted Indoor Units | 252000 | 12.2 | 21.6 | 282000 | 3.95 | 200000 | 2.92 | R-410A | 21
9085418 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
9085419 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Ducted Indoor Units | 276000 | 11.5 | 21.2 | 308000 | 3.85 | 216000 | 2.92 | R-410A | 23
9085420 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
9085421 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Ducted Indoor Units | 276000 | 11.4 | 20.8 | 308000 | 3.8 | 216000 | 2.83 | R-410A | 23
9085422 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
9085423 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Ducted Indoor Units | 298000 | 11 | 20.9 | 334000 | 3.7 | 236000 | 2.75 | R-410A | 24.8333
9085424 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
9085425 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Ducted Indoor Units | 320000 | 10.6 | 20.7 | 360000 | 3.52 | 268000 | 2.6 | R-410A | 26.6667
9085426 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 386000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
9085427 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Ducted Indoor Units | 342000 | 12 | 21.4 | 386000 | 3.7 | 284000 | 2.75 | R-410A | 28.5
9085428 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
9085429 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Ducted Indoor Units | 366000 | 11.2 | 20.8 | 410000 | 3.58 | 294000 | 2.66 | R-410A | 30.5
9085430 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 435000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
9085431 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Ducted Indoor Units | 390000 | 11.2 | 20.6 | 435000 | 3.4 | 310000 | 2.6 | R-410A | 32.5
9085432 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 435000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
9085433 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Ducted Indoor Units | 390000 | 10.8 | 20.2 | 435000 | 3.35 | 310000 | 2.58 | R-410A | 32.5
9085434 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
9085435 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Ducted Indoor Units | 410000 | 10.4 | 20 | 460000 | 3.35 | 328000 | 2.55 | R-410A | 34.1667
9085437 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4566HT9P-UL | Ducted Indoor Units | 435000 | 10 | 19.8 | 490000 | 3.28 | 350000 | 2.52 | R-410A | 36.25
9085448 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP2646HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.8 | 22.2 | 282000 | 3.8 | 200000 | 2.79 | R-410A | 21
9085449 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP2886HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.3 | 21.85 | 308000 | 3.72 | 216000 | 2.78 | R-410A | 23
9085450 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL |  |  | MMY-AP288S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.15 | 21.5 | 308000 | 3.65 | 216000 | 2.7 | R-410A | 23
9085451 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL |  |  | MMY-AP3126HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 21.5 | 334000 | 3.56 | 236000 | 2.67 | R-410A | 24.8333
9085452 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1686HT9P-UL |  |  | MMY-AP3366HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 21.35 | 360000 | 3.43 | 268000 | 2.53 | R-410A | 26.6667
9085453 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3606HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.8 | 21.9 | 386000 | 3.61 | 284000 | 2.66 | R-410A | 28.5
9085454 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP3846HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.9 | 21.3 | 410000 | 3.49 | 294000 | 2.6 | R-410A | 30.5
9085455 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1446HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4086HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.8 | 21 | 434000 | 3.39 | 310000 | 2.55 | R-410A | 32.5
9085456 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1206HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP408S6HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.5 | 20.6 | 434000 | 3.32 | 310000 | 2.53 | R-410A | 32.5
9085457 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMY-MAP1686HT9P-UL | MMY-MAP1446HT9P-UL | MMY-MAP1206HT9P-UL |  | MMY-AP4326HT9P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.2 | 20.65 | 460000 | 3.31 | 328000 | 2.51 | R-410A | 34.1667
8989560 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Non-Ducted Indoor Units | 252000 | 11.4 | 22.8 | 282000 | 3.65 | 200000 | 2.66 | R-410A | 21
8989561 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Non-Ducted Indoor Units | 276000 | 11.1 | 22.5 | 308000 | 3.6 | 216000 | 2.65 | R-410A | 23
8989562 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Non-Ducted Indoor Units | 276000 | 10.9 | 22.2 | 308000 | 3.5 | 216000 | 2.58 | R-410A | 23
8989563 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Non-Ducted Indoor Units | 298000 | 10.4 | 22.1 | 334000 | 3.42 | 236000 | 2.6 | R-410A | 24.8333
8989564 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Non-Ducted Indoor Units | 320000 | 10.3 | 22 | 360000 | 3.35 | 268000 | 2.46 | R-410A | 26.6667
8989565 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Non-Ducted Indoor Units | 342000 | 11.6 | 22.4 | 386000 | 3.52 | 284000 | 2.58 | R-410A | 28.5
8989576 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Ducted Indoor Units | 252000 | 12.2 | 21.6 | 282000 | 3.95 | 200000 | 2.92 | R-410A | 21
8989577 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Ducted Indoor Units | 276000 | 11.5 | 21.2 | 308000 | 3.85 | 216000 | 2.92 | R-410A | 23
8989578 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Ducted Indoor Units | 276000 | 11.4 | 20.8 | 308000 | 3.8 | 216000 | 2.83 | R-410A | 23
8989579 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Ducted Indoor Units | 298000 | 11 | 20.9 | 334000 | 3.7 | 236000 | 2.75 | R-410A | 24.8333
8989580 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Ducted Indoor Units | 320000 | 10.6 | 20.7 | 360000 | 3.52 | 268000 | 2.6 | R-410A | 26.6667
8989617 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP2646HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 11.8 | 22.2 | 282000 | 3.8 | 200000 | 2.79 | R-410A | 21
8989618 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1446HT6P-UL |  |  | MMY-AP2886HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.3 | 21.85 | 308000 | 3.72 | 216000 | 2.78 | R-410A | 23
8989619 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1206HT6P-UL |  |  | MMY-AP288S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.15 | 21.5 | 308000 | 3.65 | 216000 | 2.7 | R-410A | 23
8989620 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1446HT6P-UL |  |  | MMY-AP3126HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 10.7 | 21.5 | 334000 | 3.56 | 236000 | 2.67 | R-410A | 24.8333
8989621 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1686HT6P-UL |  |  | MMY-AP3366HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.45 | 21.35 | 360000 | 3.43 | 268000 | 2.53 | R-410A | 26.6667
8989623 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Ducted Indoor Units | 342000 | 12 | 21.4 | 386000 | 3.7 | 284000 | 2.75 | R-410A | 28.5
8989624 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Non-Ducted Indoor Units | 366000 | 10.6 | 21.8 | 410000 | 3.4 | 294000 | 2.55 | R-410A | 30.5
8989625 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.4 | 21.4 | 435000 | 3.38 | 310000 | 2.5 | R-410A | 32.5
8989626 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Non-Ducted Indoor Units | 390000 | 10.2 | 21 | 435000 | 3.3 | 310000 | 2.48 | R-410A | 32.5
8989627 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Non-Ducted Indoor Units | 410000 | 10 | 21.3 | 460000 | 3.28 | 328000 | 2.48 | R-410A | 34.1667
8989629 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP3606HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.8 | 21.9 | 386000 | 3.61 | 284000 | 2.66 | R-410A | 28.5
8989630 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Ducted Indoor Units | 366000 | 11.2 | 20.8 | 410000 | 3.58 | 294000 | 2.66 | R-410A | 30.5
8989631 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Ducted Indoor Units | 390000 | 11.2 | 20.6 | 435000 | 3.4 | 310000 | 2.6 | R-410A | 32.5
8989632 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Ducted Indoor Units | 390000 | 10.8 | 20.2 | 435000 | 3.35 | 310000 | 2.58 | R-410A | 32.5
8989633 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Ducted Indoor Units | 410000 | 10.4 | 20 | 460000 | 3.35 | 328000 | 2.55 | R-410A | 34.1667
8989634 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1686HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP4566HT6P-UL | Ducted Indoor Units | 435000 | 10 | 19.8 | 490000 | 3.28 | 350000 | 2.52 | R-410A | 36.25
8989635 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP3846HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 10.9 | 21.3 | 410000 | 3.49 | 294000 | 2.6 | R-410A | 30.5
8989636 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1446HT6P-UL | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP4086HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.8 | 21 | 434000 | 3.39 | 310000 | 2.55 | R-410A | 32.5
8989637 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1206HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP408S6HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 10.5 | 20.6 | 434000 | 3.32 | 310000 | 2.53 | R-410A | 32.5
8989638 | 1/1/2027 | TOSHIBA CARRIER | HMSV-A-CB | MMYMAP1686HT6P-UL | MMYMAP1446HT6P-UL | MMYMAP1206HT6P-UL |  | MMY-AP4326HT6P-UL | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.2 | 20.65 | 460000 | 3.31 | 328000 | 2.51 | R-410A | 34.1667
8715619 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP096B31S |  | YVAHP336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
8715620 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP096B41S |  | YVAHP336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
8715625 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR096B31S |  | YVAHR336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
8715626 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR096B41S |  | YVAHR336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
8715631 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP096B31S |  | HVAHP336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
8715632 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP096B41S |  | HVAHP336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
8715637 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR096B31S |  | HVAHR336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
8715638 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR096B41S |  | HVAHR336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
8715643 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP096B31S |  | TVAHP336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
8715644 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP096B41S |  | TVAHP336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
8715649 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR096B31S |  | TVAHR336B31LM | Non-Ducted Indoor Units | 320000 | 10.5 | 17.7 | 344000 | 3.51 | 266000 | 2.12 | R-410A | 26.6667
8715650 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR096B41S |  | TVAHR336B41LM | Non-Ducted Indoor Units | 320000 | 10 | 17.7 | 344000 | 3.51 | 266000 | 2.1 | R-410A | 26.6667
8715655 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP096B31S |  | YVAHP336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
8715656 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP096B41S |  | YVAHP336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
8715657 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP120B31S |  | YVAHP360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
8715658 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP120B41S |  | YVAHP360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
8715661 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR096B31S |  | YVAHR336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
8715662 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR096B41S |  | YVAHR336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
8715663 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR120B31S |  | YVAHR360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
8715664 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR120B41S |  | YVAHR360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
8715667 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP096B31S |  | HVAHP336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
8715668 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP096B41S |  | HVAHP336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
8715669 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP120B31S |  | HVAHP360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
8715670 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP120B41S |  | HVAHP360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
8715673 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR096B31S |  | HVAHR336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
8715674 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR096B41S |  | HVAHR336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
8715675 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR120B31S |  | HVAHR360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
8715676 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR120B41S |  | HVAHR360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
8715679 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP096B31S |  | TVAHP336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
8715680 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP096B41S |  | TVAHP336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
8715681 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP120B31S |  | TVAHP360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
8715682 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP120B41S |  | TVAHP360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
8715685 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR096B31S |  | TVAHR336B31LM | Ducted Indoor Units | 320000 | 10.8 | 18.6 | 344000 | 3.54 | 266000 | 2.53 | R-410A | 26.6667
8715686 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR096B41S |  | TVAHR336B41LM | Ducted Indoor Units | 320000 | 10.3 | 17.7 | 344000 | 3.39 | 266000 | 2.45 | R-410A | 26.6667
8715687 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR120B31S |  | TVAHR360B31LM | Ducted Indoor Units | 344000 | 10.2 | 18.7 | 366000 | 3.53 | 268000 | 2.47 | R-410A | 28.6667
8715688 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR120B41S |  | TVAHR360B41LM | Ducted Indoor Units | 344000 | 9.7 | 17.8 | 366000 | 3.38 | 268000 | 2.38 | R-410A | 28.6667
8715691 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP096B31S |  | YVAHP336B31LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.65 | 18.15 | 344000 | 3.52 | 266000 | 2.32 | R-410A | 26.6667
8715692 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP096B41S |  | YVAHP336B41LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.15 | 17.7 | 344000 | 3.45 | 266000 | 2.27 | R-410A | 26.6667
8715693 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP120B31S |  | YVAHP360B31LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 18.45 | 366000 | 3.44 | 268000 | 2.26 | R-410A | 28.6667
8715694 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP120B41S | YVAHP120B41S |  | YVAHP360B41LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.7 | 17.65 | 366000 | 3.36 | 268000 | 2.19 | R-410A | 28.6667
8715697 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR096B31S |  | YVAHR336B31LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.65 | 18.15 | 344000 | 3.52 | 266000 | 2.32 | R-410A | 26.6667
8715698 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR096B41S |  | YVAHR336B41LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.15 | 17.7 | 344000 | 3.45 | 266000 | 2.27 | R-410A | 26.6667
8715699 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR120B31S |  | YVAHR360B31LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 18.45 | 366000 | 3.44 | 268000 | 2.26 | R-410A | 28.6667
8715700 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR120B41S | YVAHR120B41S |  | YVAHR360B41LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.7 | 17.65 | 366000 | 3.36 | 268000 | 2.19 | R-410A | 28.6667
8715703 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP096B31S |  | HVAHP336B31LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.65 | 18.15 | 344000 | 3.52 | 266000 | 2.32 | R-410A | 26.6667
8715704 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP096B41S |  | HVAHP336B41LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.15 | 17.7 | 344000 | 3.45 | 266000 | 2.27 | R-410A | 26.6667
8715705 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP120B31S |  | HVAHP360B31LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 18.45 | 366000 | 3.44 | 268000 | 2.26 | R-410A | 28.6667
8715706 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP120B41S | HVAHP120B41S |  | HVAHP360B41LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.7 | 17.65 | 366000 | 3.36 | 268000 | 2.19 | R-410A | 28.6667
8715709 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR096B31S |  | HVAHR336B31LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.65 | 18.15 | 344000 | 3.52 | 266000 | 2.32 | R-410A | 26.6667
8715710 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR096B41S |  | HVAHR336B41LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.15 | 17.7 | 344000 | 3.45 | 266000 | 2.27 | R-410A | 26.6667
8715711 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR120B31S |  | HVAHR360B31LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 18.45 | 366000 | 3.44 | 268000 | 2.26 | R-410A | 28.6667
8715712 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR120B41S | HVAHR120B41S |  | HVAHR360B41LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.7 | 17.65 | 366000 | 3.36 | 268000 | 2.19 | R-410A | 28.6667
8715715 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP096B31S |  | TVAHP336B31LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.65 | 18.15 | 344000 | 3.52 | 266000 | 2.32 | R-410A | 26.6667
8715716 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP096B41S |  | TVAHP336B41LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.15 | 17.7 | 344000 | 3.45 | 266000 | 2.27 | R-410A | 26.6667
8715717 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP120B31S |  | TVAHP360B31LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 18.45 | 366000 | 3.44 | 268000 | 2.26 | R-410A | 28.6667
8715718 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP120B41S | TVAHP120B41S |  | TVAHP360B41LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.7 | 17.65 | 366000 | 3.36 | 268000 | 2.19 | R-410A | 28.6667
8715721 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR096B31S |  | TVAHR336B31LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.65 | 18.15 | 344000 | 3.52 | 266000 | 2.32 | R-410A | 26.6667
8715722 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR096B41S |  | TVAHR336B41LM | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.15 | 17.7 | 344000 | 3.45 | 266000 | 2.27 | R-410A | 26.6667
8715723 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR120B31S |  | TVAHR360B31LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.2 | 18.45 | 366000 | 3.44 | 268000 | 2.26 | R-410A | 28.6667
8715724 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR120B41S | TVAHR120B41S |  | TVAHR360B41LM | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.7 | 17.65 | 366000 | 3.36 | 268000 | 2.19 | R-410A | 28.6667
7041897 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU | RXYQ144TTJU |  |  | RXYQ288TTJU | Ducted Indoor Units | 274000 | 10.5 | 19.3 | 308000 | 3.31 | 200000 | 2.13 | R-410A | 22.8333
7041898 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN | RXYQ144TYDN |  |  | RXYQ288TYDN | Ducted Indoor Units | 274000 | 10.5 | 19.3 | 308000 | 3.31 | 200000 | 2.13 | R-410A | 22.8333
7041899 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU | RXYQ144TTJU |  |  | RXYQ288TTJU | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
7041900 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN | RXYQ144TYDN |  |  | RXYQ288TYDN | Non-Ducted Indoor Units | 274000 | 10.5 | 20.1 | 308000 | 3.25 | 200000 | 2.07 | R-410A | 22.8333
7042723 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU | RXYQ144TTJU |  |  | RXYQ288TTJU | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 19.7 | 308000 | 3.28 | 200000 | 2.1 | R-410A | 22.8333
7042724 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN | RXYQ144TYDN |  |  | RXYQ288TYDN | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.5 | 19.7 | 308000 | 3.28 | 200000 | 2.1 | R-410A | 22.8333
7064658 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU | RXYQ168TTJU |  |  | RXYQ312TTJU | Ducted Indoor Units | 296000 | 9.8 | 18.8 | 334000 | 3.26 | 206000 | 2.2 | R-410A | 24.6667
7064659 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN | RXYQ168TYDN |  |  | RXYQ312TYDN | Ducted Indoor Units | 296000 | 9.8 | 18.8 | 334000 | 3.26 | 206000 | 2.2 | R-410A | 24.6667
7064660 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU | RXYQ168TTJU |  |  | RXYQ312TTJU | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
7064661 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN | RXYQ168TYDN |  |  | RXYQ312TYDN | Non-Ducted Indoor Units | 296000 | 9.8 | 19.9 | 334000 | 3.3 | 206000 | 2.32 | R-410A | 24.6667
7064662 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ120TTJU | RXYQ120TTJU |  | RXYQ360TTJU | Ducted Indoor Units | 342000 | 10.9 | 18.5 | 384000 | 3.25 | 250000 | 2.41 | R-410A | 28.5
7064663 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ120TYDN | RXYQ120TYDN |  | RXYQ360TYDN | Ducted Indoor Units | 342000 | 10.9 | 18.5 | 384000 | 3.25 | 250000 | 2.41 | R-410A | 28.5
7064664 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ120TTJU | RXYQ120TTJU |  | RXYQ360TTJU | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 384000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
7064665 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ120TYDN | RXYQ120TYDN |  | RXYQ360TYDN | Non-Ducted Indoor Units | 342000 | 10.3 | 19.4 | 384000 | 3.46 | 250000 | 2.47 | R-410A | 28.5
7064666 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU | RXYQ120TTJU | RXYQ168TTJU |  | RXYQ384TTJU | Ducted Indoor Units | 364000 | 10 | 18.5 | 410000 | 3.26 | 274000 | 2.28 | R-410A | 30.3333
7064667 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN | RXYQ120TYDN | RXYQ168TYDN |  | RXYQ384TYDN | Ducted Indoor Units | 364000 | 10 | 18.5 | 410000 | 3.26 | 274000 | 2.28 | R-410A | 30.3333
7064672 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TTJU | RXYQ168TTJU |  |  | RXYQ312TTJU | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.8 | 19.35 | 334000 | 3.28 | 206000 | 2.26 | R-410A | 24.6667
7064673 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ144TYDN | RXYQ168TYDN |  |  | RXYQ312TYDN | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 9.8 | 19.35 | 334000 | 3.28 | 206000 | 2.26 | R-410A | 24.6667
7064674 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ120TTJU | RXYQ120TTJU |  | RXYQ360TTJU | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.6 | 18.95 | 384000 | 3.35 | 250000 | 2.44 | R-410A | 28.5
7064675 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ120TYDN | RXYQ120TYDN |  | RXYQ360TYDN | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 10.6 | 18.95 | 384000 | 3.35 | 250000 | 2.44 | R-410A | 28.5
7064676 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TTJU | RXYQ120TTJU | RXYQ168TTJU |  | RXYQ384TTJU | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.75 | 19.45 | 410000 | 3.28 | 274000 | 2.28 | R-410A | 30.3333
7064677 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ96TYDN | RXYQ120TYDN | RXYQ168TYDN |  | RXYQ384TYDN | Mixed Ducted and Non-Ducted Indoor Units | 364000 | 9.75 | 19.45 | 410000 | 3.28 | 274000 | 2.28 | R-410A | 30.3333
7064758 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ144TYDN |  |  | RXYQ264TYDN | Non-Ducted Indoor Units | 250000 | 10.9 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 20.8333
7064761 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ144TTJU |  |  | RXYQ264TTJU | Ducted Indoor Units | 250000 | 10.5 | 19.3 | 282000 | 3.35 | 186000 | 2.3 | R-410A | 20.8333
7064762 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ144TYDN |  |  | RXYQ264TYDN | Ducted Indoor Units | 250000 | 10.5 | 19.3 | 282000 | 3.35 | 186000 | 2.3 | R-410A | 20.8333
7064763 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ144TTJU |  |  | RXYQ264TTJU | Non-Ducted Indoor Units | 250000 | 10.9 | 20.3 | 282000 | 3.33 | 186000 | 2.43 | R-410A | 20.8333
7064764 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TTJU | RXYQ144TTJU |  |  | RXYQ264TTJU | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 10.7 | 19.8 | 282000 | 3.34 | 186000 | 2.36 | R-410A | 20.8333
7064765 | 1/1/2027 | DAIKIN | HMSV-A-CB | RXYQ120TYDN | RXYQ144TYDN |  |  | RXYQ264TYDN | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 10.7 | 19.8 | 282000 | 3.34 | 186000 | 2.36 | R-410A | 20.8333
7089785 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM120FXVAFH | AM144FXVAFH |  | AM336FXVAFH | Non-Ducted Indoor Units | 320000 | 10.2 | 20.5 | 360000 | 3.27 | 234000 | 2.39 | R-410A | 26.6667
7089786 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM120FXVAJH | AM144FXVAJH |  | AM336FXVAJH | Non-Ducted Indoor Units | 320000 | 10.2 | 20.5 | 360000 | 3.27 | 234000 | 2.39 | R-410A | 26.6667
7133818 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM120FXVAFR | AM144FXVAFR |  | AM336FXVAFR | Non-Ducted Indoor Units | 320000 | 10.2 | 20.5 | 360000 | 3.27 | 234000 | 2.39 | R-410A | 26.6667
7133819 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM120FXVAJR | AM144FXVAJR |  | AM336FXVAJR | Non-Ducted Indoor Units | 320000 | 10.2 | 20.5 | 360000 | 3.27 | 234000 | 2.39 | R-410A | 26.6667
7490379 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P72TKMU-U | PUHY-P72TKMU-U |  | PUHY-P264TSKMU-U | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
7490381 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P72TKMU-U | PUHY-P72TKMU-U |  | PUHY-P264TSKMU-U | Ducted Indoor Units | 252000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 21
7490382 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P72YKMU-U | PUHY-P72YKMU-U |  | PUHY-P264YSKMU-U | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
7490384 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P72YKMU-U | PUHY-P72YKMU-U |  | PUHY-P264YSKMU-U | Ducted Indoor Units | 250000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 20.8333
7490385 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P96TKMU-U | PUHY-P72TKMU-U |  | PUHY-P288TSKMU-U | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
7490387 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P96TKMU-U | PUHY-P72TKMU-U |  | PUHY-P288TSKMU-U | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
7490388 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P96YKMU-U | PUHY-P72YKMU-U |  | PUHY-P288YSKMU-U | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
7490390 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P96YKMU-U | PUHY-P72YKMU-U |  | PUHY-P288YSKMU-U | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
7490392 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P120TKMU-U | PUHY-P72TKMU-U |  | PUHY-P312TSKMU-U | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
7490394 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P120TKMU-U | PUHY-P72TKMU-U |  | PUHY-P312TSKMU-U | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
7490395 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P120YKMU-U | PUHY-P72YKMU-U |  | PUHY-P312YSKMU-U | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
7490397 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P120YKMU-U | PUHY-P72YKMU-U |  | PUHY-P312YSKMU-U | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
7490399 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P120TKMU-U | PUHY-P96TKMU-U |  | PUHY-P336TSKMU-U | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
7490400 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P120TKMU-U | PUHY-P96TKMU-U |  | PUHY-P336TSKMU-U | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
7490402 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P120YKMU-U | PUHY-P96YKMU-U |  | PUHY-P336YSKMU-U | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
7490404 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P120YKMU-U | PUHY-P96YKMU-U |  | PUHY-P336YSKMU-U | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
7490406 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-U | PUHY-P120TKMU-U | PUHY-P120TKMU-U |  | PUHY-P360TSKMU-U | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
7490412 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-U | PUHY-P120YKMU-U | PUHY-P120YKMU-U |  | PUHY-P360YSKMU-U | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
7490454 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-U | PURY-P120TKMU-U |  |  | PURY-P264TSKMU-U | Ducted Indoor Units | 250000 | 11 | 17.7 | 280000 | 3.4 | 200000 | 2.36 | R-410A | 20.8333
7490455 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-U | PURY-P120TKMU-U |  |  | PURY-P264TSKMU-U | Non-Ducted Indoor Units | 250000 | 11 | 18.4 | 280000 | 3.25 | 200000 | 2.08 | R-410A | 20.8333
7490457 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-U | PURY-P120YKMU-U |  |  | PURY-P264YSKMU-U | Ducted Indoor Units | 250000 | 11 | 17.7 | 280000 | 3.4 | 200000 | 2.36 | R-410A | 20.8333
7490458 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-U | PURY-P120YKMU-U |  |  | PURY-P264YSKMU-U | Non-Ducted Indoor Units | 250000 | 11 | 18.4 | 280000 | 3.25 | 200000 | 2.08 | R-410A | 20.8333
7490459 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-U | PURY-P144TKMU-U |  |  | PURY-P288TSKMU-U | Ducted Indoor Units | 274000 | 11.2 | 17.6 | 304000 | 3.41 | 216000 | 2.36 | R-410A | 22.8333
7490461 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-U | PURY-P144YKMU-U |  |  | PURY-P288YSKMU-U | Ducted Indoor Units | 274000 | 11.2 | 17.6 | 304000 | 3.41 | 216000 | 2.36 | R-410A | 22.8333
7505375 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ288PBTJ | Non-Ducted Indoor Units | 274000 | 10.7 | 19 | 308000 | 3.35 | 208000 | 2.4 | R-410A | 22.8333
7505376 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ288PBTJ | Ducted Indoor Units | 274000 | 10.7 | 17.5 | 308000 | 3.4 | 208000 | 2.35 | R-410A | 22.8333
7505377 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ288PBYD | Non-Ducted Indoor Units | 274000 | 10.7 | 19 | 308000 | 3.35 | 208000 | 2.4 | R-410A | 22.8333
7505378 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ288PBYD | Ducted Indoor Units | 274000 | 10.7 | 17.5 | 308000 | 3.4 | 208000 | 2.35 | R-410A | 22.8333
7505399 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ96PBTJ |  | REYQ264PBTJ | Non-Ducted Indoor Units | 250000 | 10.8 | 18.7 | 282000 | 3.4 | 190000 | 2.4 | R-410A | 20.8333
7505400 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ96PBTJ |  | REYQ264PBTJ | Ducted Indoor Units | 250000 | 11.3 | 18.1 | 282000 | 3.3 | 190000 | 2.3 | R-410A | 20.8333
7505401 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ96PBYD |  | REYQ264PBYD | Non-Ducted Indoor Units | 250000 | 10.8 | 18.7 | 282000 | 3.4 | 190000 | 2.4 | R-410A | 20.8333
7505402 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ96PBYD |  | REYQ264PBYD | Ducted Indoor Units | 250000 | 11.3 | 18.1 | 282000 | 3.3 | 190000 | 2.3 | R-410A | 20.8333
7505419 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ96PBTJ |  | REYQ264PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11.05 | 18.4 | 282000 | 3.35 | 190000 | 2.35 | R-410A | 20.8333
7505420 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ96PBYD |  | REYQ264PBYD | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11.05 | 18.4 | 282000 | 3.35 | 190000 | 2.35 | R-410A | 20.8333
7505421 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ288PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.7 | 18.25 | 308000 | 3.37 | 208000 | 2.37 | R-410A | 22.8333
7505422 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ288PBYD | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.7 | 18.25 | 308000 | 3.37 | 208000 | 2.37 | R-410A | 22.8333
7505424 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ312PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.25 | 16.55 | 334000 | 3.28 | 224000 | 2.25 | R-410A | 24.6667
7505425 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ312PBYD | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.25 | 16.55 | 334000 | 3.28 | 224000 | 2.25 | R-410A | 24.6667
7628337 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ144TTJU |  |  | REYQ264TTJU | Ducted Indoor Units | 246000 | 10.5 | 19.6 | 276000 | 3.38 | 196000 | 2.26 | R-410A | 20.5
7628340 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ144TYDN |  |  | REYQ264TYDN | Ducted Indoor Units | 246000 | 10.5 | 19.6 | 276000 | 3.38 | 196000 | 2.26 | R-410A | 20.5
7628572 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ144TTJU |  |  | REYQ264TTJU | Non-Ducted Indoor Units | 246000 | 11.8 | 21.6 | 276000 | 3.55 | 196000 | 2.42 | R-410A | 20.5
7628574 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ144TYDN |  |  | REYQ264TYDN | Non-Ducted Indoor Units | 246000 | 11.8 | 21.6 | 276000 | 3.55 | 196000 | 2.42 | R-410A | 20.5
7628576 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU | REYQ144TTJU |  |  | REYQ288TTJU | Non-Ducted Indoor Units | 268000 | 11.8 | 21.4 | 300000 | 3.51 | 210000 | 2.41 | R-410A | 22.3333
7628579 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN | REYQ144TYDN |  |  | REYQ288TYDN | Non-Ducted Indoor Units | 268000 | 11.8 | 21.4 | 300000 | 3.51 | 210000 | 2.41 | R-410A | 22.3333
7628581 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU | REYQ168TTJU |  |  | REYQ312TTJU | Non-Ducted Indoor Units | 290000 | 11.3 | 20.2 | 326000 | 3.56 | 230000 | 2.41 | R-410A | 24.1667
7628585 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TTJU | REYQ168TTJU |  |  | REYQ336TTJU | Non-Ducted Indoor Units | 312000 | 10.7 | 19 | 352000 | 3.52 | 262000 | 2.18 | R-410A | 26
7628588 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TYDN | REYQ168TYDN |  |  | REYQ336TYDN | Non-Ducted Indoor Units | 312000 | 10.7 | 19 | 352000 | 3.52 | 262000 | 2.18 | R-410A | 26
7628589 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ120TTJU | REYQ120TTJU |  | REYQ360TTJU | Non-Ducted Indoor Units | 334000 | 10.8 | 19.6 | 376000 | 3.51 | 264000 | 2.42 | R-410A | 27.8333
7628592 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ120TYDN | REYQ120TYDN |  | REYQ360TYDN | Non-Ducted Indoor Units | 334000 | 10.8 | 19.6 | 376000 | 3.51 | 264000 | 2.42 | R-410A | 27.8333
7628644 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU | REYQ144TTJU |  |  | REYQ288TTJU | Ducted Indoor Units | 268000 | 10.9 | 19.6 | 300000 | 3.26 | 210000 | 2.24 | R-410A | 22.3333
7628647 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN | REYQ144TYDN |  |  | REYQ288TYDN | Ducted Indoor Units | 268000 | 10.9 | 19.6 | 300000 | 3.26 | 210000 | 2.24 | R-410A | 22.3333
7628657 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ120TTJU | REYQ120TTJU |  | REYQ360TTJU | Ducted Indoor Units | 334000 | 11 | 20.1 | 376000 | 3.31 | 264000 | 2.17 | R-410A | 27.8333
7628659 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ120TYDN | REYQ120TYDN |  | REYQ360TYDN | Ducted Indoor Units | 334000 | 11 | 20.1 | 376000 | 3.31 | 264000 | 2.17 | R-410A | 27.8333
7629610 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ144TTJU |  |  | REYQ264TTJU | Mixed Ducted and Non-Ducted Indoor Units | 246000 | 11.15 | 20.6 | 276000 | 3.46 | 196000 | 2.34 | R-410A | 20.5
7629612 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ144TYDN |  |  | REYQ264TYDN | Mixed Ducted and Non-Ducted Indoor Units | 246000 | 11.15 | 20.6 | 276000 | 3.46 | 196000 | 2.34 | R-410A | 20.5
7629614 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU | REYQ144TTJU |  |  | REYQ288TTJU | Mixed Ducted and Non-Ducted Indoor Units | 268000 | 11.35 | 20.5 | 300000 | 3.38 | 210000 | 2.32 | R-410A | 22.3333
7629617 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN | REYQ144TYDN |  |  | REYQ288TYDN | Mixed Ducted and Non-Ducted Indoor Units | 268000 | 11.35 | 20.5 | 300000 | 3.38 | 210000 | 2.32 | R-410A | 22.3333
7629619 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TTJU | REYQ168TTJU |  |  | REYQ312TTJU | Mixed Ducted and Non-Ducted Indoor Units | 290000 | 10.95 | 19.6 | 326000 | 3.39 | 230000 | 2.32 | R-410A | 24.1667
7629622 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TTJU | REYQ168TTJU |  |  | REYQ336TTJU | Mixed Ducted and Non-Ducted Indoor Units | 312000 | 10.35 | 18.6 | 352000 | 3.36 | 262000 | 2.12 | R-410A | 26
7629623 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ168TYDN | REYQ168TYDN |  |  | REYQ336TYDN | Mixed Ducted and Non-Ducted Indoor Units | 312000 | 10.35 | 18.6 | 352000 | 3.36 | 262000 | 2.12 | R-410A | 26
7629626 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TTJU | REYQ120TTJU | REYQ120TTJU |  | REYQ360TTJU | Mixed Ducted and Non-Ducted Indoor Units | 334000 | 10.9 | 19.85 | 376000 | 3.41 | 264000 | 2.29 | R-410A | 27.8333
7629628 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ120TYDN | REYQ120TYDN | REYQ120TYDN |  | REYQ360TYDN | Mixed Ducted and Non-Ducted Indoor Units | 334000 | 10.9 | 19.85 | 376000 | 3.41 | 264000 | 2.29 | R-410A | 27.8333
7783690 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN | REYQ168TYDN |  |  | REYQ312TYDN | Non-Ducted Indoor Units | 290000 | 11.3 | 20.2 | 326000 | 3.56 | 230000 | 2.41 | R-410A | 24.1667
7783693 | 1/1/2027 | DAIKIN | HMSR-A-CB | REYQ144TYDN | REYQ168TYDN |  |  | REYQ312TYDN | Mixed Ducted and Non-Ducted Indoor Units | 290000 | 10.95 | 19.6 | 326000 | 3.39 | 230000 | 2.32 | R-410A | 24.1667
7850835 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA72TLCV |  | AOUA264TLCVG | Ducted Indoor Units | 252000 | 10.9 | 20.1 | 282000 | 3.4 | 194000 | 2.27 | R-410A | 21
7850837 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA96TLCV |  | AOUA288TLCVG | Ducted Indoor Units | 274000 | 10.6 | 20.1 | 308000 | 3.31 | 210000 | 2.27 | R-410A | 22.8333
7850855 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA72RLCV |  | AOUA264RLCVG | Ducted Indoor Units | 252000 | 10.9 | 20.1 | 282000 | 3.4 | 194000 | 2.27 | R-410A | 21
7850857 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA96RLCV |  | AOUA288RLCVG | Ducted Indoor Units | 274000 | 10.6 | 20.1 | 308000 | 3.31 | 210000 | 2.27 | R-410A | 22.8333
7850866 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA72TLCV |  | AOUA264TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 20.45 | 282000 | 3.42 | 194000 | 2.28 | R-410A | 21
7850867 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLCV | AOUA96TLCV | AOUA96TLCV |  | AOUA288TLCVG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 20.45 | 308000 | 3.33 | 210000 | 2.28 | R-410A | 22.8333
7850876 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA72RLCV |  | AOUA264RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 20.45 | 282000 | 3.42 | 194000 | 2.28 | R-410A | 21
7850877 | 1/1/2027 | FUJITSU | HMSV-A-CB | AOUA96RLCV | AOUA96RLCV | AOUA96RLCV |  | AOUA288RLCVG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 20.45 | 308000 | 3.33 | 210000 | 2.28 | R-410A | 22.8333
7987142 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
7987143 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
7987144 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S |  | TVAHP288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
7987145 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S |  | TVAHP288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
7987146 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP072B31S |  | TVAHP312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
7987147 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP072B31S |  | TVAHP312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
7987148 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
7987149 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
7987151 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
7987162 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
7987163 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
7987164 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S |  | TVAHR288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
7987165 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S |  | TVAHR288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
7987166 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR072B31S |  | TVAHR312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
7987167 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR072B31S |  | TVAHR312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
7987168 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
7987169 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
7987171 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
7987188 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
7987189 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
7987191 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP096B41S | TVAHP072B41S |  | TVAHP288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
7987194 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
7987195 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
7987197 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
7987208 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
7987209 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
7987211 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR096B41S | TVAHR072B41S |  | TVAHR288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
7987214 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
7987215 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
7987217 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
7987234 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
7987235 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
7987236 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S |  | HVAHP288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
7987237 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S |  | HVAHP288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
7987238 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP072B31S |  | HVAHP312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
7987239 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP072B31S |  | HVAHP312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
7987240 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
7987241 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
7987243 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
7987254 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
7987255 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
7987256 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S |  | HVAHR288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
7987257 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S |  | HVAHR288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
7987258 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR072B31S |  | HVAHR312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
7987259 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR072B31S |  | HVAHR312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
7987260 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
7987261 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
7987263 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
7987280 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
7987281 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
7987283 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP096B41S | HVAHP072B41S |  | HVAHP288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
7987286 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
7987287 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
7987289 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
7987300 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
7987301 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
7987303 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR096B41S | HVAHR072B41S |  | HVAHR288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
7987306 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
7987307 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
7987309 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
7987326 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
7987327 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
7987328 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S |  | YVAHP288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
7987329 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S |  | YVAHP288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
7987330 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP072B31S |  | YVAHP312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
7987331 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP072B31S |  | YVAHP312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
7987332 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
7987333 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
7987335 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
7987346 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR264B31S | Non-Ducted Indoor Units | 252000 | 10.3 | 18.8 | 280000 | 3.61 | 200000 | 2.37 | R-410A | 21
7987347 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR264B31S | Ducted Indoor Units | 252000 | 11.3 | 19.4 | 280000 | 3.65 | 200000 | 2.54 | R-410A | 21
7987348 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S |  | YVAHR288B31S | Non-Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.7 | 216000 | 2.42 | R-410A | 23
7987349 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S |  | YVAHR288B31S | Ducted Indoor Units | 276000 | 10.5 | 19.4 | 308000 | 3.69 | 216000 | 2.54 | R-410A | 23
7987350 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR072B31S |  | YVAHR312B31S | Non-Ducted Indoor Units | 298000 | 9.6 | 18.8 | 334000 | 3.56 | 236000 | 2.37 | R-410A | 24.8333
7987351 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR072B31S |  | YVAHR312B31S | Ducted Indoor Units | 298000 | 9.9 | 19.8 | 334000 | 3.55 | 236000 | 2.47 | R-410A | 24.8333
7987352 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR336B31S | Non-Ducted Indoor Units | 320000 | 11.1 | 21.2 | 360000 | 3.87 | 268000 | 2.6 | R-410A | 26.6667
7987353 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR336B31S | Ducted Indoor Units | 320000 | 11 | 20.8 | 360000 | 3.68 | 268000 | 2.58 | R-410A | 26.6667
7987355 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR360B31S | Ducted Indoor Units | 344000 | 10.2 | 19 | 386000 | 3.67 | 284000 | 2.48 | R-410A | 28.6667
7987372 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
7987373 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
7987375 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP096B41S | YVAHP072B41S |  | YVAHP288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
7987378 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
7987379 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
7987381 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
7987392 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR264B41S | Non-Ducted Indoor Units | 252000 | 10 | 18.2 | 280000 | 3.5 | 200000 | 2.3 | R-410A | 21
7987393 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR264B41S | Ducted Indoor Units | 252000 | 10.7 | 19 | 280000 | 3.47 | 200000 | 2.41 | R-410A | 21
7987395 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR096B41S | YVAHR072B41S |  | YVAHR288B41S | Ducted Indoor Units | 276000 | 10.1 | 19 | 308000 | 3.52 | 216000 | 2.45 | R-410A | 23
7987398 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR336B41S | Non-Ducted Indoor Units | 320000 | 10.5 | 20.2 | 360000 | 3.68 | 268000 | 2.52 | R-410A | 26.6667
7987399 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR336B41S | Ducted Indoor Units | 320000 | 10.5 | 19.8 | 360000 | 3.52 | 268000 | 2.5 | R-410A | 26.6667
7987401 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR360B41S | Ducted Indoor Units | 344000 | 9.7 | 18.1 | 386000 | 3.51 | 284000 | 2.39 | R-410A | 28.6667
7990699 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP072B31S | TVAHP072B31S |  | TVAHP264B31S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.1 | 280000 | 3.63 | 200000 | 2.45 | R-410A | 21
7990700 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S |  | TVAHP288B31S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.25 | 19 | 308000 | 3.69 | 216000 | 2.48 | R-410A | 23
7990701 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP120B31S | TVAHP072B31S |  | TVAHP312B31S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.75 | 19.3 | 334000 | 3.55 | 236000 | 2.42 | R-410A | 24.8333
7990702 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP336B31S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.05 | 21 | 360000 | 3.77 | 268000 | 2.59 | R-410A | 26.6667
7990703 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B31S | TVAHP096B31S | TVAHP072B31S | TVAHP072B31S | TVAHP360B31S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 18.75 | 386000 | 3.77 | 284000 | 2.47 | R-410A | 28.6667
7990712 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR072B31S | TVAHR072B31S |  | TVAHR264B31S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.1 | 280000 | 3.63 | 200000 | 2.45 | R-410A | 21
7990713 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S |  | TVAHR288B31S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.25 | 19 | 308000 | 3.69 | 216000 | 2.48 | R-410A | 23
7990714 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR120B31S | TVAHR072B31S |  | TVAHR312B31S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.75 | 19.3 | 334000 | 3.55 | 236000 | 2.42 | R-410A | 24.8333
7990715 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR336B31S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.05 | 21 | 360000 | 3.77 | 268000 | 2.59 | R-410A | 26.6667
7990716 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B31S | TVAHR096B31S | TVAHR072B31S | TVAHR072B31S | TVAHR360B31S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 18.75 | 386000 | 3.77 | 284000 | 2.47 | R-410A | 28.6667
7990725 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP072B41S | TVAHP072B41S |  | TVAHP264B41S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.35 | 18.6 | 280000 | 3.48 | 200000 | 2.35 | R-410A | 21
7990726 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP096B41S | TVAHP072B41S |  | TVAHP288B41S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.8 | 18.35 | 308000 | 3.55 | 216000 | 2.39 | R-410A | 23
7990728 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP096B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP336B41S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20 | 360000 | 3.6 | 268000 | 2.51 | R-410A | 26.6667
7990730 | 1/1/2027 | JOHNSON CONTROLS | HMSV-A-CB | TVAHP120B41S | TVAHP096B41S | TVAHP072B41S | TVAHP072B41S | TVAHP360B41S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.59 | 284000 | 2.37 | R-410A | 28.6667
7990739 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR072B41S | TVAHR072B41S |  | TVAHR264B41S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.35 | 18.6 | 280000 | 3.48 | 200000 | 2.35 | R-410A | 21
7990740 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR096B41S | TVAHR072B41S |  | TVAHR288B41S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.8 | 18.35 | 308000 | 3.55 | 216000 | 2.39 | R-410A | 23
7990742 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR096B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR336B41S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20 | 360000 | 3.6 | 268000 | 2.51 | R-410A | 26.6667
7990743 | 1/1/2027 | JOHNSON CONTROLS | HMSR-A-CB | TVAHR120B41S | TVAHR096B41S | TVAHR072B41S | TVAHR072B41S | TVAHR360B41S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.59 | 284000 | 2.37 | R-410A | 28.6667
7990752 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP072B31S | HVAHP072B31S |  | HVAHP264B31S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.1 | 280000 | 3.63 | 200000 | 2.45 | R-410A | 21
7990753 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S |  | HVAHP288B31S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.25 | 19 | 308000 | 3.69 | 216000 | 2.48 | R-410A | 23
7990754 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP120B31S | HVAHP072B31S |  | HVAHP312B31S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.75 | 19.3 | 334000 | 3.55 | 236000 | 2.42 | R-410A | 24.8333
7990755 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP336B31S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.05 | 21 | 360000 | 3.77 | 268000 | 2.59 | R-410A | 26.6667
7990756 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B31S | HVAHP096B31S | HVAHP072B31S | HVAHP072B31S | HVAHP360B31S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 18.75 | 386000 | 3.77 | 284000 | 2.47 | R-410A | 28.6667
7990766 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR072B31S | HVAHR072B31S |  | HVAHR264B31S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.1 | 280000 | 3.63 | 200000 | 2.45 | R-410A | 21
7990767 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S |  | HVAHR288B31S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.25 | 19 | 308000 | 3.69 | 216000 | 2.48 | R-410A | 23
7990768 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR120B31S | HVAHR072B31S |  | HVAHR312B31S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.75 | 19.3 | 334000 | 3.55 | 236000 | 2.42 | R-410A | 24.8333
7990769 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR336B31S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.05 | 21 | 360000 | 3.77 | 268000 | 2.59 | R-410A | 26.6667
7990770 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B31S | HVAHR096B31S | HVAHR072B31S | HVAHR072B31S | HVAHR360B31S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 18.75 | 386000 | 3.77 | 284000 | 2.47 | R-410A | 28.6667
7990779 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP072B41S | HVAHP072B41S |  | HVAHP264B41S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.35 | 18.6 | 280000 | 3.48 | 200000 | 2.35 | R-410A | 21
7990780 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP096B41S | HVAHP072B41S |  | HVAHP288B41S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.8 | 18.35 | 308000 | 3.55 | 216000 | 2.39 | R-410A | 23
7990782 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP096B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP336B41S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20 | 360000 | 3.6 | 268000 | 2.51 | R-410A | 26.6667
7990783 | 1/1/2027 | HITACHI | HMSV-A-CB | HVAHP120B41S | HVAHP096B41S | HVAHP072B41S | HVAHP072B41S | HVAHP360B41S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.59 | 284000 | 2.37 | R-410A | 28.6667
7990792 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR072B41S | HVAHR072B41S |  | HVAHR264B41S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.35 | 18.6 | 280000 | 3.48 | 200000 | 2.35 | R-410A | 21
7990793 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR096B41S | HVAHR072B41S |  | HVAHR288B41S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.8 | 18.35 | 308000 | 3.55 | 216000 | 2.39 | R-410A | 23
7990796 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR096B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR336B41S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20 | 360000 | 3.6 | 268000 | 2.51 | R-410A | 26.6667
7990797 | 1/1/2027 | HITACHI | HMSR-A-CB | HVAHR120B41S | HVAHR096B41S | HVAHR072B41S | HVAHR072B41S | HVAHR360B41S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.59 | 284000 | 2.37 | R-410A | 28.6667
7990806 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP072B31S | YVAHP072B31S |  | YVAHP264B31S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.1 | 280000 | 3.63 | 200000 | 2.45 | R-410A | 21
7990807 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S |  | YVAHP288B31S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.25 | 19 | 308000 | 3.69 | 216000 | 2.48 | R-410A | 23
7990808 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP120B31S | YVAHP072B31S |  | YVAHP312B31S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.75 | 19.3 | 334000 | 3.55 | 236000 | 2.42 | R-410A | 24.8333
7990809 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP336B31S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.05 | 21 | 360000 | 3.77 | 268000 | 2.59 | R-410A | 26.6667
7990810 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B31S | YVAHP096B31S | YVAHP072B31S | YVAHP072B31S | YVAHP360B31S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 18.75 | 386000 | 3.77 | 284000 | 2.47 | R-410A | 28.6667
7990819 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR072B31S | YVAHR072B31S |  | YVAHR264B31S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.8 | 19.1 | 280000 | 3.63 | 200000 | 2.45 | R-410A | 21
7990820 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S |  | YVAHR288B31S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 10.25 | 19 | 308000 | 3.69 | 216000 | 2.48 | R-410A | 23
7990821 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR120B31S | YVAHR072B31S |  | YVAHR312B31S | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 9.75 | 19.3 | 334000 | 3.55 | 236000 | 2.42 | R-410A | 24.8333
7990822 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR336B31S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.05 | 21 | 360000 | 3.77 | 268000 | 2.59 | R-410A | 26.6667
7990823 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B31S | YVAHR096B31S | YVAHR072B31S | YVAHR072B31S | YVAHR360B31S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.85 | 18.75 | 386000 | 3.77 | 284000 | 2.47 | R-410A | 28.6667
7990832 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP072B41S | YVAHP072B41S |  | YVAHP264B41S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.35 | 18.6 | 280000 | 3.48 | 200000 | 2.35 | R-410A | 21
7990833 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP096B41S | YVAHP072B41S |  | YVAHP288B41S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.8 | 18.35 | 308000 | 3.55 | 216000 | 2.39 | R-410A | 23
7990835 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP096B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP336B41S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20 | 360000 | 3.6 | 268000 | 2.51 | R-410A | 26.6667
7990836 | 1/1/2027 | YORK | HMSV-A-CB | YVAHP120B41S | YVAHP096B41S | YVAHP072B41S | YVAHP072B41S | YVAHP360B41S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.59 | 284000 | 2.37 | R-410A | 28.6667
7990845 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR072B41S | YVAHR072B41S |  | YVAHR264B41S | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.35 | 18.6 | 280000 | 3.48 | 200000 | 2.35 | R-410A | 21
7990846 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR096B41S | YVAHR072B41S |  | YVAHR288B41S | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 9.8 | 18.35 | 308000 | 3.55 | 216000 | 2.39 | R-410A | 23
7990848 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR096B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR336B41S | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.5 | 20 | 360000 | 3.6 | 268000 | 2.51 | R-410A | 26.6667
7990849 | 1/1/2027 | YORK | HMSR-A-CB | YVAHR120B41S | YVAHR096B41S | YVAHR072B41S | YVAHR072B41S | YVAHR360B41S | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 9.6 | 17.8 | 386000 | 3.59 | 284000 | 2.37 | R-410A | 28.6667
8033349 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P72TKMU-* | PUHY-P72TKMU-* |  | PUHY-P264TSKMU-* | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
8033350 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P72TKMU-* | PUHY-P72TKMU-* |  | PUHY-P264TSKMU-* | Ducted Indoor Units | 252000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 21
8033351 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P72YKMU-* | PUHY-P72YKMU-* |  | PUHY-P264YSKMU-* | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
8033352 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P72YKMU-* | PUHY-P72YKMU-* |  | PUHY-P264YSKMU-* | Ducted Indoor Units | 250000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 20.8333
8033353 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P96TKMU-* | PUHY-P72TKMU-* |  | PUHY-P288TSKMU-* | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
8033354 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P96TKMU-* | PUHY-P72TKMU-* |  | PUHY-P288TSKMU-* | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
8033355 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P96YKMU-* | PUHY-P72YKMU-* |  | PUHY-P288YSKMU-* | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
8033356 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P96YKMU-* | PUHY-P72YKMU-* |  | PUHY-P288YSKMU-* | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
8033357 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P120TKMU-* | PUHY-P72TKMU-* |  | PUHY-P312TSKMU-* | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
8033358 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P120TKMU-* | PUHY-P72TKMU-* |  | PUHY-P312TSKMU-* | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
8033359 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P120YKMU-* | PUHY-P72YKMU-* |  | PUHY-P312YSKMU-* | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
8033360 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P120YKMU-* | PUHY-P72YKMU-* |  | PUHY-P312YSKMU-* | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
8033361 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P120TKMU-* | PUHY-P96TKMU-* |  | PUHY-P336TSKMU-* | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
8033362 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P120TKMU-* | PUHY-P96TKMU-* |  | PUHY-P336TSKMU-* | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
8033363 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P120YKMU-* | PUHY-P96YKMU-* |  | PUHY-P336YSKMU-* | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
8033364 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P120YKMU-* | PUHY-P96YKMU-* |  | PUHY-P336YSKMU-* | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
8033365 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-* | PUHY-P120TKMU-* | PUHY-P120TKMU-* |  | PUHY-P360TSKMU-* | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
8033368 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-* | PUHY-P120YKMU-* | PUHY-P120YKMU-* |  | PUHY-P360YSKMU-* | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
8033387 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-* | PURY-P120TKMU-* |  |  | PURY-P264TSKMU-* | Ducted Indoor Units | 250000 | 11 | 17.7 | 280000 | 3.4 | 200000 | 2.36 | R-410A | 20.8333
8033389 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-* | PURY-P120YKMU-* |  |  | PURY-P264YSKMU-* | Ducted Indoor Units | 250000 | 11 | 17.7 | 280000 | 3.4 | 200000 | 2.36 | R-410A | 20.8333
8033391 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-* | PURY-P144TKMU-* |  |  | PURY-P288TSKMU-* | Ducted Indoor Units | 274000 | 11.2 | 17.6 | 304000 | 3.41 | 216000 | 2.36 | R-410A | 22.8333
8033393 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-* | PURY-P144YKMU-* |  |  | PURY-P288YSKMU-* | Ducted Indoor Units | 274000 | 11.2 | 17.6 | 304000 | 3.41 | 216000 | 2.36 | R-410A | 22.8333
8175498 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  | PUHY-P264YSLMU-A | Ducted Indoor Units | 252000 | 12.4 | 21.1 | 280000 | 3.6 | 200000 | 2.39 | R-410A | 21
8175499 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P72YLMU-A | PUHY-P72YLMU-A |  | PUHY-P264YSLMU-A | Non-Ducted Indoor Units | 252000 | 13.6 | 24 | 280000 | 3.75 | 200000 | 2.16 | R-410A | 21
8175500 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  | PUHY-P288YSLMU-A | Ducted Indoor Units | 274000 | 12 | 20.4 | 308000 | 3.47 | 216000 | 2.4 | R-410A | 22.8333
8175501 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P96YLMU-A | PUHY-P72YLMU-A |  | PUHY-P288YSLMU-A | Non-Ducted Indoor Units | 274000 | 13.5 | 24 | 308000 | 3.7 | 216000 | 2.21 | R-410A | 22.8333
8175502 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  | PUHY-P312YSLMU-A | Ducted Indoor Units | 296000 | 12 | 20.3 | 334000 | 3.45 | 236000 | 2.31 | R-410A | 24.6667
8175503 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P72YLMU-A |  | PUHY-P312YSLMU-A | Non-Ducted Indoor Units | 296000 | 13.4 | 23.4 | 334000 | 3.66 | 236000 | 2.22 | R-410A | 24.6667
8175504 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  | PUHY-P336YSLMU-A | Ducted Indoor Units | 320000 | 11.8 | 20.3 | 360000 | 3.43 | 268000 | 2.26 | R-410A | 26.6667
8175505 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P96YLMU-A |  | PUHY-P336YSLMU-A | Non-Ducted Indoor Units | 320000 | 13.2 | 23.4 | 360000 | 3.52 | 268000 | 2.13 | R-410A | 26.6667
8175506 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YLMU-A | PUHY-P120YLMU-A | PUHY-P120YLMU-A |  | PUHY-P360YSLMU-A | Ducted Indoor Units | 342000 | 11.8 | 20.1 | 386000 | 3.41 | 284000 | 2.2 | R-410A | 28.5
8175528 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  | PUHY-P264TSLMU-A | Ducted Indoor Units | 252000 | 12.4 | 21.1 | 280000 | 3.6 | 200000 | 2.39 | R-410A | 21
8175529 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P72TLMU-A | PUHY-P72TLMU-A |  | PUHY-P264TSLMU-A | Non-Ducted Indoor Units | 252000 | 13.6 | 24 | 280000 | 3.75 | 200000 | 2.16 | R-410A | 21
8175530 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  | PUHY-P288TSLMU-A | Ducted Indoor Units | 274000 | 12 | 20.4 | 308000 | 3.47 | 216000 | 2.4 | R-410A | 22.8333
8175531 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P96TLMU-A | PUHY-P72TLMU-A |  | PUHY-P288TSLMU-A | Non-Ducted Indoor Units | 274000 | 13.5 | 24 | 308000 | 3.7 | 216000 | 2.21 | R-410A | 22.8333
8175532 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  | PUHY-P312TSLMU-A | Ducted Indoor Units | 296000 | 12 | 20.3 | 334000 | 3.45 | 236000 | 2.31 | R-410A | 24.6667
8175533 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P72TLMU-A |  | PUHY-P312TSLMU-A | Non-Ducted Indoor Units | 296000 | 13.4 | 23.4 | 334000 | 3.66 | 236000 | 2.22 | R-410A | 24.6667
8175534 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  | PUHY-P336TSLMU-A | Ducted Indoor Units | 320000 | 11.8 | 20.3 | 360000 | 3.43 | 268000 | 2.26 | R-410A | 26.6667
8175535 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P96TLMU-A |  | PUHY-P336TSLMU-A | Non-Ducted Indoor Units | 320000 | 13.2 | 23.4 | 360000 | 3.52 | 268000 | 2.13 | R-410A | 26.6667
8175536 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TLMU-A | PUHY-P120TLMU-A | PUHY-P120TLMU-A |  | PUHY-P360TSLMU-A | Ducted Indoor Units | 342000 | 11.8 | 20.1 | 386000 | 3.41 | 284000 | 2.2 | R-410A | 28.5
4677081 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ72PBTJ | RXYQ120PBTJ |  | RXYQ264PBTJ | Non-Ducted Indoor Units | 250000 | 11.3 | 20.8 | 282000 | 3.5 | 184000 | 2.45 | R-410A | 20.8333
4677082 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ72PBTJ | RXYQ120PBTJ |  | RXYQ264PBTJ | Ducted Indoor Units | 250000 | 11.7 | 19.1 | 282000 | 3.5 | 184000 | 2.3 | R-410A | 20.8333
4677083 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ72PBTJ | RXYQ120PBTJ |  | RXYQ264PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11.5 | 19.95 | 282000 | 3.5 | 184000 | 2.37 | R-410A | 20.8333
4677084 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ96PBTJ | RXYQ120PBTJ |  | RXYQ288PBTJ | Non-Ducted Indoor Units | 274000 | 11.5 | 19.6 | 308000 | 3.5 | 200000 | 2.45 | R-410A | 22.8333
4677085 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ96PBTJ | RXYQ120PBTJ |  | RXYQ288PBTJ | Ducted Indoor Units | 274000 | 10.5 | 18.8 | 308000 | 3.45 | 200000 | 2.45 | R-410A | 22.8333
4677086 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ96PBTJ | RXYQ120PBTJ |  | RXYQ288PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11 | 19.2 | 308000 | 3.47 | 200000 | 2.45 | R-410A | 22.8333
4677087 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ120PBTJ | RXYQ120PBTJ |  | RXYQ312PBTJ | Non-Ducted Indoor Units | 296000 | 10.7 | 18.2 | 334000 | 3.3 | 222000 | 2.35 | R-410A | 24.6667
4677088 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ120PBTJ | RXYQ120PBTJ |  | RXYQ312PBTJ | Ducted Indoor Units | 296000 | 11.5 | 17 | 334000 | 3.3 | 222000 | 2.35 | R-410A | 24.6667
4677089 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBTJ | RXYQ120PBTJ | RXYQ120PBTJ |  | RXYQ312PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.1 | 17.6 | 334000 | 3.3 | 222000 | 2.35 | R-410A | 24.6667
4677114 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ72PBYD | RXYQ120PBYD |  | RXYQ264PBYD | Non-Ducted Indoor Units | 250000 | 11.3 | 20.8 | 282000 | 3.5 | 184000 | 2.45 | R-410A | 20.8333
4677115 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ72PBYD | RXYQ120PBYD |  | RXYQ264PBYD | Ducted Indoor Units | 250000 | 11.7 | 19.1 | 282000 | 3.5 | 184000 | 2.3 | R-410A | 20.8333
4677116 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ72PBYD | RXYQ120PBYD |  | RXYQ264PBYD | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11.5 | 19.95 | 282000 | 3.5 | 184000 | 2.37 | R-410A | 20.8333
4677117 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ96PBYD | RXYQ120PBYD |  | RXYQ288PBYD | Non-Ducted Indoor Units | 274000 | 11.5 | 19.6 | 308000 | 3.5 | 200000 | 2.45 | R-410A | 22.8333
4677118 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ96PBYD | RXYQ120PBYD |  | RXYQ288PBYD | Ducted Indoor Units | 274000 | 10.5 | 18.8 | 308000 | 3.45 | 200000 | 2.45 | R-410A | 22.8333
4677119 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ96PBYD | RXYQ120PBYD |  | RXYQ288PBYD | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11 | 19.2 | 308000 | 3.47 | 200000 | 2.45 | R-410A | 22.8333
4677120 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ120PBYD | RXYQ120PBYD |  | RXYQ312PBYD | Non-Ducted Indoor Units | 296000 | 10.7 | 18.2 | 334000 | 3.3 | 222000 | 2.35 | R-410A | 24.6667
4677121 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ120PBYD | RXYQ120PBYD |  | RXYQ312PBYD | Ducted Indoor Units | 296000 | 11.5 | 17 | 334000 | 3.3 | 222000 | 2.35 | R-410A | 24.6667
4677122 | 1/1/2027 | VRVIII | HMSV-A-CB | RXYQ72PBYD | RXYQ120PBYD | RXYQ120PBYD |  | RXYQ312PBYD | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 11.1 | 17.6 | 334000 | 3.3 | 222000 | 2.35 | R-410A | 24.6667
4677141 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ72PBTJ | REMQ120PBTJ |  | REYQ264PBTJ | Non-Ducted Indoor Units | 250000 | 10.8 | 18.7 | 282000 | 3.4 | 190000 | 2.4 | R-410A | 20.8333
4677142 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ72PBTJ | REMQ120PBTJ |  | REYQ264PBTJ | Ducted Indoor Units | 250000 | 11.3 | 18.1 | 282000 | 3.3 | 190000 | 2.3 | R-410A | 20.8333
4677143 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ72PBTJ | REMQ120PBTJ |  | REYQ264PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11.05 | 18.4 | 282000 | 3.35 | 190000 | 2.35 | R-410A | 20.8333
4677144 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ288PBTJ | Non-Ducted Indoor Units | 274000 | 10.7 | 19 | 308000 | 3.35 | 208000 | 2.4 | R-410A | 22.8333
4677145 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ288PBTJ | Ducted Indoor Units | 274000 | 10.7 | 17.5 | 308000 | 3.4 | 208000 | 2.35 | R-410A | 22.8333
4677146 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ288PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.7 | 18.25 | 308000 | 3.37 | 208000 | 2.37 | R-410A | 22.8333
4677149 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBTJ | REMQ96PBTJ | REMQ120PBTJ |  | REYQ312PBTJ | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.25 | 16.55 | 334000 | 3.28 | 224000 | 2.25 | R-410A | 24.6667
4677165 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD | REMQ120PBYD |  | REYQ264PBYD | Non-Ducted Indoor Units | 250000 | 10.8 | 18.7 | 282000 | 3.4 | 190000 | 2.4 | R-410A | 20.8333
4677166 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD | REMQ120PBYD |  | REYQ264PBYD | Ducted Indoor Units | 250000 | 11.3 | 18.1 | 282000 | 3.3 | 190000 | 2.3 | R-410A | 20.8333
4677167 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ72PBYD | REMQ120PBYD |  | REYQ264PBYD | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11.05 | 18.4 | 282000 | 3.35 | 190000 | 2.35 | R-410A | 20.8333
4677168 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ288PBYD | Non-Ducted Indoor Units | 274000 | 10.7 | 19 | 308000 | 3.35 | 208000 | 2.4 | R-410A | 22.8333
4677169 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ288PBYD | Ducted Indoor Units | 274000 | 10.7 | 17.5 | 308000 | 3.4 | 208000 | 2.35 | R-410A | 22.8333
4677170 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ72PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ288PBYD | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.7 | 18.25 | 308000 | 3.37 | 208000 | 2.37 | R-410A | 22.8333
4677173 | 1/1/2027 | VRVIII | HMSR-A-CB | REMQ96PBYD | REMQ96PBYD | REMQ120PBYD |  | REYQ312PBYD | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 10.25 | 16.55 | 334000 | 3.28 | 224000 | 2.25 | R-410A | 24.6667
4679558 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BT3 | ARUB144BT3 |  |  | ARUB264BT3 | Ducted Indoor Units | 250000 | 11.2 | 17 | 282000 | 3.28 | 184000 | 2.35 | R-410A | 20.8333
4679559 | 1/1/2027 | LG | HMSR-A-CB | ARUB121BT3 | ARUB144BT3 |  |  | ARUB264BT3 | Non-Ducted Indoor Units | 250000 | 11.6 | 18.1 | 282000 | 3.51 | 184000 | 2.45 | R-410A | 20.8333
4679560 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DT3 | ARUB144DT3 |  |  | ARUB264DT3 | Ducted Indoor Units | 250000 | 11.2 | 17 | 282000 | 3.28 | 184000 | 2.35 | R-410A | 20.8333
4679561 | 1/1/2027 | LG | HMSR-A-CB | ARUB121DT3 | ARUB144DT3 |  |  | ARUB264DT3 | Non-Ducted Indoor Units | 250000 | 11.6 | 18.1 | 282000 | 3.51 | 184000 | 2.45 | R-410A | 20.8333
4679562 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BT3 | ARUB144BT3 |  |  | ARUB288BT3 | Ducted Indoor Units | 274000 | 10.9 | 17 | 308000 | 3.26 | 200000 | 2.34 | R-410A | 22.8333
4679563 | 1/1/2027 | LG | HMSR-A-CB | ARUB144BT3 | ARUB144BT3 |  |  | ARUB288BT3 | Non-Ducted Indoor Units | 274000 | 11.5 | 17.8 | 308000 | 3.48 | 200000 | 2.4 | R-410A | 22.8333
4679564 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DT3 | ARUB144DT3 |  |  | ARUB288DT3 | Ducted Indoor Units | 274000 | 10.9 | 17 | 308000 | 3.26 | 200000 | 2.34 | R-410A | 22.8333
4679565 | 1/1/2027 | LG | HMSR-A-CB | ARUB144DT3 | ARUB144DT3 |  |  | ARUB288DT3 | Non-Ducted Indoor Units | 274000 | 11.5 | 17.8 | 308000 | 3.48 | 200000 | 2.4 | R-410A | 22.8333
4679566 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB096BT3 | ARUB144BT3 |  | ARUB312BT3 | Ducted Indoor Units | 296000 | 11.3 | 18 | 334000 | 3.25 | 222000 | 2.36 | R-410A | 24.6667
4679567 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BT3 | ARUB096BT3 | ARUB144BT3 |  | ARUB312BT3 | Non-Ducted Indoor Units | 296000 | 11.8 | 18.2 | 334000 | 3.46 | 222000 | 2.36 | R-410A | 24.6667
4679568 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB096DT3 | ARUB144DT3 |  | ARUB312DT3 | Ducted Indoor Units | 296000 | 11.3 | 18 | 334000 | 3.25 | 222000 | 2.36 | R-410A | 24.6667
4679569 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DT3 | ARUB096DT3 | ARUB144DT3 |  | ARUB312DT3 | Non-Ducted Indoor Units | 296000 | 11.8 | 18.2 | 334000 | 3.46 | 222000 | 2.36 | R-410A | 24.6667
4679602 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BT3 | ARUN144BT3 |  |  | ARUN264BT3 | Ducted Indoor Units | 250000 | 11.2 | 17 | 282000 | 3.28 | 184000 | 2.35 | R-410A | 20.8333
4679603 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BT3 | ARUN144BT3 |  |  | ARUN264BT3 | Non-Ducted Indoor Units | 250000 | 11.6 | 18.1 | 282000 | 3.51 | 184000 | 2.45 | R-410A | 20.8333
4679604 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DT3 | ARUN144DT3 |  |  | ARUN264DT3 | Ducted Indoor Units | 250000 | 11.2 | 17 | 282000 | 3.28 | 184000 | 2.35 | R-410A | 20.8333
4679605 | 1/1/2027 | LG | HMSV-A-CB | ARUN121DT3 | ARUN144DT3 |  |  | ARUN264DT3 | Non-Ducted Indoor Units | 250000 | 11.6 | 18.1 | 282000 | 3.51 | 184000 | 2.45 | R-410A | 20.8333
4679606 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BT3 | ARUN144BT3 |  |  | ARUN288BT3 | Ducted Indoor Units | 274000 | 10.9 | 17 | 308000 | 3.26 | 200000 | 2.34 | R-410A | 22.8333
4679607 | 1/1/2027 | LG | HMSV-A-CB | ARUN144BT3 | ARUN144BT3 |  |  | ARUN288BT3 | Non-Ducted Indoor Units | 274000 | 11.5 | 17.8 | 308000 | 3.48 | 200000 | 2.4 | R-410A | 22.8333
4679608 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DT3 | ARUN144DT3 |  |  | ARUN288DT3 | Ducted Indoor Units | 274000 | 10.9 | 17 | 308000 | 3.26 | 200000 | 2.34 | R-410A | 22.8333
4679609 | 1/1/2027 | LG | HMSV-A-CB | ARUN144DT3 | ARUN144DT3 |  |  | ARUN288DT3 | Non-Ducted Indoor Units | 274000 | 11.8 | 18.2 | 308000 | 3.46 | 200000 | 2.4 | R-410A | 22.8333
4679610 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN096BT3 | ARUN144BT3 |  | ARUN312BT3 | Ducted Indoor Units | 296000 | 11.3 | 18 | 334000 | 3.25 | 222000 | 2.36 | R-410A | 24.6667
4679611 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BT3 | ARUN096BT3 | ARUN144BT3 |  | ARUN312BT3 | Non-Ducted Indoor Units | 296000 | 11.5 | 18 | 334000 | 3.44 | 222000 | 2.36 | R-410A | 24.6667
4679612 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN096DT3 | ARUN144DT3 |  | ARUN312DT3 | Ducted Indoor Units | 296000 | 11.3 | 18 | 334000 | 3.25 | 222000 | 2.36 | R-410A | 24.6667
4679613 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DT3 | ARUN096DT3 | ARUN144DT3 |  | ARUN312DT3 | Non-Ducted Indoor Units | 296000 | 11.8 | 18.2 | 334000 | 3.46 | 222000 | 2.36 | R-410A | 24.6667
5358546 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  | PUHY-P264YSKMU-A | Ducted Indoor Units | 250000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 20.8333
5358547 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  | PUHY-P264YSKMU-A | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
5358548 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P72YKMU-A | PUHY-P72YKMU-A |  | PUHY-P264YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 12.5 | 18.85 | 280000 | 3.64 | 200000 | 2.34 | R-410A | 20.8333
5358549 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  | PUHY-P288YSKMU-A | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
5358550 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  | PUHY-P288YSKMU-A | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
5358551 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P96YKMU-A | PUHY-P72YKMU-A |  | PUHY-P288YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 12.4 | 18.85 | 308000 | 3.63 | 216000 | 2.37 | R-410A | 22.8333
5358552 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  | PUHY-P312YSKMU-A | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
5358553 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  | PUHY-P312YSKMU-A | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
5358554 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P72YKMU-A |  | PUHY-P312YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 12.1 | 18.25 | 334000 | 3.49 | 236000 | 2.32 | R-410A | 24.6667
5358555 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  | PUHY-P336YSKMU-A | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
5358556 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  | PUHY-P336YSKMU-A | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
5358557 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P96YKMU-A |  | PUHY-P336YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.95 | 18 | 360000 | 3.43 | 268000 | 2.25 | R-410A | 26.6667
5358558 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P120YKMU-A |  | PUHY-P360YSKMU-A | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
5358560 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120YKMU-A | PUHY-P120YKMU-A | PUHY-P120YKMU-A |  | PUHY-P360YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.75 | 17.5 | 386000 | 3.3 | 284000 | 2.18 | R-410A | 28.5
5358585 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A | PUHY-P72TKMU-A |  | PUHY-P264TSKMU-A | Ducted Indoor Units | 252000 | 12.5 | 19 | 280000 | 3.68 | 200000 | 2.52 | R-410A | 21
5358586 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A | PUHY-P72TKMU-A |  | PUHY-P264TSKMU-A | Non-Ducted Indoor Units | 252000 | 12.5 | 18.7 | 280000 | 3.6 | 200000 | 2.16 | R-410A | 21
5358587 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P72TKMU-A | PUHY-P72TKMU-A |  | PUHY-P264TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 12.5 | 18.85 | 280000 | 3.64 | 200000 | 2.34 | R-410A | 21
5358588 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  | PUHY-P288TSKMU-A | Ducted Indoor Units | 274000 | 12.4 | 19 | 308000 | 3.68 | 216000 | 2.53 | R-410A | 22.8333
5358589 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  | PUHY-P288TSKMU-A | Non-Ducted Indoor Units | 274000 | 12.4 | 18.7 | 308000 | 3.59 | 216000 | 2.21 | R-410A | 22.8333
5358590 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P96TKMU-A | PUHY-P72TKMU-A |  | PUHY-P288TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 12.4 | 18.85 | 308000 | 3.63 | 216000 | 2.37 | R-410A | 22.8333
5358591 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  | PUHY-P312TSKMU-A | Ducted Indoor Units | 296000 | 12.1 | 18.4 | 334000 | 3.54 | 236000 | 2.43 | R-410A | 24.6667
5358592 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  | PUHY-P312TSKMU-A | Non-Ducted Indoor Units | 296000 | 12.1 | 18.1 | 334000 | 3.45 | 236000 | 2.22 | R-410A | 24.6667
5358593 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P72TKMU-A |  | PUHY-P312TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 296000 | 12.1 | 18.25 | 334000 | 3.49 | 236000 | 2.32 | R-410A | 24.6667
5358594 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  | PUHY-P336TSKMU-A | Ducted Indoor Units | 320000 | 11.9 | 18.2 | 360000 | 3.5 | 268000 | 2.38 | R-410A | 26.6667
5358595 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  | PUHY-P336TSKMU-A | Non-Ducted Indoor Units | 320000 | 12 | 17.8 | 360000 | 3.36 | 268000 | 2.13 | R-410A | 26.6667
5358596 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P96TKMU-A |  | PUHY-P336TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 11.95 | 18 | 360000 | 3.43 | 268000 | 2.25 | R-410A | 26.6667
5358597 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P120TKMU-A |  | PUHY-P360TSKMU-A | Ducted Indoor Units | 342000 | 11.7 | 17.8 | 386000 | 3.39 | 284000 | 2.32 | R-410A | 28.5
5358599 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120TKMU-A | PUHY-P120TKMU-A | PUHY-P120TKMU-A |  | PUHY-P360TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 342000 | 11.75 | 17.5 | 386000 | 3.3 | 284000 | 2.18 | R-410A | 28.5
5358627 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-A | PURY-P120YKMU-A |  |  | PURY-P264YSKMU-A | Ducted Indoor Units | 250000 | 11 | 17.7 | 280000 | 3.4 | 200000 | 2.36 | R-410A | 20.8333
5358629 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-A | PURY-P120YKMU-A |  |  | PURY-P264YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11 | 18.05 | 280000 | 3.31 | 200000 | 2.21 | R-410A | 20.8333
5358630 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-A | PURY-P144YKMU-A |  |  | PURY-P288YSKMU-A | Ducted Indoor Units | 274000 | 11.2 | 17.6 | 304000 | 3.41 | 216000 | 2.36 | R-410A | 22.8333
5358632 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144YKMU-A | PURY-P144YKMU-A |  |  | PURY-P288YSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.25 | 18.1 | 304000 | 3.31 | 216000 | 2.2 | R-410A | 22.8333
5358654 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-A | PURY-P120TKMU-A |  |  | PURY-P264TSKMU-A | Ducted Indoor Units | 250000 | 11 | 17.7 | 280000 | 3.4 | 200000 | 2.36 | R-410A | 20.8333
5358656 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-A | PURY-P120TKMU-A |  |  | PURY-P264TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 250000 | 11 | 18.05 | 280000 | 3.31 | 200000 | 2.21 | R-410A | 20.8333
5358657 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-A | PURY-P144TKMU-A |  |  | PURY-P288TSKMU-A | Ducted Indoor Units | 274000 | 11.2 | 17.6 | 304000 | 3.41 | 216000 | 2.36 | R-410A | 22.8333
5358659 | 1/1/2027 | CITY MULTI | HMSR-A-CB | PURY-P144TKMU-A | PURY-P144TKMU-A |  |  | PURY-P288TSKMU-A | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 11.25 | 18.1 | 304000 | 3.31 | 216000 | 2.2 | R-410A | 22.8333
5733077 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAFH | AM144FXVAFH |  |  | AM264FXVAFH | Ducted Indoor Units | 252000 | 10.1 | 18.6 | 282000 | 3.25 | 184000 | 2.26 | R-410A | 21
5733078 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAJH | AM144FXVAJH |  |  | AM264FXVAJH | Ducted Indoor Units | 252000 | 10.1 | 18.5 | 282000 | 3.25 | 184000 | 2.26 | R-410A | 21
5733079 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAFH | AM144FXVAFH |  |  | AM264FXVAFH | Non-Ducted Indoor Units | 252000 | 10.5 | 21.5 | 282000 | 3.45 | 184000 | 2.41 | R-410A | 21
5733080 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM120FXVAJH | AM144FXVAJH |  |  | AM264FXVAJH | Non-Ducted Indoor Units | 252000 | 10.1 | 21.5 | 282000 | 3.45 | 184000 | 2.41 | R-410A | 21
5733081 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAFR | AM144FXVAFR |  |  | AM264FXVAFR | Ducted Indoor Units | 252000 | 10.1 | 18.6 | 282000 | 3.25 | 184000 | 2.26 | R-410A | 21
5733082 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAJR | AM144FXVAJR |  |  | AM264FXVAJR | Ducted Indoor Units | 252000 | 10.1 | 18.5 | 282000 | 3.25 | 184000 | 2.26 | R-410A | 21
5733083 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAFR | AM144FXVAFR |  |  | AM264FXVAFR | Non-Ducted Indoor Units | 252000 | 10.5 | 21.5 | 282000 | 3.45 | 184000 | 2.41 | R-410A | 21
5733084 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM120FXVAJR | AM144FXVAJR |  |  | AM264FXVAJR | Non-Ducted Indoor Units | 252000 | 10.1 | 21.5 | 282000 | 3.45 | 184000 | 2.41 | R-410A | 21
5733085 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAFH | AM144FXVAFH |  |  | AM288FXVAFH | Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.25 | 200000 | 2.12 | R-410A | 23
5733086 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM144FXVAJH |  |  | AM288FXVAJH | Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.25 | 200000 | 2.12 | R-410A | 23
5733088 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM144FXVAJH | AM144FXVAJH |  |  | AM288FXVAJH | Non-Ducted Indoor Units | 276000 | 9.9 | 21 | 308000 | 3.26 | 200000 | 2.29 | R-410A | 23
5733089 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR | AM144FXVAFR |  |  | AM288FXVAFR | Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.25 | 200000 | 2.12 | R-410A | 23
5733090 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM144FXVAJR |  |  | AM288FXVAJR | Ducted Indoor Units | 276000 | 10 | 18.6 | 308000 | 3.25 | 200000 | 2.12 | R-410A | 23
5733092 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM144FXVAJR |  |  | AM288FXVAJR | Non-Ducted Indoor Units | 276000 | 9.9 | 21 | 308000 | 3.26 | 200000 | 2.29 | R-410A | 23
5733095 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAFH | AM096FXVAFH | AM144FXVAFH |  | AM312FXVAFH | Non-Ducted Indoor Units | 298000 | 10.5 | 21.2 | 334000 | 3.38 | 218000 | 2.54 | R-410A | 24.8333
5733096 | 1/1/2027 | SAMSUNG | HMSV-A-CB | AM072FXVAJH | AM096FXVAJH | AM144FXVAJH |  | AM312FXVAJH | Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.38 | 218000 | 2.51 | R-410A | 24.8333
5733099 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM096FXVAFR | AM144FXVAFR |  | AM312FXVAFR | Non-Ducted Indoor Units | 298000 | 10.5 | 21.2 | 334000 | 3.38 | 218000 | 2.54 | R-410A | 24.8333
5733100 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM096FXVAJR | AM144FXVAJR |  | AM312FXVAJR | Non-Ducted Indoor Units | 298000 | 10.6 | 20.9 | 334000 | 3.38 | 218000 | 2.51 | R-410A | 24.8333
6495707 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 | ARUN096DTE4 | ARUN144DTE4 |  | ARUN312DTE4 | Ducted Indoor Units | 296000 | 11.3 | 19.5 | 334000 | 3.3 | 222000 | 2.37 | R-410A | 24.6667
6495708 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 | ARUN096BTE4 | ARUN144BTE4 |  | ARUN312BTE4 | Ducted Indoor Units | 296000 | 11.3 | 19.5 | 334000 | 3.3 | 222000 | 2.37 | R-410A | 24.6667
6495709 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 | ARUB096DTE4 | ARUB144DTE4 |  | ARUB312DTE4 | Ducted Indoor Units | 296000 | 11.3 | 19.5 | 334000 | 3.3 | 222000 | 2.37 | R-410A | 24.6667
6495710 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 | ARUB096BTE4 | ARUB144BTE4 |  | ARUB312BTE4 | Ducted Indoor Units | 296000 | 11.3 | 19.5 | 334000 | 3.3 | 222000 | 2.37 | R-410A | 24.6667
6495711 | 1/1/2027 | LG | HMSR-A-CB | ARUB072BTE4 | ARUB096BTE4 | ARUB144BTE4 |  | ARUB312BTE4 | Non-Ducted Indoor Units | 296000 | 11.2 | 20 | 334000 | 3.55 | 222000 | 2.4 | R-410A | 24.6667
6495712 | 1/1/2027 | LG | HMSR-A-CB | ARUB072DTE4 | ARUB096DTE4 | ARUB144DTE4 |  | ARUB312DTE4 | Non-Ducted Indoor Units | 296000 | 11.2 | 20 | 334000 | 3.55 | 222000 | 2.4 | R-410A | 24.6667
6495713 | 1/1/2027 | LG | HMSV-A-CB | ARUN072DTE4 | ARUN096DTE4 | ARUN144DTE4 |  | ARUN312DTE4 | Non-Ducted Indoor Units | 296000 | 11.2 | 20 | 334000 | 3.55 | 222000 | 2.4 | R-410A | 24.6667
6495714 | 1/1/2027 | LG | HMSV-A-CB | ARUN072BTE4 | ARUN096BTE4 | ARUN144DTE4 |  | ARUN312BTE4 | Non-Ducted Indoor Units | 296000 | 11.2 | 20 | 334000 | 3.55 | 222000 | 2.4 | R-410A | 24.6667
6495715 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN096DTE4 | ARUN144DTE4 |  | ARUN336DTE4 | Non-Ducted Indoor Units | 320000 | 10.8 | 20 | 360000 | 3.51 | 234000 | 2.42 | R-410A | 26.6667
6495716 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN096BTE4 | ARUN144BTE4 |  | ARUN336BTE4 | Non-Ducted Indoor Units | 320000 | 10.8 | 20 | 360000 | 3.51 | 234000 | 2.42 | R-410A | 26.6667
6495717 | 1/1/2027 | LG | HMSR-A-CB | ARUB096BTE4 | ARUB096BTE4 | ARUB144BTE4 |  | ARUB336BTE4 | Non-Ducted Indoor Units | 320000 | 10.8 | 20 | 360000 | 3.51 | 234000 | 2.42 | R-410A | 26.6667
6495718 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB096DTE4 | ARUB144DTE4 |  | ARUB336DTE4 | Non-Ducted Indoor Units | 320000 | 10.8 | 20 | 360000 | 3.51 | 234000 | 2.42 | R-410A | 26.6667
6495719 | 1/1/2027 | LG | HMSR-A-CB | ARUB096DTE4 | ARUB096DTE4 | ARUB144DTE4 |  | ARUB336DTE4 | Ducted Indoor Units | 320000 | 11.1 | 19 | 360000 | 3.27 | 234000 | 2.38 | R-410A | 26.6667
6495720 | 1/1/2027 | LG | HMSR-A-CB | ARUN096BTE4 | ARUB096BTE4 | ARUB144BTE4 |  | ARUB336BTE4 | Ducted Indoor Units | 320000 | 11.1 | 19 | 360000 | 3.27 | 234000 | 2.38 | R-410A | 26.6667
6495721 | 1/1/2027 | LG | HMSV-A-CB | ARUN096BTE4 | ARUN096BTE4 | ARUN144BTE4 |  | ARUN336BTE4 | Ducted Indoor Units | 320000 | 11.1 | 19 | 360000 | 3.27 | 234000 | 2.38 | R-410A | 26.6667
6495722 | 1/1/2027 | LG | HMSV-A-CB | ARUN096DTE4 | ARUN096DTE4 | ARUN144DTE4 |  | ARUN336DTE4 | Ducted Indoor Units | 320000 | 11.1 | 19 | 360000 | 3.27 | 234000 | 2.38 | R-410A | 26.6667
6687556 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA72TLBV |  | AOUA264TLBVG | Ducted Indoor Units | 252000 | 10.9 | 20.1 | 282000 | 3.4 | 194000 | 2.27 | R-410A | 21
6687558 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA96TLBV |  | AOUA288TLBVG | Ducted Indoor Units | 274000 | 10.6 | 20.1 | 308000 | 3.31 | 210000 | 2.27 | R-410A | 22.8333
6691445 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA72TLBV |  | AOUA264TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 10.9 | 20.45 | 282000 | 3.42 | 194000 | 2.28 | R-410A | 21
6691446 | 1/1/2027 | FUJITSU | HMSR-A-CB | AOUA96TLBV | AOUA96TLBV | AOUA96TLBV |  | AOUA288TLBVG | Mixed Ducted and Non-Ducted Indoor Units | 274000 | 10.6 | 20.45 | 308000 | 3.33 | 210000 | 2.28 | R-410A | 22.8333
8657033 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P96ZKMU-A |  | PUHY-P336ZSKMU-A | Ducted Indoor Units | 320000 | 11.6 | 20 | 360000 | 3.42 | 268000 | 2.38 | R-410A | 26.6667
8657031 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P72ZKMU-A |  | PUHY-P312ZSKMU-A | Ducted Indoor Units | 296000 | 11.9 | 20 | 334000 | 3.46 | 236000 | 2.43 | R-410A | 24.6667
8657029 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P96ZKMU-A | PUHY-P72ZKMU-A |  | PUHY-P288ZSKMU-A | Ducted Indoor Units | 274000 | 11.8 | 20.1 | 308000 | 3.49 | 216000 | 2.53 | R-410A | 22.8333
8657027 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P72ZKMU-A | PUHY-P72ZKMU-A |  | PUHY-P264ZSKMU-A | Ducted Indoor Units | 252000 | 11.9 | 20.7 | 280000 | 3.47 | 200000 | 2.52 | R-410A | 21
8657035 | 1/1/2027 | CITY MULTI | HMSV-A-CB | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A | PUHY-P120ZKMU-A |  | PUHY-P360ZSKMU-A | Ducted Indoor Units | 342000 | 11.4 | 19.8 | 386000 | 3.32 | 284000 | 2.32 | R-410A | 28.5
205281487 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
205281488 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
205281489 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
202566112 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Non-Ducted Indoor Units | 252000 | 12.5 | 22 | 282000 | 3.56 | 182000 | 2.52 | R-410A | 21
202566113 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Ducted Indoor Units | 252000 | 11.5 | 21.5 | 282000 | 3.38 | 182000 | 2.38 | R-410A | 21
202566114 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Non-Ducted Indoor Units | 276000 | 12.2 | 22 | 308000 | 3.55 | 198000 | 2.5 | R-410A | 23
202566115 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Ducted Indoor Units | 276000 | 11.3 | 21 | 308000 | 3.33 | 198000 | 2.35 | R-410A | 23
202566116 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Non-Ducted Indoor Units | 298000 | 11 | 22 | 332000 | 3.53 | 222000 | 2.48 | R-410A | 24.8333
202566117 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Ducted Indoor Units | 298000 | 11 | 21 | 332000 | 3.25 | 222000 | 2.3 | R-410A | 24.8333
202566118 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM121CTE5 |  |  | ARUM336CTE5 | Non-Ducted Indoor Units | 320000 | 9.8 | 20.5 | 358000 | 3.52 | 234000 | 2.36 | R-410A | 26.6667
202566120 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM144CTE5 |  |  | ARUM360CTE5 | Non-Ducted Indoor Units | 344000 | 10.8 | 20 | 384000 | 3.51 | 248000 | 2.3 | R-410A | 28.6667
202566122 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM168CTE5 |  |  | ARUM384CTE5 | Non-Ducted Indoor Units | 366000 | 10 | 19 | 410000 | 3.4 | 266000 | 2.28 | R-410A | 30.5
202566124 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM192CTE5 |  |  | ARUM408CTE5 | Non-Ducted Indoor Units | 390000 | 9.8 | 18.8 | 434000 | 3.34 | 284000 | 2.26 | R-410A | 32.5
202566126 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM121CTE5 | ARUM121CTE5 |  | ARUM432CTE5 | Non-Ducted Indoor Units | 410000 | 9.8 | 19.8 | 460000 | 3.28 | 298000 | 2.32 | R-410A | 34.1667
202534327 | 1/1/2027 | LG | HMSR-A-CB | ARUB121CTE4 | ARUB144CTE4 |  |  | ARUB264CTE4 | Non-Ducted Indoor Units | 250000 | 11.6 | 20.5 | 280000 | 3.54 | 182000 | 2.49 | R-410A | 20.8333
202534328 | 1/1/2027 | LG | HMSR-A-CB | ARUB144CTE4 | ARUB144CTE4 |  |  | ARUB288CTE4 | Non-Ducted Indoor Units | 274000 | 11.6 | 20.5 | 306000 | 3.5 | 198000 | 2.47 | R-410A | 22.8333
202534329 | 1/1/2027 | LG | HMSR-A-CB | ARUB144CTE4 | ARUB168CTE4 |  |  | ARUB313CTE4 | Non-Ducted Indoor Units | 296000 | 11.2 | 20 | 334000 | 3.56 | 222000 | 2.36 | R-410A | 24.6667
202534330 | 1/1/2027 | LG | HMSR-A-CB | ARUB168CTE4 | ARUB168CTE4 |  |  | ARUB337CTE4 | Non-Ducted Indoor Units | 320000 | 10.7 | 20 | 360000 | 3.51 | 234000 | 2.34 | R-410A | 26.6667
202534331 | 1/1/2027 | LG | HMSR-A-CB | ARUB096CTE4 | ARUB121CTE4 | ARUB144CTE4 |  | ARUB360CTE4 | Non-Ducted Indoor Units | 342000 | 10.5 | 19.5 | 386000 | 3.5 | 248000 | 2.4 | R-410A | 28.5
202534339 | 1/1/2027 | LG | HMSR-A-CB | ARUB121CTE4 | ARUB144CTE4 |  |  | ARUB264CTE4 | Ducted Indoor Units | 250000 | 11.4 | 19.5 | 280000 | 3.38 | 182000 | 2.38 | R-410A | 20.8333
202534340 | 1/1/2027 | LG | HMSR-A-CB | ARUB144CTE4 | ARUB144CTE4 |  |  | ARUB288CTE4 | Ducted Indoor Units | 274000 | 11.2 | 19.5 | 306000 | 3.31 | 198000 | 2.35 | R-410A | 22.8333
202534343 | 1/1/2027 | LG | HMSR-A-CB | ARUB096CTE4 | ARUB121CTE4 | ARUB144CTE4 |  | ARUB360CTE4 | Ducted Indoor Units | 342000 | 11 | 20 | 386000 | 3.3 | 248000 | 2.4 | R-410A | 28.5
202534351 | 1/1/2027 | LG | HMSV-A-CB | ARUN121CTE4 | ARUN144CTE4 |  |  | ARUN264CTE4 | Non-Ducted Indoor Units | 250000 | 11.6 | 20.5 | 280000 | 3.54 | 182000 | 2.49 | R-410A | 20.8333
202534352 | 1/1/2027 | LG | HMSV-A-CB | ARUN144CTE4 | ARUN144CTE4 |  |  | ARUN288CTE4 | Non-Ducted Indoor Units | 274000 | 11.6 | 20.5 | 306000 | 3.5 | 198000 | 2.47 | R-410A | 22.8333
202534353 | 1/1/2027 | LG | HMSV-A-CB | ARUN144CTE4 | ARUN168CTE4 |  |  | ARUN313CTE4 | Non-Ducted Indoor Units | 296000 | 11.2 | 20 | 334000 | 3.56 | 222000 | 2.36 | R-410A | 24.6667
202534354 | 1/1/2027 | LG | HMSV-A-CB | ARUN168CTE4 | ARUN168CTE4 |  |  | ARUN337CTE4 | Non-Ducted Indoor Units | 320000 | 10.7 | 20 | 360000 | 3.51 | 234000 | 2.34 | R-410A | 26.6667
202534355 | 1/1/2027 | LG | HMSV-A-CB | ARUN096CTE4 | ARUN121CTE4 | ARUN144CTE4 |  | ARUN360CTE4 | Non-Ducted Indoor Units | 342000 | 10.5 | 19.5 | 386000 | 3.5 | 248000 | 2.4 | R-410A | 28.5
202534363 | 1/1/2027 | LG | HMSV-A-CB | ARUN121CTE4 | ARUN144CTE4 |  |  | ARUN264CTE4 | Ducted Indoor Units | 250000 | 11.4 | 19.5 | 280000 | 3.38 | 182000 | 2.38 | R-410A | 20.8333
202534364 | 1/1/2027 | LG | HMSV-A-CB | ARUN144CTE4 | ARUN144CTE4 |  |  | ARUN288CTE4 | Ducted Indoor Units | 274000 | 11.2 | 19.5 | 306000 | 3.31 | 198000 | 2.35 | R-410A | 22.8333
202534367 | 1/1/2027 | LG | HMSV-A-CB | ARUN096CTE4 | ARUN121CTE4 | ARUN144CTE4 |  | ARUN360CTE4 | Ducted Indoor Units | 342000 | 11 | 20 | 386000 | 3.3 | 248000 | 2.4 | R-410A | 28.5
206453568 | 1/1/2027 | LG | HMSR-A-CB | ARUM168CTE5 | ARUM096CTE5 |  |  | ARUM264CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 252000 | 12 | 21.75 | 282000 | 3.47 | 182000 | 2.45 | R-410A | 21
206453569 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM096CTE5 |  |  | ARUM288CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 276000 | 11.75 | 21.5 | 308000 | 3.44 | 198000 | 2.42 | R-410A | 23
206453570 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM096CTE5 |  |  | ARUM312CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 298000 | 11 | 21.5 | 332000 | 3.39 | 222000 | 2.39 | R-410A | 24.8333
206453571 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM121CTE5 |  |  | ARUM336CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 320000 | 10.3 | 20.5 | 358000 | 3.38 | 234000 | 2.3 | R-410A | 26.6667
206453572 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM144CTE5 |  |  | ARUM360CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 344000 | 10.5 | 19.75 | 384000 | 3.37 | 248000 | 2.25 | R-410A | 28.6667
206453573 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM168CTE5 |  |  | ARUM384CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 366000 | 9.9 | 19.15 | 410000 | 3.31 | 266000 | 2.24 | R-410A | 30.5
206453574 | 1/1/2027 | LG | HMSR-A-CB | ARUM216CTE5 | ARUM192CTE5 |  |  | ARUM408CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 390000 | 9.75 | 18.9 | 434000 | 3.28 | 284000 | 2.22 | R-410A | 32.5
206453575 | 1/1/2027 | LG | HMSR-A-CB | ARUM192CTE5 | ARUM121CTE5 | ARUM121CTE5 |  | ARUM432CTE5 | Mixed Ducted and Non-Ducted Indoor Units | 410000 | 10.15 | 19.9 | 460000 | 3.25 | 298000 | 2.24 | R-410A | 34.1667
208102054 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
208102059 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP120C432G | VEP120C432G |  | VEP336C432G | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
208102056 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
208102057 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP120C432Y |  | VEP312C432Y | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
208102052 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP096C432Y |  | VEP288C432Y | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
208102049 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
208102047 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432Y | VEP096C432Y | VEP096C432Y |  | VEP264C432Y | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
208102044 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
208102064 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
208102066 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Non-Ducted Indoor Units | 342000 | 9.9 | 19.5 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
208102067 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP120C432Y | VEP120C432Y | VEP120C432Y |  | VEP360C432Y | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
10306460 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV120H3CDC720(A) | IOV120H3CDC720(A) | IOV120H3CDC720(A) |  | IOV360H3CDC761(A) | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
10306454 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV096H3CDC716(A) | IOV096H3CDC716(A) |  | IOV288H3CDC749(A) | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
10306452 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV072H3CDC712(A) | IOV096H3CDC716(A) | IOV096H3CDC716(A) |  | IOV264H3CDC745(A) | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
10267496 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-360WM/B-U(U) | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
10267497 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-360WM/B-U(U) | Non-Ducted Indoor Units | 342000 | 9.9 | 19.5 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
201903132 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
201903134 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432G | VEP120C432G | VEP120C432G |  | VEP360C432G | Non-Ducted Indoor Units | 342000 | 9.9 | 19.5 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
201903128 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP120C432G | VEP120C432G |  | VEP336C432G | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
201903124 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
201903126 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP120C432G |  | VEP312C432G | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
201903120 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432G | VEP096C432G | VEP096C432G |  | VEP288C432G | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
201903116 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432G | VEP096C432G | VEP096C432G |  | VEP264C432G | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
202584338 | 1/1/2027 | LG | HMSV-A-CB | ARUN121BTE4 | ARUN144BTE4 |  |  | ARUN264BTE4 | Non-Ducted Indoor Units | 250000 | 11.9 | 21.8 | 280000 | 3.6 | 182000 | 2.49 | R-410A | 20.8333
204442751 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAFR | AM144FXVAFR |  |  | AM288JXVAFR | Non-Ducted Indoor Units | 276000 | 11 | 22.6 | 308000 | 3.54 | 200000 | 2.46 | R-410A | 23
204442768 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAJR | AM168HXVAJR |  |  | AM336JXVAJR | Non-Ducted Indoor Units | 320000 | 10.6 | 21.5 | 360000 | 3.46 | 234000 | 2.49 | R-410A | 26.6667
204442766 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM144FXVAJR | AM144FXVAJR |  |  | AM288JXVAJR | Non-Ducted Indoor Units | 276000 | 11 | 22.6 | 308000 | 3.54 | 200000 | 2.46 | R-410A | 23
204442755 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAFR | AM144FXVAFR | AM192HXVAFR |  | AM408JXVAFR | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
204442753 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM168HXVAFR | AM168HXVAFR |  |  | AM336JXVAFR | Non-Ducted Indoor Units | 320000 | 10.6 | 21.5 | 360000 | 3.46 | 234000 | 2.49 | R-410A | 26.6667
204442806 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTJR | AM096KXVTJR | AM096KXVTJR |  | AM288KXVTJR | Non-Ducted Indoor Units | 276000 | 12.8 | 28.1 | 308000 | 3.7 | 308000 | 2.1 | R-410A | 23
204442770 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM072FXVAJR | AM144FXVAJR | AM192HXVAJR |  | AM408JXVAJR | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
204442798 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM096KXVTFR | AM096KXVTFR | AM096KXVTFR |  | AM288KXVTFR | Non-Ducted Indoor Units | 276000 | 12.8 | 28.1 | 308000 | 3.7 | 308000 | 2.1 | R-410A | 23
204442812 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM192HXVAJR | AM216KXVGJR |  |  | AM408KXVGJR | Non-Ducted Indoor Units | 390000 | 9.8 | 21 | 436000 | 3.3 | 284000 | 2.4 | R-410A | 32.5
204442813 | 1/1/2027 | SAMSUNG | HMSR-A-CB | AM216KXVGJR | AM216KXVGJR |  |  | AM432KXVGJR | Non-Ducted Indoor Units | 416000 | 9.8 | 21 | 460000 | 3.3 | 300000 | 2.4 | R-410A | 34.6667
10032555 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-F(U) | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) |  | GMV-264WM/B-F(U) | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
10225961 | 1/1/2027 | INNOVAIR | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP120C432Y |  | VEP312C432Y | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10324126 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV096H3CDC716(A) | IOV120H3CDC720(A) |  | IOV312H3CDC753(A) | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10267493 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-336WM/B-U(U) | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
10267487 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-288WM/B-U(U) | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
10267490 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-312WM/B-U(U) | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10267491 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) | GMV-120WM/B-U(U) |  | GMV-312WM/B-U(U) | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10267484 | 1/1/2027 | GREE | HMSV-A-CB | GMV-72WM/B-U(U) | GMV-96WM/B-U(U) | GMV-96WM/B-U(U) |  | GMV-264WM/B-U(U) | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
10257466 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP120C432Y |  | VEP312C432Y | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10257470 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP120C432Y | VEP120C432Y | VEP120C432Y |  | VEP360C432Y | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
10257463 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP096C432Y |  | VEP288C432Y | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
10257464 | 1/1/2027 | LENNOX VRF | HMSV-A-CB | VEP072C432Y | VEP096C432Y | VEP096C432Y |  | VEP264C432Y | Ducted Indoor Units | 250000 | 10.5 | 20.5 | 282000 | 3.3 | 186000 | 2.2 | R-410A | 20.8333
10035096 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) | GMV-120WM/B-F(U) |  | GMV-312WM/B-F(U) | Ducted Indoor Units | 296000 | 10.5 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10035094 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) |  | GMV-288WM/B-F(U) | Ducted Indoor Units | 274000 | 10.5 | 20 | 308000 | 3.25 | 200000 | 2.2 | R-410A | 22.8333
9964029 | 1/1/2027 | GREE | HMSV-A-CB | GMV-120WM/B-F(U) | GMV-120WM/B-F(U) | GMV-120WM/B-F(U) |  | GMV-360WM/B-F(U) | Ducted Indoor Units | 342000 | 10.5 | 19 | 384000 | 3.25 | 250000 | 2.2 | R-410A | 28.5
202616839 | 1/1/2027 | LG | HMSV-A-CB | ARUN145BTE4 | ARUN145BTE4 | ARUN145BTE4 |  | ARUN432BTE4 | Non-Ducted Indoor Units | 410000 | 9.8 | 19.5 | 460000 | 3.3 | 298000 | 2.3 | R-410A | 34.1667
202616840 | 1/1/2027 | LG | HMSV-A-CB | ARUN145BTE4 | ARUN145BTE4 | ARUN145BTE4 |  | ARUN432BTE4 | Ducted Indoor Units | 410000 | 10.4 | 19.8 | 460000 | 3.3 | 298000 | 2.25 | R-410A | 34.1667
10035097 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-96WM/B-F(U) | GMV-120WM/B-F(U) |  | GMV-312WM/B-F(U) | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10035098 | 1/1/2027 | GREE | HMSV-A-CB | GMV-96WM/B-F(U) | GMV-120WM/B-F(U) | GMV-120WM/B-F(U) |  | GMV-336WM/B-F(U) | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
10324127 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV096H3CDC716(A) | IOV120H3CDC720(A) |  | IOV312H3CDC753(A) | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
10306458 | 1/1/2027 | INNOVAIR | HMSV-A-CB | IOV096H3CDC716(A) | IOV120H3CDC720(A) | IOV120H3CDC720(A) |  | IOV336H3CDC758(A) | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667
10594392 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-120U8STB |  |  | AVWT-264U8SZB | Non-Ducted Indoor Units | 258000 | 11.05 | 24.1 | 282000 | 3.69 | 180000 | 2.39 | R-410A | 21.5
10594393 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-144U8S1B |  |  | AVWT-288U8SZB | Non-Ducted Indoor Units | 276000 | 10.7 | 23.35 | 300000 | 3.59 | 192000 | 2.3 | R-410A | 23
10594394 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-168U8S1B | AVWT-144U8S1B |  |  | AVWT-312U8SZB | Non-Ducted Indoor Units | 298000 | 10.45 | 21.2 | 316000 | 3.57 | 202000 | 2.22 | R-410A | 24.8333
10594395 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-168U8S1B | AVWT-168U8S1B |  |  | AVWT-336U8SZB | Non-Ducted Indoor Units | 320000 | 10.25 | 20.6 | 324000 | 3.57 | 210000 | 2.24 | R-410A | 26.6667
10594396 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-144U8S1B | AVWT-072U8SNB |  | AVWT-360U8SZB | Non-Ducted Indoor Units | 346000 | 10.65 | 21.15 | 372000 | 3.55 | 244000 | 2.33 | R-410A | 28.8333
10594397 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-144U8S1B | AVWT-96U8STB |  | AVWT-384U8SZB | Non-Ducted Indoor Units | 370000 | 10.5 | 21.55 | 400000 | 3.47 | 260000 | 2.33 | R-410A | 30.8333
10594401 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-120U8STB |  |  | AVWT-264U8SZB | Ducted Indoor Units | 258000 | 11.55 | 24.3 | 282000 | 3.31 | 180000 | 2.25 | R-410A | 21.5
10595368 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-144U8S1B | AVWT-120U8STB |  | AVWT-408U8SZB | Ducted Indoor Units | 390000 | 11.25 | 22.9 | 435000 | 3.36 | 278000 | 2.34 | R-410A | 32.5
10595370 | 1/1/2027 | HISENSE | HMSV-A-CB | AVWT-144U8S1B | AVWT-144U8S1B | AVWT-120U8STB |  | AVWT-408U8SZB | Non-Ducted Indoor Units | 390000 | 10.15 | 22.2 | 435000 | 3.59 | 278000 | 2.31 | R-410A | 32.5
208102058 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP096C432Y | VEP120C432Y |  | VEP312C432Y | Non-Ducted Indoor Units | 296000 | 10.2 | 20 | 334000 | 3.25 | 206000 | 2.2 | R-410A | 24.6667
208102062 | 1/1/2027 | LENNOX | HMSV-A-CB | VEP096C432Y | VEP120C432Y | VEP120C432Y |  | VEP336C432Y | Ducted Indoor Units | 320000 | 10.5 | 19 | 360000 | 3.25 | 210000 | 2.2 | R-410A | 26.6667

## Commercial Water Loop HP
AHRI Certified Reference Number | Equipment Type | Outdoor Unit Brand Name | Outdoor Unit Model Number | Indoor Unit Model Number | Full Load Cooling Capacity (Btuh) | EER | Full Load Heating Capacity (Btuh) | COP | Tonnage | Tax Credit (IRA) Eligibility
216128491 | Water Loop | GEOSTAR | G5TV036BD1**2 |  | 36000 | 17.9 | 42300 | 5.6 | 3 | Yes
216411470 | Water Loop | ClimateMaster | SJ/PN036A | SAN036A | 36400 | 17.3 | 39400 | 5.3 | 3.0333 | Yes
216621313 | Water Loop | GEOSTAR | G5A(V/H)024*S0**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216621314 | Water Loop | GEOSTAR | G5A(V/H)030*S0**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216621315 | Water Loop | GEOSTAR | G5A(V/H)036*S0**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216621316 | Water Loop | GEOSTAR | G5A(V/H)042*S0**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216621333 | Water Loop | GEOSTAR | G5A(V/H)030*D0**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216621334 | Water Loop | GEOSTAR | G5A(V/H)030*D3**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216621335 | Water Loop | GEOSTAR | G5A(V/H)030*D0**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216621336 | Water Loop | GEOSTAR | G5A(V/H)030*D3**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216621337 | Water Loop | GEOSTAR | G5A(V/H)036*D0**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216621338 | Water Loop | GEOSTAR | G5A(V/H)036*D3**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
217754425 | Water Loop | DAIKIN | WSSV024F1*B*T |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
217754428 | Water Loop | DAIKIN | WSSV024F1*B*C |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
217754431 | Water Loop | DAIKIN | WSSV030F1*B*T |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
217754434 | Water Loop | DAIKIN | WSSV030F1*B*C |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
217754437 | Water Loop | DAIKIN | WSSV036F1*B*T |  | 39000 | 18.4 | 44100 | 5.34 | 3.25 | No
217754440 | Water Loop | DAIKIN | WSSV036F1*B*C |  | 39000 | 18.4 | 44100 | 5.34 | 3.25 | No
217754443 | Water Loop | DAIKIN | WSSV042F1*B*T |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
217754446 | Water Loop | DAIKIN | WSSV042F1*B*C |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
217754449 | Water Loop | DAIKIN | WSSV048F1*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
9035993 | Water Loop | GEOCOMFORT | GZT024******B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | Yes
9035994 | Water Loop | HYDRON MODULE | HZT024******B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | Yes
9035995 | Water Loop | TETCO | TZT024******B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | Yes
9035996 | Water Loop | GEOCOMFORT | GZT024*2****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9035997 | Water Loop | HYDRON MODULE | HZT024*2****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9035998 | Water Loop | TETCO | TZT024*2****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9035999 | Water Loop | GEOCOMFORT | GZT024*3****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036000 | Water Loop | HYDRON MODULE | HZT024*3****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036001 | Water Loop | TETCO | TZT024*3****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036002 | Water Loop | GEOCOMFORT | GZT024*A****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036003 | Water Loop | HYDRON MODULE | HZT024*A****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036004 | Water Loop | TETCO | TZT024*A****B |  | 25600 | 17 | 30000 | 5.5 | 2.1333 | No
9036975 | Water Loop | GEOCOMFORT | GZT036******B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | Yes
9036998 | Water Loop | HYDRON MODULE | HZT036******B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | Yes
9037017 | Water Loop | TETCO | TZT036******B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | Yes
9037062 | Water Loop | GEOCOMFORT | GZT036*2****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037081 | Water Loop | HYDRON MODULE | HZT036*2****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037097 | Water Loop | TETCO | TZT036*2****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037137 | Water Loop | GEOCOMFORT | GZT036*3****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037158 | Water Loop | HYDRON MODULE | HZT036*3****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037175 | Water Loop | TETCO | TZT036*3****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037215 | Water Loop | GEOCOMFORT | GZT036*A****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037240 | Water Loop | HYDRON MODULE | HZT036*A****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
9037275 | Water Loop | TETCO | TZT036*A****B |  | 36500 | 17 | 43300 | 5.3 | 3.0417 | No
215400209 | Water Loop | DAIKIN | WSSV042F3*B*C |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
215400212 | Water Loop | DAIKIN | WSSV048E1*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215400213 | Water Loop | DAIKIN | WSSV048F3*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215400216 | Water Loop | DAIKIN | WSSV048E1*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215400217 | Water Loop | DAIKIN | WSSV048F3*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215400220 | Water Loop | DAIKIN | WSSV060E1*B*T |  | 64000 | 17.4 | 78000 | 5.3 | 5.3333 | No
215400221 | Water Loop | DAIKIN | WSSV060F3*B*T |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
215400222 | Water Loop | DAIKIN | WSSV060E1*B*C |  | 64000 | 17.4 | 78000 | 5.3 | 5.3333 | No
215400223 | Water Loop | DAIKIN | WSSV060F3*B*C |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
215402546 | Water Loop | DAIKIN | WSSV007E1*B*T |  | 7100 | 17.99 | 8100 | 5.49 | 0.59167 | No
215402548 | Water Loop | DAIKIN | WSSV009E1*B*T |  | 9200 | 17.49 | 11000 | 4.98 | 0.76667 | No
215402550 | Water Loop | DAIKIN | WSSV024E1*B*T |  | 24400 | 18.37 | 28000 | 5.79 | 2.0333 | No
215402551 | Water Loop | DAIKIN | WSSV024F3*B*T |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215402554 | Water Loop | DAIKIN | WSSV024E1*B*C |  | 24400 | 18.37 | 28000 | 5.79 | 2.0333 | No
215402555 | Water Loop | DAIKIN | WSSV024F3*B*C |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215402558 | Water Loop | DAIKIN | WSSV030E1*B*T |  | 29200 | 19.17 | 34500 | 5.67 | 2.4333 | No
215402559 | Water Loop | DAIKIN | WSSV030F3*B*T |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
215402562 | Water Loop | DAIKIN | WSSV030E1*B*C |  | 29200 | 19.17 | 34500 | 5.67 | 2.4333 | No
215402563 | Water Loop | DAIKIN | WSSV030F3*B*C |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
215402566 | Water Loop | DAIKIN | WSSV036E1*B*T |  | 39000 | 19.02 | 44100 | 5.35 | 3.25 | No
215402567 | Water Loop | DAIKIN | WSSV036F3*B*T |  | 39000 | 18.4 | 44100 | 5.34 | 3.25 | No
9910450 | Water Loop | HYDRON MODULE | HZS018*****1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | Yes
9910451 | Water Loop | TETCO | TZS018*****1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | Yes
9910452 | Water Loop | GEOCOMFORT | GZS018*A***1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | No
9910453 | Water Loop | HYDRON MODULE | HZS018*A***1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | No
9910454 | Water Loop | TETCO | TZS018*A***1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | No
9910548 | Water Loop | GEOCOMFORT | GZS024*****1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | Yes
9910549 | Water Loop | HYDRON MODULE | HZS024*****1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | Yes
9910550 | Water Loop | TETCO | TZS024*****1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | Yes
9910551 | Water Loop | GEOCOMFORT | GZS024*2***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910552 | Water Loop | HYDRON MODULE | HZS024*2***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910553 | Water Loop | TETCO | TZS024*2***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910554 | Water Loop | GEOCOMFORT | GZS024*3***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910555 | Water Loop | HYDRON MODULE | HZS024*3***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910556 | Water Loop | TETCO | TZS024*3***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910557 | Water Loop | GEOCOMFORT | GZS024*A***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910558 | Water Loop | HYDRON MODULE | HZS024*A***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910559 | Water Loop | TETCO | TZS024*A***1B |  | 25000 | 17.9 | 29300 | 5.6 | 2.0833 | No
9910584 | Water Loop | GEOCOMFORT | GZS030*****1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | Yes
9910585 | Water Loop | HYDRON MODULE | HZS030*****1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | Yes
9910586 | Water Loop | TETCO | TZS030*****1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | Yes
9910587 | Water Loop | GEOCOMFORT | GZS030*2***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910588 | Water Loop | HYDRON MODULE | HZS030*2***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910589 | Water Loop | TETCO | TZS030*2***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910590 | Water Loop | GEOCOMFORT | GZS030*3***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910591 | Water Loop | HYDRON MODULE | HZS030*3***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910592 | Water Loop | TETCO | TZS030*3***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910593 | Water Loop | GEOCOMFORT | GZS030*A***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910594 | Water Loop | HYDRON MODULE | HZS030*A***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
9910595 | Water Loop | TETCO | TZS030*A***1B |  | 29500 | 17.5 | 33000 | 5.7 | 2.4583 | No
215852874 | Water Loop | DAIKIN | WSTV036E1*C/S*C |  | 38100 | 18.45 | 41100 | 5.18 | 3.175 | No
215852875 | Water Loop | DAIKIN | WSTV036F3*C/S*C |  | 38100 | 18.08 | 41100 | 5.08 | 3.175 | No
215852878 | Water Loop | DAIKIN | WSTV042E1*C/S*C |  | 43500 | 17.3 | 50000 | 5.06 | 3.625 | No
215852882 | Water Loop | DAIKIN | WSTV048E1*C/S*C |  | 50800 | 17.62 | 58500 | 5.52 | 4.2333 | No
215852883 | Water Loop | DAIKIN | WSTV048F3*C/S*C |  | 50800 | 17.27 | 58500 | 5.41 | 4.2333 | No
215852884 | Water Loop | DAIKIN | WSTV060E1*C/S*C |  | 60500 | 17.3 | 74700 | 5.5 | 5.0417 | No
207337513 | Water Loop | GEOSTAR | 103J036**1 | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | No
207337514 | Water Loop | GEOSTAR | 103J036**1 | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | No
6501947 | Water Loop | GEOSTAR | GBV/GBH038**3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501948 | Water Loop | GEOSTAR | GBV/GBH038**4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501949 | Water Loop | GEOSTAR | GBV/GBH038**4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214067548 | Water Loop | GeoSmart Energy | GBV/GBH024**3*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214067549 | Water Loop | GeoSmart Energy | GBV/GBH024**3*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214067551 | Water Loop | GeoSmart Energy | GBV/GBH024**4*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214067552 | Water Loop | GeoSmart Energy | GBV/GBH024**4*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214067557 | Water Loop | GeoSmart Energy | GBV/GBH030**3*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
214067558 | Water Loop | GeoSmart Energy | GBV/GBH030**3*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214067559 | Water Loop | GeoSmart Energy | GBV/GBH030**3*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214067560 | Water Loop | GeoSmart Energy | GBV/GBH030**4*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
214067561 | Water Loop | GeoSmart Energy | GBV/GBH030**4*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214067562 | Water Loop | GeoSmart Energy | GBV/GBH030**4*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214067564 | Water Loop | GeoSmart Energy | GBV/GBH036**3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214067565 | Water Loop | GeoSmart Energy | GBV/GBH036**3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214067567 | Water Loop | GeoSmart Energy | GBV/GBH036**4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214067568 | Water Loop | GeoSmart Energy | GBV/GBH036**4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214067569 | Water Loop | GeoSmart Energy | GBV/GBH038**3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214067570 | Water Loop | GeoSmart Energy | GBV/GBH038**3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214067571 | Water Loop | GeoSmart Energy | GBV/GBH038**4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214067572 | Water Loop | GeoSmart Energy | GBV/GBH038**4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214067574 | Water Loop | GeoSmart Energy | GBV/GBH042**3*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214067575 | Water Loop | GeoSmart Energy | GBV/GBH042**3*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214067577 | Water Loop | GeoSmart Energy | GBV/GBH042**4*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214067578 | Water Loop | GeoSmart Energy | GBV/GBH042**4*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214067584 | Water Loop | GeoSmart Energy | GBV/GBH049**3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
214067585 | Water Loop | GeoSmart Energy | GBV/GBH049**3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
214067586 | Water Loop | GeoSmart Energy | GBV/GBH049**4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
214067587 | Water Loop | GeoSmart Energy | GBV/GBH049**4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
215837810 | Water Loop | DAIKIN | WSSH024F3*C/S*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837811 | Water Loop | DAIKIN | WSSH024J1*C/S*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837813 | Water Loop | DAIKIN | WSSH024K3*C/S*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837818 | Water Loop | DAIKIN | WSSH024F3*C/S*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837820 | Water Loop | DAIKIN | WSSH024J1*C/S*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
215837821 | Water Loop | DAIKIN | WSSH024K3*C/S*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
7519727 | Water Loop | GEOCOMFORT | GVS024*****1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | Yes
7519748 | Water Loop | HYDRON MODULE | HVS024*****1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | Yes
7519756 | Water Loop | TETCO | TVS024*****1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | Yes
7519769 | Water Loop | GEOCOMFORT | GVS024*A***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519770 | Water Loop | HYDRON MODULE | HVS024*A***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519771 | Water Loop | TETCO | TVS024*A***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519772 | Water Loop | GEOCOMFORT | GVS024*2***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519773 | Water Loop | HYDRON MODULE | HVS024*2***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519774 | Water Loop | TETCO | TVS024*2***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519775 | Water Loop | GEOCOMFORT | GVS024*3***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519776 | Water Loop | HYDRON MODULE | HVS024*3***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7519777 | Water Loop | TETCO | TVS024*3***1 |  | 25900 | 18.4 | 29800 | 5.9 | 2.1583 | No
7520238 | Water Loop | GEOCOMFORT | GVS030*****1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | Yes
7520239 | Water Loop | HYDRON MODULE | HVS030*****1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | Yes
7520240 | Water Loop | TETCO | TVS030*****1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | Yes
7520241 | Water Loop | GEOCOMFORT | GVS030*2***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520242 | Water Loop | HYDRON MODULE | HVS030*2***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520243 | Water Loop | TETCO | TVS030*2***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520244 | Water Loop | TETCO | TVS030*3***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520245 | Water Loop | HYDRON MODULE | HVS030*3***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520246 | Water Loop | GEOCOMFORT | GVS030*A***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520247 | Water Loop | HYDRON MODULE | HVS030*A***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520248 | Water Loop | TETCO | TVS030*A***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7520249 | Water Loop | GEOCOMFORT | GVS030*3***1 |  | 30100 | 17.6 | 36200 | 5.9 | 2.5083 | No
7523956 | Water Loop | GEOCOMFORT | GVS018*****1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | Yes
7523957 | Water Loop | HYDRON MODULE | HVS018*****1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | Yes
203254607 | Water Loop | BRYANT | GB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254608 | Water Loop | ARCOAIRE | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203254609 | Water Loop | HEIL | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254610 | Water Loop | KEEPRITE | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254611 | Water Loop | TEMPSTAR | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254612 | Water Loop | COMFORTMAKER | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254614 | Water Loop | DAY & NIGHT | HB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
215268682 | Water Loop | WaterFurnace | V5A(V/H)024*S2**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268683 | Water Loop | WaterFurnace | V5A(V/H)024*S3**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268684 | Water Loop | WaterFurnace | V5A(V/H)024*S4**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268685 | Water Loop | WaterFurnace | V5A(V/H)024*S0**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268686 | Water Loop | WaterFurnace | V5A(V/H)024*S2**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268687 | Water Loop | WaterFurnace | V5A(V/H)024*S3**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268688 | Water Loop | WaterFurnace | V5A(V/H)024*S4**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268689 | Water Loop | WaterFurnace | V5A(V/H)030*S3**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268690 | Water Loop | WaterFurnace | V5A(V/H)030*S0**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268691 | Water Loop | WaterFurnace | V5A(V/H)030*S3**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268692 | Water Loop | WaterFurnace | V5A(V/H)036*S3**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268693 | Water Loop | WaterFurnace | V5A(V/H)036*S0**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268694 | Water Loop | WaterFurnace | V5A(V/H)036*S3**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268695 | Water Loop | WaterFurnace | V5A(V/H)036*S0**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268696 | Water Loop | WaterFurnace | V5A(V/H)036*S3**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268697 | Water Loop | WaterFurnace | V5A(V/H)042*S3**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268698 | Water Loop | WaterFurnace | V5A(V/H)042*S0**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268699 | Water Loop | WaterFurnace | V5A(V/H)042*S3**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268700 | Water Loop | WaterFurnace | V5A(V/H)042*S0**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268701 | Water Loop | WaterFurnace | V5A(V/H)042*S3**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268713 | Water Loop | WaterFurnace | V5A(V/H)030*S2**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268714 | Water Loop | WaterFurnace | V5A(V/H)030*S4**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268715 | Water Loop | WaterFurnace | V5A(V/H)030*S2**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268716 | Water Loop | WaterFurnace | V5A(V/H)030*S4**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
215268717 | Water Loop | WaterFurnace | V5A(V/H)036*S4**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268718 | Water Loop | WaterFurnace | V5A(V/H)036*S2**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268719 | Water Loop | WaterFurnace | V5A(V/H)036*S4**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268720 | Water Loop | WaterFurnace | V5A(V/H)036*S2**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268721 | Water Loop | WaterFurnace | V5A(V/H)036*S4**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268722 | Water Loop | WaterFurnace | V5A(V/H)042*S4**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268723 | Water Loop | WaterFurnace | V5A(V/H)042*S2**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268724 | Water Loop | WaterFurnace | V5A(V/H)042*S4**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268725 | Water Loop | WaterFurnace | V5A(V/H)042*S4**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
214796344 | Water Loop | WaterFurnace | W5A(V/H)030BD1**2 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | Yes
214796345 | Water Loop | WaterFurnace | W5A(V/H)036BD1**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | Yes
214810493 | Water Loop | GEOSTAR | G5A(V/H)030BD1**2 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | Yes
214810494 | Water Loop | GEOSTAR | G5A(V/H)036BD1**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | Yes
214823446 | Water Loop | GeoSmart Energy | S5A(V/H)030BD1**2 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | Yes
214823447 | Water Loop | GeoSmart Energy | S5A(V/H)036BD1**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | Yes
214823482 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030BD1**2 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | Yes
202921957 | Water Loop | FHP | EP036-1VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921958 | Water Loop | FHP | EP036-3VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921959 | Water Loop | FHP | EP036-4VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921960 | Water Loop | BOSCH | BP036-1VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922716 | Water Loop | CARRIER | 50PSV036***3/CA |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202922719 | Water Loop | CARRIER | 50PSV036***5/EA |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202922722 | Water Loop | CARRIER | 50PSV036***6/FA |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202922725 | Water Loop | CARRIER | GB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202922728 | Water Loop | BRYANT | GB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922731 | Water Loop | HEIL | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202922734 | Water Loop | ARCOAIRE | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922737 | Water Loop | KEEPRITE | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922740 | Water Loop | TEMPSTAR | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922742 | Water Loop | COMFORTMAKER | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
202922745 | Water Loop | DAY & NIGHT | HB036V******1**1 |  | 36000 | 17.1 | 41000 | 5.5 | 3 | Yes
7418887 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7418965 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7421327 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
7421397 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
7421438 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
7421969 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
7421970 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
215399772 | Water Loop | DAIKIN | WSMV015A1*C/S*T |  | 15500 | 17.51 | 17000 | 5.09 | 1.2917 | No
215399776 | Water Loop | DAIKIN | WSMV015A1*C/S*C |  | 15500 | 17.51 | 17000 | 5.09 | 1.2917 | No
215399790 | Water Loop | DAIKIN | WSMV024J1*C/S*T |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
217531660 | Water Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)006A |  | 6300 | 17 | 7600 | 5.5 | 0.525 | Yes
5295984 | Water Loop | WaterFurnace | NBV/NBH024**0*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295985 | Water Loop | WaterFurnace | NBV/NBH024**3*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295986 | Water Loop | WaterFurnace | NBV/NBH024**2*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295987 | Water Loop | WaterFurnace | NBV/NBH024**4*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295988 | Water Loop | WaterFurnace | NBV/NBH024**4*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295989 | Water Loop | WaterFurnace | NBV/NBH024**3*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295990 | Water Loop | WaterFurnace | NBV/NBH024**0*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295991 | Water Loop | WaterFurnace | NBV/NBH024**2*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
5295992 | Water Loop | WaterFurnace | NBV/NBH030**0*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
5295993 | Water Loop | WaterFurnace | NBV/NBH030**3*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
5295994 | Water Loop | WaterFurnace | NBV/NBH030**4*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
5295995 | Water Loop | WaterFurnace | NBV/NBH030**2*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
5295996 | Water Loop | WaterFurnace | NBV/NBH030**0*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5295997 | Water Loop | WaterFurnace | NBV/NBH030**2*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
207348707 | Water Loop | WaterFurnace | URD038*0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348708 | Water Loop | WaterFurnace | URD038*0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348709 | Water Loop | WaterFurnace | URD038*0*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348710 | Water Loop | WaterFurnace | URD038*3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348711 | Water Loop | WaterFurnace | URD038*3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348712 | Water Loop | WaterFurnace | URD038*3*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348713 | Water Loop | WaterFurnace | URD038*4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348714 | Water Loop | WaterFurnace | URD038*4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348715 | Water Loop | WaterFurnace | URD038*4*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207348716 | Water Loop | WaterFurnace | URD049*0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348717 | Water Loop | WaterFurnace | URD049*0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348718 | Water Loop | WaterFurnace | URD049*0*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348719 | Water Loop | WaterFurnace | URD049*3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348720 | Water Loop | WaterFurnace | URD049*3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348721 | Water Loop | WaterFurnace | URD049*3*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348722 | Water Loop | WaterFurnace | URD049*4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348723 | Water Loop | WaterFurnace | URD049*4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207348724 | Water Loop | WaterFurnace | URD049*4*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
217754453 | Water Loop | DAIKIN | WSSV048F1*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217754457 | Water Loop | DAIKIN | WSSV060F1*B*T |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
217754461 | Water Loop | DAIKIN | WSSV060F1*B*C |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
217754473 | Water Loop | DAIKIN | WSTH024E1*B*C |  | 24500 | 17.53 | 26100 | 5.29 | 2.0417 | No
217754474 | Water Loop | DAIKIN | WSTH024F1*B*C |  | 24500 | 17.18 | 26100 | 5.19 | 2.0417 | No
217754477 | Water Loop | DAIKIN | WSTH030E1*B*C |  | 31400 | 17.12 | 34900 | 5.36 | 2.6167 | No
217754481 | Water Loop | DAIKIN | WSTH036E1*B*C |  | 38000 | 18.43 | 42900 | 5.36 | 3.1667 | No
217754482 | Water Loop | DAIKIN | WSTH036F1*B*C |  | 38000 | 18.06 | 42900 | 5.25 | 3.1667 | No
217754485 | Water Loop | DAIKIN | WSTH042E1*B*C |  | 44000 | 17.59 | 50300 | 5.12 | 3.6667 | No
217754486 | Water Loop | DAIKIN | WSTH042F1*B*C |  | 44000 | 17.24 | 50300 | 5.02 | 3.6667 | No
217754489 | Water Loop | DAIKIN | WSTH048E1*B*C |  | 48200 | 17.34 | 56900 | 5.08 | 4.0167 | No
217754501 | Water Loop | DAIKIN | WSTV024E1*B*C |  | 24300 | 17.59 | 28000 | 5.81 | 2.025 | No
217754502 | Water Loop | DAIKIN | WSTV024F1*B*C |  | 24300 | 17.24 | 28000 | 5.7 | 2.025 | No
217037792 | Water Loop | YORK BY JOHNSON CONTROLS | Y5SS036BD1 | Y5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217037797 | Water Loop | YORK BY JOHNSON CONTROLS | Y5SZ036BD1 | Y5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217037802 | Water Loop | YORK BY JOHNSON CONTROLS | Y5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217037807 | Water Loop | YORK BY JOHNSON CONTROLS | Y5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217037812 | Water Loop | GeoSmart Energy | S5SS036BD1 | S5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217037817 | Water Loop | GeoSmart Energy | S5SZ036BD1 | S5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217037822 | Water Loop | GeoSmart Energy | S5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
963510 | Water Loop | WaterFurnace | NLV/NXV095T*3 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
963511 | Water Loop | WaterFurnace | NLV/NXV095T*4 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
963512 | Water Loop | WaterFurnace | NLV/NXV095T*5 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
202211042 | Water Loop | WaterFurnace | URD038*0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211043 | Water Loop | WaterFurnace | URD038*0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211044 | Water Loop | WaterFurnace | URD038*0*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211045 | Water Loop | WaterFurnace | URD038*3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211046 | Water Loop | WaterFurnace | URD038*3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211047 | Water Loop | WaterFurnace | URD038*3*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202211048 | Water Loop | WaterFurnace | URD049*0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202211049 | Water Loop | WaterFurnace | URD049*0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202211050 | Water Loop | WaterFurnace | URD049*0*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
7523958 | Water Loop | TETCO | TVS018*****1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | Yes
7523959 | Water Loop | GEOCOMFORT | GVS018*A***1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | No
7523960 | Water Loop | HYDRON MODULE | HVS018*A***1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | No
7523961 | Water Loop | TETCO | TVS018*A***1 |  | 20700 | 18.8 | 23700 | 6.2 | 1.725 | No
206347035 | Water Loop | DAIKIN | WCCH*015*J***14* |  | 15600 | 17.6 | 17200 | 5.6 | 1.3 | No
206347037 | Water Loop | DAIKIN | WCCH*015*E***14* |  | 16000 | 17.6 | 18100 | 5.6 | 1.3333 | No
206347960 | Water Loop | HYDROTECH | WSS6006*6* |  | 8000 | 17 | 8800 | 5.4 | 0.66667 | No
214772074 | Water Loop | TRANE | EXVK0097 |  | 8700 | 18.1 | 10700 | 6.4 | 0.725 | No
214772075 | Water Loop | TRANE | EXVK0127 |  | 11400 | 17.1 | 14300 | 5.9 | 0.95 | No
214772077 | Water Loop | TRANE | EXVK0187 |  | 18900 | 17.5 | 23000 | 5.43 | 1.575 | No
214772078 | Water Loop | TRANE | EXVK024B |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772079 | Water Loop | TRANE | EXVK0244 |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772080 | Water Loop | TRANE | EXVK0247 |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772081 | Water Loop | TRANE | EXVK030B |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772082 | Water Loop | TRANE | EXVK0304 |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772083 | Water Loop | TRANE | EXVK0307 |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772084 | Water Loop | TRANE | EXVK036B |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772085 | Water Loop | TRANE | EXVK0364 |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772086 | Water Loop | TRANE | EXVK0367 |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
216439574 | Water Loop | GeoSmart Energy | S5TV036BD1**2 |  | 36000 | 17.9 | 42300 | 5.6 | 3 | Yes
207323903 | Water Loop | WaterFurnace | NSZ036J1* | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
207323912 | Water Loop | WaterFurnace | NSZ036J1* | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
207324064 | Water Loop | WaterFurnace | NVV/NVH036C1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
207335136 | Water Loop | GEOSTAR | 101/102J030**1*(1,4)***** |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | Yes
207335137 | Water Loop | GEOSTAR | 101/102K036**1*(1,2,4)***** |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | Yes
207335138 | Water Loop | GEOSTAR | 101/102K042**1*(1,2,4)***** |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | Yes
207335143 | Water Loop | GEOSTAR | 101/102K038**1*(1,2,4)***** |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207335144 | Water Loop | GEOSTAR | 101/102K049**1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207335251 | Water Loop | GEOSTAR | 161/162K038**1*(1,2,4)***** |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
215827093 | Water Loop | DAIKIN | WSLV072F1*C/S |  | 74000 | 17 | 87000 | 5.2 | 6.1667 | No
215827095 | Water Loop | DAIKIN | WSLV072K1*C/S |  | 74000 | 17 | 87000 | 5.2 | 6.1667 | No
215827097 | Water Loop | DAIKIN | WSLV072L1*C/S |  | 74000 | 17 | 87000 | 5.1 | 6.1667 | No
216625656 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S3**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625657 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S3**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625658 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S4**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625659 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S4**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625660 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625661 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625662 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625663 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625664 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625665 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625666 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625667 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625668 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625669 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625670 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625671 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625672 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625673 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625674 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625675 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625676 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625677 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625678 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625679 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625680 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625681 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625682 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625683 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625694 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625695 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625696 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625697 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S2**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625698 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625699 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625700 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625701 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625702 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625703 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
215268745 | Water Loop | WaterFurnace | V5A(V/H)030*D0**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268746 | Water Loop | WaterFurnace | V5A(V/H)030*D3**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268747 | Water Loop | WaterFurnace | V5A(V/H)030*D0**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268748 | Water Loop | WaterFurnace | V5A(V/H)030*D3**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268749 | Water Loop | WaterFurnace | V5A(V/H)036*D0**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268750 | Water Loop | WaterFurnace | V5A(V/H)036*D3**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268751 | Water Loop | WaterFurnace | V5A(V/H)036*D0**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268752 | Water Loop | WaterFurnace | V5A(V/H)036*D3**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268753 | Water Loop | WaterFurnace | V5A(V/H)036*D0**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268754 | Water Loop | WaterFurnace | V5A(V/H)036*D3**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268775 | Water Loop | WaterFurnace | V5A(V/H)030*D2**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268776 | Water Loop | WaterFurnace | V5A(V/H)030*D4**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268777 | Water Loop | WaterFurnace | V5A(V/H)030*D2**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268778 | Water Loop | WaterFurnace | V5A(V/H)030*D4**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215268779 | Water Loop | WaterFurnace | V5A(V/H)036*D2**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268780 | Water Loop | WaterFurnace | V5A(V/H)036*D4**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268781 | Water Loop | WaterFurnace | V5A(V/H)036*D2**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268782 | Water Loop | WaterFurnace | V5A(V/H)036*D4**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268783 | Water Loop | WaterFurnace | V5A(V/H)036*D2**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268784 | Water Loop | WaterFurnace | V5A(V/H)036*D4**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215746915 | Water Loop | TRANE | GSK036A3 |  | 40281 | 19.2 | 47492 | 6.06 | 3.3567 | No
215746916 | Water Loop | TRANE | GSK048A3 |  | 53537 | 17.6 | 62760 | 5.79 | 4.4614 | No
215746918 | Water Loop | TRANE | GSK060A3 |  | 64919 | 17.4 | 76308 | 5.61 | 5.4099 | No
215746919 | Water Loop | TRANE | GSK072A3 |  | 84370 | 18.1 | 92045 | 5.75 | 7.0308 | No
215746920 | Water Loop | TRANE | GSK090A3 |  | 99665 | 17.8 | 109831 | 5.66 | 8.3054 | No
213154467 | Water Loop | GeoSmart Energy | GS030**1*1********L |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | Yes
213154468 | Water Loop | GeoSmart Energy | GS036**1*1********L |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | Yes
213154469 | Water Loop | GeoSmart Energy | GS042**1*1********L |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | Yes
213154474 | Water Loop | GeoSmart Energy | GT038**1*1********L |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
213154475 | Water Loop | GeoSmart Energy | GT049**1*1********L |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
8560948 | Water Loop | TETCO | TVS015*****1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | Yes
8560949 | Water Loop | GEOCOMFORT | GVS015*A***1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | No
8560950 | Water Loop | HYDRON MODULE | HVS015*A***1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | No
8560951 | Water Loop | TETCO | TVS015*A***1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | No
216772586 | Water Loop | Enertech | EVS015* |  | 15775 | 19.9 | 17700 | 6.4 | 1.3146 | Yes
216772594 | Water Loop | Enertech | EZS018* |  | 19725 | 18 | 21900 | 5.5 | 1.6438 | Yes
214772120 | Water Loop | TRANE | EXHK0097 |  | 8700 | 18.1 | 10700 | 6.4 | 0.725 | No
214772121 | Water Loop | TRANE | EXHK0127 |  | 11400 | 17.1 | 14300 | 5.9 | 0.95 | No
214772123 | Water Loop | TRANE | EXHK0187 |  | 18900 | 17.5 | 23000 | 5.43 | 1.575 | No
214772124 | Water Loop | TRANE | EXHK024B |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772125 | Water Loop | TRANE | EXHK0244 |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772126 | Water Loop | TRANE | EXHK0247 |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214772127 | Water Loop | TRANE | EXHK030B |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772128 | Water Loop | TRANE | EXHK0304 |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772129 | Water Loop | TRANE | EXHK0307 |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214772130 | Water Loop | TRANE | EXHK036B |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772131 | Water Loop | TRANE | EXHK0364 |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772132 | Water Loop | TRANE | EXHK0367 |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214772133 | Water Loop | TRANE | EXHK042B |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214772134 | Water Loop | TRANE | EXHK0424 |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214772135 | Water Loop | TRANE | EXHK048B |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214772136 | Water Loop | TRANE | EXHK0484 |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214772137 | Water Loop | TRANE | EXHK060B |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214772138 | Water Loop | TRANE | EXHK0604 |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214772139 | Water Loop | TRANE | EXHK070B |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
214772140 | Water Loop | TRANE | EXHK0704 |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
214772141 | Water Loop | TRANE | DXHK024A |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772142 | Water Loop | TRANE | DXHK036A |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
202330571 | Water Loop | AAON, Inc. | M2-006-4-H-BCAC-V0-10-000-A |  | 66700 | 18.2 | 57200 | 4.9 | 5.5583 | No
215399791 | Water Loop | DAIKIN | WSMV024K3*C/S*T |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215399794 | Water Loop | DAIKIN | WSMV024J1*C/S*C |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215399795 | Water Loop | DAIKIN | WSMV024K3*C/S*C |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215399815 | Water Loop | DAIKIN | WSMV036K3*C/S*T |  | 36800 | 17.02 | 42700 | 5.03 | 3.0667 | No
215399819 | Water Loop | DAIKIN | WSMV036K3*C/S*C |  | 36800 | 17.02 | 42700 | 5.03 | 3.0667 | No
215837673 | Water Loop | DAIKIN | WSMH024F3*C/S*T |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837675 | Water Loop | DAIKIN | WSMH024J1*C/S*T |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837676 | Water Loop | DAIKIN | WSMH024K3*C/S*T |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837681 | Water Loop | DAIKIN | WSMH024F3*C/S*C |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837683 | Water Loop | DAIKIN | WSMH024J1*C/S*C |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837685 | Water Loop | DAIKIN | WSMH024K3*C/S*C |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
215837698 | Water Loop | DAIKIN | WSMH030F3*C/S*T |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
215837701 | Water Loop | DAIKIN | WSMH030K3*C/S*T |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
215837707 | Water Loop | DAIKIN | WSMH030F3*C/S*C |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
215837709 | Water Loop | DAIKIN | WSMH030K3*C/S*C |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
217903418 | Water Loop | WaterFurnace | V5R036*S0**1* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903419 | Water Loop | WaterFurnace | V5R036*S0**4* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903420 | Water Loop | WaterFurnace | V5R036*S0**5* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903430 | Water Loop | WaterFurnace | V5R036*S3**1* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903431 | Water Loop | WaterFurnace | V5R036*S3**4* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903432 | Water Loop | WaterFurnace | V5R036*S3**5* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903433 | Water Loop | WaterFurnace | V5R036*S4**1* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903434 | Water Loop | WaterFurnace | V5R036*S4**4* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903435 | Water Loop | WaterFurnace | V5R036*S4**5* |  | 34600 | 18 | 37400 | 5.6 | 2.8833 | No
217903454 | Water Loop | WaterFurnace | V5R036*D4**1* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903455 | Water Loop | WaterFurnace | V5R036*D4**4* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903456 | Water Loop | WaterFurnace | V5R036*D4**5* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
9910660 | Water Loop | GEOCOMFORT | GZS042*****1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | Yes
9910661 | Water Loop | HYDRON MODULE | HZS042*****1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | Yes
9910662 | Water Loop | TETCO | TZS042*****1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | Yes
9910663 | Water Loop | GEOCOMFORT | GZS042*2***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910664 | Water Loop | HYDRON MODULE | HZS042*2***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910665 | Water Loop | TETCO | TZS042*2***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910666 | Water Loop | GEOCOMFORT | GZS042*3***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910667 | Water Loop | HYDRON MODULE | HZS042*3***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
9910668 | Water Loop | TETCO | TZS042*3***1B |  | 42500 | 17.7 | 49600 | 5.4 | 3.5417 | No
205767467 | Water Loop | ClimateMaster | QEV/H/D1860 |  | 48000 | 17.3 | 60000 | 5.5 | 4 | Yes
205767473 | Water Loop | ClimateMaster | TEV/H/D026B |  | 25000 | 17.4 | 31400 | 6 | 2.0833 | Yes
205767474 | Water Loop | ClimateMaster | TEV/H/D038B |  | 37700 | 17.9 | 45700 | 5.8 | 3.1417 | Yes
207200598 | Water Loop | GeoSmart Energy | GSZ036*1*J | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
207200605 | Water Loop | GeoSmart Energy | GSZ036*1*J | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
207200614 | Water Loop | GeoSmart Energy | VI036**1*(1,2)** |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
9111998 | Water Loop | BOSCH | SM036-1VT/CF*-*****B |  | 39300 | 18.6 | 46300 | 6.2 | 3.275 | No
9113183 | Water Loop | BOSCH | SM036-1VT/CF*-*****B |  | 39300 | 18.6 | 46300 | 6.2 | 3.275 | Yes
216759832 | Water Loop | GEOSTAR | G5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
217752688 | Water Loop | DAIKIN | WSSH042K1*B*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217752690 | Water Loop | DAIKIN | WSSH042K1*B*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217752692 | Water Loop | DAIKIN | WSSH048K1*B*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217752693 | Water Loop | DAIKIN | WSSH048L1*B*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217752694 | Water Loop | DAIKIN | WSSH048K1*B*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217752695 | Water Loop | DAIKIN | WSSH048L1*B*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217752696 | Water Loop | DAIKIN | WSSH060K1*B*T |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
217752698 | Water Loop | DAIKIN | WSSH060K1*B*C |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
217752700 | Water Loop | DAIKIN | WSSH070K1*B*T |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
217752702 | Water Loop | DAIKIN | WSSH070K1*B*C |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
217752704 | Water Loop | DAIKIN | WSSV024K1*B*T |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
217752705 | Water Loop | DAIKIN | WSSV024K1*B*C |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
217752706 | Water Loop | DAIKIN | WSSV030K1*B*T |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
217752707 | Water Loop | DAIKIN | WSSV030K1*B*C |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
217752708 | Water Loop | DAIKIN | WSSV036K1*B*T |  | 39000 | 18.32 | 44100 | 5.34 | 3.25 | No
217752709 | Water Loop | DAIKIN | WSSV036K1*B*C |  | 39000 | 18.32 | 44100 | 5.34 | 3.25 | No
217752710 | Water Loop | DAIKIN | WSSV042K1*B*T |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
217752711 | Water Loop | DAIKIN | WSSV042K1*B*C |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
217752712 | Water Loop | DAIKIN | WSSV048K1*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217752713 | Water Loop | DAIKIN | WSSV048L1*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217752714 | Water Loop | DAIKIN | WSSV048K1*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217752715 | Water Loop | DAIKIN | WSSV048L1*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
217752716 | Water Loop | DAIKIN | WSSV060K1*B*T |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
217752718 | Water Loop | DAIKIN | WSSV060K1*B*C |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
217752724 | Water Loop | DAIKIN | WSTH024K1*B*C |  | 24500 | 17 | 26100 | 5.14 | 2.0417 | No
215400095 | Water Loop | DAIKIN | WSMV024F3*C/S*T |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215400098 | Water Loop | DAIKIN | WSMV024E1*C/S*C |  | 24700 | 18.03 | 28600 | 5.25 | 2.0583 | No
215400099 | Water Loop | DAIKIN | WSMV024F3*C/S*C |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
215400114 | Water Loop | DAIKIN | WSMV036E1*C/S*P |  | 37300 | 17.25 | 43000 | 5.02 | 3.1083 | No
215400118 | Water Loop | DAIKIN | WSMV036E1*C/S*T |  | 37200 | 17.68 | 43100 | 5.17 | 3.1 | No
215400119 | Water Loop | DAIKIN | WSMV036F3*C/S*T |  | 36800 | 17.09 | 42700 | 5.03 | 3.0667 | No
215400122 | Water Loop | DAIKIN | WSMV036E1*C/S*C |  | 37200 | 17.68 | 43100 | 5.17 | 3.1 | No
215400123 | Water Loop | DAIKIN | WSMV036F3*C/S*C |  | 36800 | 17.09 | 42700 | 5.03 | 3.0667 | No
215400130 | Water Loop | DAIKIN | WSMV042E1*C/S*T |  | 41200 | 17.13 | 49300 | 5.36 | 3.4333 | No
215400134 | Water Loop | DAIKIN | WSMV042E1*C/S*C |  | 41200 | 17.13 | 49300 | 5.36 | 3.4333 | No
207338127 | Water Loop | GEOSTAR | 141/142C036**1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
207348654 | Water Loop | WaterFurnace | URS036*0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348655 | Water Loop | WaterFurnace | URS036*0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348656 | Water Loop | WaterFurnace | URS036*0*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348657 | Water Loop | WaterFurnace | URS036*3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348658 | Water Loop | WaterFurnace | URS036*3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348659 | Water Loop | WaterFurnace | URS036*3*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348660 | Water Loop | WaterFurnace | URS036*4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348661 | Water Loop | WaterFurnace | URS036*4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
207348662 | Water Loop | WaterFurnace | URS036*4*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907628 | Water Loop | WaterFurnace | URD038*4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
201907629 | Water Loop | WaterFurnace | URD038*4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
201907630 | Water Loop | WaterFurnace | URD038*4*5 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
201907631 | Water Loop | WaterFurnace | URD049*4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
201907632 | Water Loop | WaterFurnace | URD049*4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
201907633 | Water Loop | WaterFurnace | URD049*4*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
206346951 | Water Loop | DAIKIN | WVFC*030*E***14 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
206346952 | Water Loop | DAIKIN | WVFC*030*F***14 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
206346953 | Water Loop | DAIKIN | WVFC*030*J***14 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
216739949 | Water Loop | DAIKIN | WSNV024E1*C/S*C |  | 23900 | 17 | 27100 | 5.2 | 1.9917 | No
216739961 | Water Loop | DAIKIN | WSNV036E1*C/S*C |  | 36700 | 18.2 | 39400 | 5.1 | 3.0583 | No
216739962 | Water Loop | DAIKIN | WSNV036F3*C/S*C |  | 36700 | 17.8 | 39400 | 5 | 3.0583 | No
216739963 | Water Loop | DAIKIN | WSNV036J1*C/S*C |  | 36700 | 17.8 | 39400 | 5 | 3.0583 | No
216739964 | Water Loop | DAIKIN | WSNV036K3*C/S*C |  | 36700 | 17.6 | 39400 | 5 | 3.0583 | No
216739969 | Water Loop | DAIKIN | WSNV042E1*C/S*C |  | 43300 | 17.1 | 49900 | 5 | 3.6083 | No
216739975 | Water Loop | DAIKIN | WSNV048E1*C/S*C |  | 49300 | 17.2 | 55800 | 5.2 | 4.1083 | No
215852854 | Water Loop | DAIKIN | WSTH036E1*C/S*C |  | 38000 | 18.43 | 42900 | 5.36 | 3.1667 | No
215852855 | Water Loop | DAIKIN | WSTH036F3*C/S*C |  | 38000 | 18.06 | 42900 | 5.25 | 3.1667 | No
215852858 | Water Loop | DAIKIN | WSTH042E1*C/S*C |  | 44000 | 17.59 | 50300 | 5.12 | 3.6667 | No
215852859 | Water Loop | DAIKIN | WSTH042F3*C/S*C |  | 44000 | 17.24 | 50300 | 5.02 | 3.6667 | No
215852868 | Water Loop | DAIKIN | WSTV024E1*C/S*C |  | 24300 | 17.59 | 28000 | 5.81 | 2.025 | No
215852869 | Water Loop | DAIKIN | WSTV024F3*C/S*C |  | 24300 | 17.24 | 28000 | 5.7 | 2.025 | No
206194171 | Water Loop | Johnson Controls | JSH/V/D030C*K B |  | 28000 | 17.3 | 35100 | 5.8 | 2.3333 | Yes
206194172 | Water Loop | SKYMARK | JSH/V/D030C*K C |  | 28000 | 17.3 | 35100 | 5.8 | 2.3333 | Yes
206194173 | Water Loop | Johnson Controls | JSH/V/D048C*K B |  | 48900 | 17.2 | 57700 | 5.2 | 4.075 | No
206194174 | Water Loop | SKYMARK | JSH/V/D048C*K C |  | 48900 | 17.2 | 57700 | 5.2 | 4.075 | No
206194175 | Water Loop | Johnson Controls | JSH/V/D060C*K B |  | 63200 | 17.2 | 73200 | 5.4 | 5.2667 | No
206194176 | Water Loop | SKYMARK | JSH/V/D060C*K C |  | 63200 | 17.2 | 73200 | 5.4 | 5.2667 | No
202835053 | Water Loop | BOSCH | SM036-1HZ*-*****C |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | Yes
202836307 | Water Loop | BOSCH | SM036-1VT*-*****C |  | 39300 | 18.6 | 46300 | 6.2 | 3.275 | Yes
7411100 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7411231 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7411380 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7411778 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7411949 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7412057 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7412253 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7412381 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
7414142 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
7414232 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7414335 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7414470 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
7414553 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7414651 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7414828 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
7414896 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7415098 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7415209 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
7415301 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
7415373 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
216625646 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D2**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625647 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D2**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
215837913 | Water Loop | DAIKIN | WSSH070F3*C/S*T |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
215837914 | Water Loop | DAIKIN | WSSH070K3*C/S*T |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
215837922 | Water Loop | DAIKIN | WSSH070F3*C/S*C |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
215837923 | Water Loop | DAIKIN | WSSH070K3*C/S*C |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
215851754 | Water Loop | DAIKIN | WSTH024J1*C/S*C |  | 24500 | 17.18 | 26100 | 5.19 | 2.0417 | No
215851756 | Water Loop | DAIKIN | WSTH024K3*C/S*C |  | 24500 | 17 | 26100 | 5.14 | 2.0417 | No
215851767 | Water Loop | DAIKIN | WSTH036J1*C/S*C |  | 38000 | 18.06 | 42900 | 5.25 | 3.1667 | No
215851769 | Water Loop | DAIKIN | WSTH036K3*C/S*C |  | 38000 | 17.88 | 42900 | 5.2 | 3.1667 | No
215851773 | Water Loop | DAIKIN | WSTH042K3*C/S*C |  | 44000 | 17.07 | 50300 | 4.97 | 3.6667 | No
10259035 | Water Loop | GEOCOMFORT | GZS015*****1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | Yes
10259036 | Water Loop | HYDRON MODULE | HZS015*****1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | Yes
10259037 | Water Loop | TETCO | TZS015*****1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | Yes
10259038 | Water Loop | GEOCOMFORT | GZS015*A***1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | No
10259039 | Water Loop | HYDRON MODULE | HZS015*A***1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | No
10259040 | Water Loop | TETCO | TZS015*A***1B |  | 14600 | 17.3 | 16700 | 5.5 | 1.2167 | No
10259054 | Water Loop | GEOCOMFORT | GZS017*****1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | Yes
10259055 | Water Loop | HYDRON MODULE | HZS017*****1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | Yes
10259056 | Water Loop | TETCO | TZS017*****1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | Yes
10259057 | Water Loop | GEOCOMFORT | GZS017*A***1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | No
10259058 | Water Loop | HYDRON MODULE | HZS017*A***1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | No
10259059 | Water Loop | TETCO | TZS017*A***1B |  | 17300 | 17.4 | 20400 | 5.6 | 1.4417 | No
10298936 | Water Loop | WaterFurnace | UVV/UVH036**0*1 |  | 37500 | 17.8 | 46000 | 5.4 | 3.125 | No
10298937 | Water Loop | WaterFurnace | UVV/UVH036**3*1 |  | 37500 | 17.8 | 46000 | 5.4 | 3.125 | No
10298938 | Water Loop | WaterFurnace | UVV/UVH036**4*1 |  | 37500 | 17.8 | 46000 | 5.4 | 3.125 | No
205996643 | Water Loop | Johnson Controls | JEV/H/D026B B |  | 25000 | 17.4 | 31400 | 6 | 2.0833 | No
205996644 | Water Loop | Johnson Controls | JEV/H/D038B B |  | 37700 | 17.9 | 45700 | 5.8 | 3.1417 | No
206570649 | Water Loop | 7 SERIES | NVV/NVH036C1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
206570652 | Water Loop | GEOSTAR | 141/142C036**1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
215268669 | Water Loop | WaterFurnace | V5A(V/H)036*S0**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
215268670 | Water Loop | WaterFurnace | V5A(V/H)042*S0**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
202921908 | Water Loop | BOSCH | EP036-1VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921909 | Water Loop | BOSCH | EP036-3VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921910 | Water Loop | BOSCH | EP036-4VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
202921911 | Water Loop | BOSCH-GEO | BP036-1VT*-*****B |  | 36000 | 17.1 | 41000 | 5.5 | 3 | No
214063756 | Water Loop | GeoSmart Energy | GBV/GBH024**2*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214063757 | Water Loop | GeoSmart Energy | GBV/GBH024**2*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214063762 | Water Loop | GeoSmart Energy | GBV/GBH030**0*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
214063763 | Water Loop | GeoSmart Energy | GBV/GBH030**0*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214063764 | Water Loop | GeoSmart Energy | GBV/GBH030**0*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214063765 | Water Loop | GeoSmart Energy | GBV/GBH030**2*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
214063766 | Water Loop | GeoSmart Energy | GBV/GBH030**2*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214063767 | Water Loop | GeoSmart Energy | GBV/GBH030**2*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
214063769 | Water Loop | GeoSmart Energy | GBV/GBH036**0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214063770 | Water Loop | GeoSmart Energy | GBV/GBH036**0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214063772 | Water Loop | GeoSmart Energy | GBV/GBH036**2*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214063773 | Water Loop | GeoSmart Energy | GBV/GBH036**2*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
214063774 | Water Loop | GeoSmart Energy | GBV/GBH038**0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214063775 | Water Loop | GeoSmart Energy | GBV/GBH038**0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214063776 | Water Loop | GeoSmart Energy | GBV/GBH038**2*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214063777 | Water Loop | GeoSmart Energy | GBV/GBH038**2*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
214063778 | Water Loop | GeoSmart Energy | GBV/GBH042**0*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214063779 | Water Loop | GeoSmart Energy | GBV/GBH042**0*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
214063780 | Water Loop | GeoSmart Energy | GBV/GBH049**0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
214063781 | Water Loop | GeoSmart Energy | GBV/GBH049**0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
215400080 | Water Loop | DAIKIN | WSMV015E1*C/S*T |  | 15500 | 17.51 | 17000 | 5.09 | 1.2917 | No
215400082 | Water Loop | DAIKIN | WSMV015E1*C/S*C |  | 15500 | 17.51 | 17000 | 5.09 | 1.2917 | No
215400094 | Water Loop | DAIKIN | WSMV024E1*C/S*T |  | 24700 | 18.03 | 28600 | 5.25 | 2.0583 | No
213710594 | Water Loop | DAIKIN | WSSH007A1*B*T |  | 7100 | 18.7 | 8100 | 6 | 0.59167 | No
213710599 | Water Loop | DAIKIN | WSSH007J1*B*T |  | 7100 | 18.7 | 8100 | 6 | 0.59167 | No
213710602 | Water Loop | DAIKIN | WSSH009A1*B*T |  | 9100 | 18 | 11200 | 5.6 | 0.75833 | No
213710607 | Water Loop | DAIKIN | WSSH009J1*B*T |  | 9100 | 17 | 11200 | 5.4 | 0.75833 | No
214772143 | Water Loop | TRANE | DXHK048A |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772144 | Water Loop | TRANE | DXHK060A |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772146 | Water Loop | TRANE | DXVK024B |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772147 | Water Loop | TRANE | DXVK0244 |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772148 | Water Loop | TRANE | DXVK036B |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772149 | Water Loop | TRANE | DXVK0364 |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772150 | Water Loop | TRANE | DXVK048B |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772151 | Water Loop | TRANE | DXVK0484 |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772152 | Water Loop | TRANE | DXVK060B |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772153 | Water Loop | TRANE | DXVK0604 |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772156 | Water Loop | TRANE | DXHK024B |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772157 | Water Loop | TRANE | DXHK0244 |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772158 | Water Loop | TRANE | DXHK036B |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772159 | Water Loop | TRANE | DXHK0364 |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772160 | Water Loop | TRANE | DXHK048B |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772161 | Water Loop | TRANE | DXHK0484 |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772162 | Water Loop | TRANE | DXHK060B |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772163 | Water Loop | TRANE | DXHK0604 |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
214772166 | Water Loop | TRANE | DXVK0247 |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772167 | Water Loop | TRANE | DXVK0367 |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772168 | Water Loop | TRANE | DXHK0247 |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772169 | Water Loop | TRANE | DXHK0367 |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214823484 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036BD1**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | Yes
217754395 | Water Loop | DAIKIN | WSSH042F1*B*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217754398 | Water Loop | DAIKIN | WSSH042F1*B*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217754401 | Water Loop | DAIKIN | WSSH048F1*B*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217754405 | Water Loop | DAIKIN | WSSH048F1*B*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
217754409 | Water Loop | DAIKIN | WSSH060F1*B*T |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
217754413 | Water Loop | DAIKIN | WSSH060F1*B*C |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
217754417 | Water Loop | DAIKIN | WSSH070F1*B*T |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
217754421 | Water Loop | DAIKIN | WSSH070F1*B*C |  | 70700 | 17.12 | 83100 | 4.76 | 5.8917 | No
203113888 | Water Loop | GEOSTAR | 103J036**1 | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
203238019 | Water Loop | BOSCH-GEO | BP042-1HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203253412 | Water Loop | BOSCH | BP042-1HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | Yes
203254606 | Water Loop | CARRIER | GB042H******1**1 |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
214595646 | Water Loop | AAON, Inc. | M2-006-2-H-GCAC-V0-10-000-A |  | 66700 | 17.8 | 54900 | 4.8 | 5.5583 | No
214595648 | Water Loop | AAON, Inc. | M2-006-3-H-GCAC-V0-10-000-A |  | 66700 | 17.8 | 54900 | 4.8 | 5.5583 | No
214595650 | Water Loop | AAON, Inc. | M2-006-4-H-GCAC-V0-10-000-A |  | 66700 | 17.8 | 54900 | 4.8 | 5.5583 | No
217193306 | Water Loop | WaterFurnace | V7A(V/H)024*V0**1* |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
217193307 | Water Loop | WaterFurnace | V7A(V/H)036*V0**1* |  | 37500 | 17.8 | 46000 | 5.5 | 3.125 | No
217193552 | Water Loop | WaterFurnace | V7A(V/H)024*V3**1* |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
217193553 | Water Loop | WaterFurnace | V7A(V/H)024*V4**1* |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
217193554 | Water Loop | WaterFurnace | V7A(V/H)036*V3**1* |  | 37500 | 17.8 | 46000 | 5.5 | 3.125 | No
217193555 | Water Loop | WaterFurnace | V7A(V/H)036*V4**1* |  | 37500 | 17.8 | 46000 | 5.5 | 3.125 | No
206342120 | Water Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*3 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
206342121 | Water Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*4 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
206342122 | Water Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*5 |  | 91000 | 17.2 | 100000 | 5.2 | 7.5833 | No
206345837 | Water Loop | HYDROTECH | WSS6006*7* |  | 8000 | 17 | 8800 | 5.4 | 0.66667 | No
5220980 | Water Loop | DAIKIN | WGTV/WGTH038B*E |  | 39000 | 17.6 | 44400 | 5.6 | 3.25 | No
5220981 | Water Loop | DAIKIN | WGTV/WGTH038B*F |  | 39000 | 17.6 | 44400 | 5.6 | 3.25 | No
5220982 | Water Loop | DAIKIN | WGTV/WGTH038B*K |  | 39000 | 17.6 | 44400 | 5.6 | 3.25 | No
5220983 | Water Loop | DAIKIN | WGTV/WGTH044B*E |  | 44400 | 17.3 | 50100 | 5.4 | 3.7 | No
5220984 | Water Loop | DAIKIN | WGTV/WGTH044B*F |  | 44400 | 17.3 | 50100 | 5.4 | 3.7 | No
5220985 | Water Loop | DAIKIN | WGTV/WGTH044B*K |  | 44400 | 17.3 | 50100 | 5.4 | 3.7 | No
5220990 | Water Loop | DAIKIN | WGTV/WGTH064B*E |  | 64800 | 17.4 | 76100 | 5.2 | 5.4 | No
5220991 | Water Loop | DAIKIN | WGTV/WGTH064B*F |  | 64800 | 17.4 | 76100 | 5.2 | 5.4 | No
5220992 | Water Loop | DAIKIN | WGTV/WGTH064B*K |  | 64800 | 17.4 | 76100 | 5.2 | 5.4 | No
208106952 | Water Loop | 5 SERIES GEO-READY | NGV/NGH038*1*(1,2) |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
208106953 | Water Loop | 5 SERIES GEO-READY | NGV/NGH049*1*(1,2) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
215400162 | Water Loop | DAIKIN | WSSV007A1*B*T |  | 7100 | 17.99 | 8100 | 5.49 | 0.59167 | No
215400166 | Water Loop | DAIKIN | WSSV009A1*B*T |  | 9200 | 17.49 | 11000 | 4.98 | 0.76667 | No
215400172 | Water Loop | DAIKIN | WSSV015E1*B*T |  | 16100 | 19.51 | 18600 | 5.82 | 1.3417 | No
215400174 | Water Loop | DAIKIN | WSSV015E1*B*C |  | 16100 | 19.51 | 18600 | 5.82 | 1.3417 | No
215400176 | Water Loop | DAIKIN | WSSV019E1*B*T |  | 19700 | 17.98 | 23500 | 5.33 | 1.6417 | No
215400178 | Water Loop | DAIKIN | WSSV019E1*B*C |  | 19700 | 17.98 | 23500 | 5.33 | 1.6417 | No
215400180 | Water Loop | DAIKIN | WSSV024J1*B*T |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215400181 | Water Loop | DAIKIN | WSSV024K3*B*T |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215400184 | Water Loop | DAIKIN | WSSV024J1*B*C |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215400185 | Water Loop | DAIKIN | WSSV024K3*B*C |  | 24400 | 17.91 | 28000 | 5.79 | 2.0333 | No
215400188 | Water Loop | DAIKIN | WSSV030J1*B*T |  | 29200 | 18.02 | 34500 | 5.67 | 2.4333 | No
215400189 | Water Loop | DAIKIN | WSSV030K3*B*T |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
215400192 | Water Loop | DAIKIN | WSSV030J1*B*C |  | 29200 | 18.02 | 34500 | 5.67 | 2.4333 | No
215400193 | Water Loop | DAIKIN | WSSV030K3*B*C |  | 29200 | 18.78 | 34500 | 5.91 | 2.4333 | No
215400196 | Water Loop | DAIKIN | WSSV036J1*B*T |  | 39000 | 17.94 | 44100 | 5.35 | 3.25 | No
215400197 | Water Loop | DAIKIN | WSSV036K3*B*T |  | 39000 | 18.32 | 44100 | 5.34 | 3.25 | No
215400200 | Water Loop | DAIKIN | WSSV036J1*B*C |  | 39000 | 17.94 | 44100 | 5.35 | 3.25 | No
215400201 | Water Loop | DAIKIN | WSSV036K3*B*C |  | 39000 | 18.32 | 44100 | 5.34 | 3.25 | No
215400204 | Water Loop | DAIKIN | WSSV042E1*B*T |  | 43000 | 18.36 | 47600 | 5.43 | 3.5833 | No
215400205 | Water Loop | DAIKIN | WSSV042F3*B*T |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
215400208 | Water Loop | DAIKIN | WSSV042E1*B*C |  | 43000 | 18.36 | 47600 | 5.43 | 3.5833 | No
217752676 | Water Loop | DAIKIN | WSSH024K1*B*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217752678 | Water Loop | DAIKIN | WSSH024K1*B*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217752680 | Water Loop | DAIKIN | WSSH030K1*B*T |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
217752682 | Water Loop | DAIKIN | WSSH030K1*B*C |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
217752684 | Water Loop | DAIKIN | WSSH036K1*B*T |  | 39000 | 18.59 | 44600 | 5.06 | 3.25 | No
217752686 | Water Loop | DAIKIN | WSSH036K1*B*C |  | 39000 | 18.59 | 44600 | 5.06 | 3.25 | No
214771937 | Water Loop | TRANE | EXVK036A |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214771938 | Water Loop | TRANE | EXVK042A |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214771939 | Water Loop | TRANE | EXVK048A |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214771940 | Water Loop | TRANE | EXVK060A |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
201907610 | Water Loop | WaterFurnace | URS036*0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907611 | Water Loop | WaterFurnace | URS036*0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907612 | Water Loop | WaterFurnace | URS036*0*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907613 | Water Loop | WaterFurnace | URS036*3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907614 | Water Loop | WaterFurnace | URS036*3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907615 | Water Loop | WaterFurnace | URS036*3*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907616 | Water Loop | WaterFurnace | URS036*4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907617 | Water Loop | WaterFurnace | URS036*4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
201907618 | Water Loop | WaterFurnace | URS036*4*5 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
206726680 | Water Loop | WaterFurnace | UVV/UVH024**0*1 |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
216739926 | Water Loop | DAIKIN | WSNH036E1*C/S*C |  | 35200 | 17.4 | 42500 | 5.3 | 2.9333 | No
216739927 | Water Loop | DAIKIN | WSNH036F3*C/S*C |  | 35200 | 17.1 | 42500 | 5.2 | 2.9333 | No
216739928 | Water Loop | DAIKIN | WSNH036J1*C/S*C |  | 35200 | 17.1 | 42500 | 5.2 | 2.9333 | No
215851795 | Water Loop | DAIKIN | WSTV024J1*C/S*C |  | 24300 | 17.24 | 28000 | 5.7 | 2.025 | No
215851796 | Water Loop | DAIKIN | WSTV024K3*C/S*C |  | 24300 | 17.06 | 28000 | 5.64 | 2.025 | No
215851809 | Water Loop | DAIKIN | WSTV036J1*C/S*C |  | 38100 | 18.08 | 41100 | 5.08 | 3.175 | No
215851810 | Water Loop | DAIKIN | WSTV036K3*C/S*C |  | 38100 | 17.89 | 41100 | 5.03 | 3.175 | No
215851818 | Water Loop | DAIKIN | WSTV048K3*C/S*C |  | 50800 | 17.27 | 58500 | 5.41 | 4.2333 | No
215851820 | Water Loop | DAIKIN | WSTV048L3*C/S*C |  | 50800 | 17.09 | 58500 | 5.35 | 4.2333 | No
215852846 | Water Loop | DAIKIN | WSTH024E1*C/S*C |  | 24500 | 17.53 | 26100 | 5.29 | 2.0417 | No
215852847 | Water Loop | DAIKIN | WSTH024F3*C/S*C |  | 24500 | 17.18 | 26100 | 5.19 | 2.0417 | No
215852850 | Water Loop | DAIKIN | WSTH030E1*C/S*C |  | 31400 | 17.12 | 34900 | 5.36 | 2.6167 | No
5599272 | Water Loop | BOSCH-GEO | SM036-1CF/HZ/VT |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
202443461 | Water Loop | GeoSmart Energy | GSZ036*1*J | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
202443470 | Water Loop | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
205767605 | Water Loop | ClimateMaster | VEV/H/D1860 |  | 48000 | 17.3 | 60000 | 5.5 | 4 | Yes
205767606 | Water Loop | ClimateMaster | VEV/H/D0930 |  | 24000 | 19.3 | 30000 | 6.6 | 2 | Yes
205767615 | Water Loop | ClimateMaster | QEV/H/D0930 |  | 24000 | 19.3 | 30000 | 6.6 | 2 | Yes
214771941 | Water Loop | TRANE | EXVK070A |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
214771953 | Water Loop | TRANE | EXHK009A |  | 8700 | 18.1 | 10700 | 6.4 | 0.725 | No
214771954 | Water Loop | TRANE | EXHK012A |  | 11400 | 17.1 | 14300 | 5.9 | 0.95 | No
214771956 | Water Loop | TRANE | EXHK018A |  | 18900 | 17.5 | 23000 | 5.43 | 1.575 | No
214771957 | Water Loop | TRANE | EXHK024A |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214771958 | Water Loop | TRANE | EXHK030A |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
214771959 | Water Loop | TRANE | EXHK036A |  | 35000 | 17.8 | 43600 | 5.62 | 2.9167 | No
214771960 | Water Loop | TRANE | EXHK042A |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214771961 | Water Loop | TRANE | EXHK048A |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214771962 | Water Loop | TRANE | EXHK060A |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214771963 | Water Loop | TRANE | EXHK070A |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
215415909 | Water Loop | CENTURY | ME(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 29000 | 5.7 | 2.1083 | Yes
215415910 | Water Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 29000 | 5.7 | 2.1083 | Yes
215415911 | Water Loop | CENTURY | ME(L/R/B/P/D/N/T/K)036A |  | 37500 | 17 | 43100 | 5.3 | 3.125 | Yes
215415912 | Water Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)036A |  | 37500 | 17 | 43100 | 5.3 | 3.125 | Yes
215415913 | Water Loop | CENTURY | ME(L/R/B/P/D/N/T/K)048A |  | 48000 | 17.2 | 60200 | 5.4 | 4 | Yes
215415914 | Water Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)048A |  | 48000 | 17.2 | 60200 | 5.4 | 4 | Yes
215415919 | Water Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 29000 | 5.7 | 2.1083 | No
215415920 | Water Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 29000 | 5.7 | 2.1083 | No
215415921 | Water Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)036A |  | 37500 | 17 | 43100 | 5.3 | 3.125 | No
215415922 | Water Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)036A |  | 37500 | 17 | 43100 | 5.3 | 3.125 | No
215415923 | Water Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)048A |  | 48000 | 17.2 | 60200 | 5.4 | 4 | No
215415924 | Water Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)048A |  | 48000 | 17.2 | 60200 | 5.4 | 4 | No
217754575 | Water Loop | DAIKIN | WSMH042E1*C/S*T |  | 39500 | 17 | 51400 | 5.4 | 3.2917 | No
217754581 | Water Loop | DAIKIN | WSMH042E1*C/S*C |  | 39500 | 17 | 51400 | 5.4 | 3.2917 | No
8740368 | Water Loop | GEOCOMFORT | GVS048*****1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | Yes
8740369 | Water Loop | HYDRON MODULE | HVS048*****1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | Yes
8740370 | Water Loop | TETCO | TVS048*****1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | Yes
8740371 | Water Loop | GEOCOMFORT | GVS048*2***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8740372 | Water Loop | HYDRON MODULE | HVS048*2***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8740373 | Water Loop | TETCO | TVS048*2***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8740374 | Water Loop | GEOCOMFORT | GVS048*3***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8740375 | Water Loop | HYDRON MODULE | HVS048*3***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
8740376 | Water Loop | TETCO | TVS048*3***1 |  | 49900 | 17.3 | 58400 | 5.5 | 4.1583 | No
6501951 | Water Loop | GEOSTAR | GBV/GBH042**0*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501952 | Water Loop | GEOSTAR | GBV/GBH042**0*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501954 | Water Loop | GEOSTAR | GBV/GBH042**3*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501955 | Water Loop | GEOSTAR | GBV/GBH042**3*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501957 | Water Loop | GEOSTAR | GBV/GBH042**4*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501958 | Water Loop | GEOSTAR | GBV/GBH042**4*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
6501970 | Water Loop | GEOSTAR | GBV/GBH049**0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6501971 | Water Loop | GEOSTAR | GBV/GBH049**0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6501972 | Water Loop | GEOSTAR | GBV/GBH049**3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6501973 | Water Loop | GEOSTAR | GBV/GBH049**3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6501974 | Water Loop | GEOSTAR | GBV/GBH049**4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
6501975 | Water Loop | GEOSTAR | GBV/GBH049**4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
200083642 | Water Loop | COMFORT-AIRE | HZV/H/D036B |  | 37700 | 17.9 | 45700 | 5.8 | 3.1417 | Yes
200083643 | Water Loop | CENTURY | HZV/H/D036B |  | 37700 | 17.9 | 45700 | 5.8 | 3.1417 | Yes
200083644 | Water Loop | COMFORT-AIRE | HZV/H/D024B |  | 25000 | 17.4 | 31400 | 6 | 2.0833 | Yes
200083645 | Water Loop | CENTURY | HZV/H/D024B |  | 25000 | 17.4 | 31400 | 6 | 2.0833 | Yes
216759817 | Water Loop | WaterFurnace | W5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
216759822 | Water Loop | GEOSTAR | G5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
216759827 | Water Loop | WaterFurnace | W5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
215837827 | Water Loop | DAIKIN | WSSH030F3*C/S*T |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
215837828 | Water Loop | DAIKIN | WSSH030J1*C/S*T |  | 29500 | 18.14 | 34500 | 5.64 | 2.4583 | No
215837829 | Water Loop | DAIKIN | WSSH030K3*C/S*T |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
215837835 | Water Loop | DAIKIN | WSSH030F3*C/S*C |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
215837836 | Water Loop | DAIKIN | WSSH030J1*C/S*C |  | 29500 | 18.14 | 34500 | 5.64 | 2.4583 | No
215837837 | Water Loop | DAIKIN | WSSH030K3*C/S*C |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
215837843 | Water Loop | DAIKIN | WSSH036F3*C/S*T |  | 39000 | 18.66 | 44600 | 5.06 | 3.25 | No
215837844 | Water Loop | DAIKIN | WSSH036J1*C/S*T |  | 39000 | 18.2 | 44600 | 5.07 | 3.25 | No
215837845 | Water Loop | DAIKIN | WSSH036K3*C/S*T |  | 39000 | 18.59 | 44600 | 5.06 | 3.25 | No
215837851 | Water Loop | DAIKIN | WSSH036F3*C/S*C |  | 39000 | 18.66 | 44600 | 5.06 | 3.25 | No
215837853 | Water Loop | DAIKIN | WSSH036J1*C/S*C |  | 39000 | 18.2 | 44600 | 5.07 | 3.25 | No
215837854 | Water Loop | DAIKIN | WSSH036K3*C/S*C |  | 39000 | 18.59 | 44600 | 5.06 | 3.25 | No
215837859 | Water Loop | DAIKIN | WSSH042F3*C/S*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837860 | Water Loop | DAIKIN | WSSH042J1*C/S*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837862 | Water Loop | DAIKIN | WSSH042K3*C/S*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837867 | Water Loop | DAIKIN | WSSH042F3*C/S*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217967025 | Water Loop | TRANE | VSVK050A |  | 50300 | 17.4 | 63000 | 5.8 | 4.1917 | No
217967028 | Water Loop | TRANE | VSHK024B |  | 24500 | 18.9 | 32000 | 6.7 | 2.0417 | No
217967029 | Water Loop | TRANE | VSVK024B |  | 25100 | 20.4 | 30500 | 6.6 | 2.0917 | No
217967031 | Water Loop | TRANE | VSVK033B |  | 33300 | 17 | 39900 | 6.1 | 2.775 | No
217967032 | Water Loop | TRANE | VSHK042B |  | 40300 | 17.9 | 50400 | 6.4 | 3.3583 | No
217967033 | Water Loop | TRANE | VSVK042B |  | 42900 | 18.8 | 54100 | 6.3 | 3.575 | No
217967035 | Water Loop | TRANE | VSVK050B |  | 50300 | 17.4 | 63000 | 5.8 | 4.1917 | No
217967038 | Water Loop | TRANE | VSHK0244 |  | 24500 | 18.9 | 32000 | 6.7 | 2.0417 | No
217967039 | Water Loop | TRANE | VSVK0244 |  | 25100 | 20.4 | 30500 | 6.6 | 2.0917 | No
217967041 | Water Loop | TRANE | VSVK0334 |  | 33300 | 17 | 39900 | 6.1 | 2.775 | No
217967042 | Water Loop | TRANE | VSHK0424 |  | 40300 | 17.9 | 50400 | 6.4 | 3.3583 | No
217967043 | Water Loop | TRANE | VSVK0424 |  | 42900 | 18.8 | 54100 | 6.3 | 3.575 | No
217967045 | Water Loop | TRANE | VSVK0504 |  | 50300 | 17.4 | 63000 | 5.8 | 4.1917 | No
206346927 | Water Loop | DAIKIN | WVFC*030*K***14 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
7499543 | Water Loop | FHP | LM024-1CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7499546 | Water Loop | FHP | LM024-2CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7499547 | Water Loop | FHP | LM024-3CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7499548 | Water Loop | FHP | LM024-4CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7499550 | Water Loop | FHP | LM036-1VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7499552 | Water Loop | FHP | LM036-2VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7499553 | Water Loop | FHP | LM036-3VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7499554 | Water Loop | FHP | LM036-4VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7499702 | Water Loop | BOSCH | SM036-1CF/HZ/VT |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | Yes
217754631 | Water Loop | DAIKIN | WSMV024F1*C/S*T |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
217754632 | Water Loop | DAIKIN | WSMV024K1*C/S*T |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
217754635 | Water Loop | DAIKIN | WSMV024F1*C/S*C |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
217754636 | Water Loop | DAIKIN | WSMV024K1*C/S*C |  | 24700 | 17.58 | 28600 | 5.12 | 2.0583 | No
217754655 | Water Loop | DAIKIN | WSMV036F1*C/S*T |  | 36800 | 17.09 | 42700 | 5.03 | 3.0667 | No
217754656 | Water Loop | DAIKIN | WSMV036K1*C/S*T |  | 36800 | 17.02 | 42700 | 5.03 | 3.0667 | No
217754659 | Water Loop | DAIKIN | WSMV036F1*C/S*C |  | 36800 | 17.09 | 42700 | 5.03 | 3.0667 | No
217754660 | Water Loop | DAIKIN | WSMV036K1*C/S*C |  | 36800 | 17.02 | 42700 | 5.03 | 3.0667 | No
7422309 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**4*1 |  | 70100 | 17 | 88000 | 4.8 | 5.8417 | No
216625542 | Water Loop | GEOSTAR | G5A(V/H)042*S4**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625543 | Water Loop | GEOSTAR | G5A(V/H)042*S2**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625636 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S0**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625637 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S0**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625638 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S2**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625639 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S2**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625640 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S3**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625641 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S3**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625642 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S4**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625643 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S4**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625644 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D0**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625645 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D0**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
214067608 | Water Loop | GeoSmart Energy | GBV/GBH072**4*1 |  | 70100 | 17 | 88000 | 4.8 | 5.8417 | No
215837869 | Water Loop | DAIKIN | WSSH042J1*C/S*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837870 | Water Loop | DAIKIN | WSSH042K3*C/S*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
215837877 | Water Loop | DAIKIN | WSSH048F3*C/S*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837879 | Water Loop | DAIKIN | WSSH048K3*C/S*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837880 | Water Loop | DAIKIN | WSSH048L3*C/S*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837886 | Water Loop | DAIKIN | WSSH048F3*C/S*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837887 | Water Loop | DAIKIN | WSSH048K3*C/S*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837889 | Water Loop | DAIKIN | WSSH048L3*C/S*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
215837895 | Water Loop | DAIKIN | WSSH060F3*C/S*T |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
215837896 | Water Loop | DAIKIN | WSSH060K3*C/S*T |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
215837904 | Water Loop | DAIKIN | WSSH060F3*C/S*C |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
215837905 | Water Loop | DAIKIN | WSSH060K3*C/S*C |  | 60872 | 17.22 | 78027 | 5.66 | 5.0727 | No
217897465 | Water Loop | CENTURY | MJN036A | MAN036A | 36400 | 17.3 | 39400 | 5.3 | 3.0333 | Yes
217897466 | Water Loop | COMFORT-AIRE | MJN036A | MAN036A | 36400 | 17.3 | 39400 | 5.3 | 3.0333 | Yes
216621339 | Water Loop | GEOSTAR | G5A(V/H)036*D0**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216621340 | Water Loop | GEOSTAR | G5A(V/H)036*D3**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216621341 | Water Loop | GEOSTAR | G5A(V/H)036*D0**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216621342 | Water Loop | GEOSTAR | G5A(V/H)036*D3**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
215268667 | Water Loop | WaterFurnace | V5A(V/H)024*S0**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
215268668 | Water Loop | WaterFurnace | V5A(V/H)030*S0**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
205129920 | Water Loop | 5 SERIES INDOOR SPLITS | NSZ036J1 | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
205129921 | Water Loop | GEOSTAR | 103J036**1 | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
214063753 | Water Loop | GeoSmart Energy | GBV/GBH024**0*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
214063754 | Water Loop | GeoSmart Energy | GBV/GBH024**0*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
215402570 | Water Loop | DAIKIN | WSSV036E1*B*C |  | 39000 | 19.02 | 44100 | 5.35 | 3.25 | No
215402571 | Water Loop | DAIKIN | WSSV036F3*B*C |  | 39000 | 18.4 | 44100 | 5.34 | 3.25 | No
217752728 | Water Loop | DAIKIN | WSTH036K1*B*C |  | 38000 | 17.88 | 42900 | 5.2 | 3.1667 | No
217752730 | Water Loop | DAIKIN | WSTH042K1*B*C |  | 44000 | 17.07 | 50300 | 4.97 | 3.6667 | No
217752744 | Water Loop | DAIKIN | WSTV024K1*B*C |  | 24300 | 17.06 | 28000 | 5.64 | 2.025 | No
217752748 | Water Loop | DAIKIN | WSTV036K1*B*C |  | 38100 | 17.89 | 41100 | 5.03 | 3.175 | No
217752752 | Water Loop | DAIKIN | WSTV048K1*B*C |  | 50800 | 17.27 | 58500 | 5.41 | 4.2333 | No
217752753 | Water Loop | DAIKIN | WSTV048L1*B*C |  | 50800 | 17.09 | 58500 | 5.35 | 4.2333 | No
217754377 | Water Loop | DAIKIN | WSSH024F1*B*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217754380 | Water Loop | DAIKIN | WSSH024F1*B*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217754383 | Water Loop | DAIKIN | WSSH030F1*B*T |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
217754386 | Water Loop | DAIKIN | WSSH030F1*B*C |  | 29500 | 18.91 | 34500 | 5.88 | 2.4583 | No
217754389 | Water Loop | DAIKIN | WSSH036F1*B*T |  | 39000 | 18.66 | 44600 | 5.06 | 3.25 | No
217754392 | Water Loop | DAIKIN | WSSH036F1*B*C |  | 39000 | 18.66 | 44600 | 5.06 | 3.25 | No
8964157 | Water Loop | BRYANT | GC036C/H/V******1*X1 + UI |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | Yes
8964158 | Water Loop | CARRIER | GC036C/H/V******1**1 + UI |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | Yes
215866231 | Water Loop | ClimateMaster | SMT24A*L |  | 25000 | 17.6 | 28000 | 5.1 | 2.0833 | No
215866538 | Water Loop | DAIKIN | WSTH048E1*C/S*C |  | 48200 | 17.34 | 56900 | 5.08 | 4.0167 | No
207349387 | Water Loop | WaterFurnace | NBV/NBH038**0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349388 | Water Loop | WaterFurnace | NBV/NBH038**3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349389 | Water Loop | WaterFurnace | NBV/NBH038**2*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349390 | Water Loop | WaterFurnace | NBV/NBH038**4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349391 | Water Loop | WaterFurnace | NBV/NBH038**0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349392 | Water Loop | WaterFurnace | NBV/NBH038**3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349393 | Water Loop | WaterFurnace | NBV/NBH038**4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349394 | Water Loop | WaterFurnace | NBV/NBH038**2*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207349395 | Water Loop | WaterFurnace | NBV/NBH049**0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349396 | Water Loop | WaterFurnace | NBV/NBH049**3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349397 | Water Loop | WaterFurnace | NBV/NBH049**4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349398 | Water Loop | WaterFurnace | NBV/NBH049**0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349399 | Water Loop | WaterFurnace | NBV/NBH049**3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207349400 | Water Loop | WaterFurnace | NBV/NBH049**4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
216625463 | Water Loop | GEOSTAR | G5A(V/H)024*S2**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625464 | Water Loop | GEOSTAR | G5A(V/H)024*S3**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625465 | Water Loop | GEOSTAR | G5A(V/H)024*S4**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625466 | Water Loop | GEOSTAR | G5A(V/H)024*S0**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625467 | Water Loop | GEOSTAR | G5A(V/H)024*S2**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625468 | Water Loop | GEOSTAR | G5A(V/H)024*S3**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625469 | Water Loop | GEOSTAR | G5A(V/H)024*S4**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625470 | Water Loop | GEOSTAR | G5A(V/H)030*S2**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625471 | Water Loop | GEOSTAR | G5A(V/H)030*S3**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625472 | Water Loop | GEOSTAR | G5A(V/H)030*S4**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625473 | Water Loop | GEOSTAR | G5A(V/H)030*S0**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625474 | Water Loop | GEOSTAR | G5A(V/H)030*S2**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625475 | Water Loop | GEOSTAR | G5A(V/H)030*S3**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625476 | Water Loop | GEOSTAR | G5A(V/H)030*S4**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625477 | Water Loop | GEOSTAR | G5A(V/H)030*D2**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625478 | Water Loop | GEOSTAR | G5A(V/H)030*D4**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625479 | Water Loop | GEOSTAR | G5A(V/H)030*D2**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625480 | Water Loop | GEOSTAR | G5A(V/H)030*D4**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625481 | Water Loop | GEOSTAR | G5A(V/H)036*S2**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625482 | Water Loop | GEOSTAR | G5A(V/H)036*S3**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625483 | Water Loop | GEOSTAR | G5A(V/H)036*S4**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625484 | Water Loop | GEOSTAR | G5A(V/H)036*S0**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625485 | Water Loop | GEOSTAR | G5A(V/H)036*S2**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625486 | Water Loop | GEOSTAR | G5A(V/H)036*S3**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625487 | Water Loop | GEOSTAR | G5A(V/H)036*S4**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625488 | Water Loop | GEOSTAR | G5A(V/H)036*S0**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625489 | Water Loop | GEOSTAR | G5A(V/H)036*S2**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625490 | Water Loop | GEOSTAR | G5A(V/H)036*S3**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625491 | Water Loop | GEOSTAR | G5A(V/H)036*S4**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625492 | Water Loop | GEOSTAR | G5A(V/H)036*D2**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625493 | Water Loop | GEOSTAR | G5A(V/H)036*D4**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625494 | Water Loop | GEOSTAR | G5A(V/H)036*D2**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625495 | Water Loop | GEOSTAR | G5A(V/H)036*D4**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625496 | Water Loop | GEOSTAR | G5A(V/H)036*D2**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625497 | Water Loop | GEOSTAR | G5A(V/H)036*D4**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625498 | Water Loop | GEOSTAR | G5A(V/H)042*S3**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625499 | Water Loop | GEOSTAR | G5A(V/H)042*S0**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625500 | Water Loop | GEOSTAR | G5A(V/H)042*S3**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625501 | Water Loop | GEOSTAR | G5A(V/H)042*S4**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625502 | Water Loop | GEOSTAR | G5A(V/H)042*S0**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625503 | Water Loop | GEOSTAR | G5A(V/H)042*S3**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625504 | Water Loop | GEOSTAR | G5A(V/H)042*S4**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
203380966 | Water Loop | BOSCH | EP042-1HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203380967 | Water Loop | BOSCH | EP042-3HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203380968 | Water Loop | BOSCH | EP042-4HZ*******B |  | 38400 | 17.15 | 42000 | 5.8 | 3.2 | No
203383883 | Water Loop | CARRIER | 50PSH042***3/CA |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203383884 | Water Loop | CARRIER | 50PSH042***5/EA |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203383885 | Water Loop | CARRIER | 50PSH042***6/FA |  | 38400 | 17.15 | 42000 | 5.8 | 3.2 | No
211594245 | Water Loop | TRANE | EXHG0187 |  | 18800 | 17.6 | 23600 | 5.7 | 1.5667 | No
211594246 | Water Loop | TRANE | EXHG024B |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
211594247 | Water Loop | TRANE | EXHG0244 |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
211594248 | Water Loop | TRANE | EXHG0247 |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
211594249 | Water Loop | TRANE | EXHG030B |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
211594250 | Water Loop | TRANE | EXHG0304 |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
211594251 | Water Loop | TRANE | EXHG0307 |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
211594252 | Water Loop | TRANE | EXHG036B |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
5295998 | Water Loop | WaterFurnace | NBV/NBH030**3*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5295999 | Water Loop | WaterFurnace | NBV/NBH030**4*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5296000 | Water Loop | WaterFurnace | NBV/NBH030**4*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5296001 | Water Loop | WaterFurnace | NBV/NBH030**3*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5296002 | Water Loop | WaterFurnace | NBV/NBH030**0*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5296003 | Water Loop | WaterFurnace | NBV/NBH030**2*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5296008 | Water Loop | WaterFurnace | NBV/NBH036**0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296009 | Water Loop | WaterFurnace | NBV/NBH036**3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296010 | Water Loop | WaterFurnace | NBV/NBH036**4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296011 | Water Loop | WaterFurnace | NBV/NBH036**2*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296012 | Water Loop | WaterFurnace | NBV/NBH036**2*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296013 | Water Loop | WaterFurnace | NBV/NBH036**0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296014 | Water Loop | WaterFurnace | NBV/NBH036**3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296015 | Water Loop | WaterFurnace | NBV/NBH036**4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
5296225 | Water Loop | WaterFurnace | NBV/NBH042**0*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
5296226 | Water Loop | WaterFurnace | NBV/NBH042**3*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
5296227 | Water Loop | WaterFurnace | NBV/NBH042**4*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
5296228 | Water Loop | WaterFurnace | NBV/NBH042**4*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
5296229 | Water Loop | WaterFurnace | NBV/NBH042**3*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
5296230 | Water Loop | WaterFurnace | NBV/NBH042**0*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
9910756 | Water Loop | HYDRON MODULE | HZS060*2***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
9910757 | Water Loop | TETCO | TZS060*2***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
9910758 | Water Loop | GEOCOMFORT | GZS060*3***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
9910759 | Water Loop | HYDRON MODULE | HZS060*3***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
9910760 | Water Loop | TETCO | TZS060*3***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
205767514 | Water Loop | ClimateMaster | TSH/V/D024C*K |  | 23900 | 17.9 | 30400 | 6.1 | 1.9917 | Yes
205767516 | Water Loop | ClimateMaster | TSH/V/D030C*K |  | 28000 | 17.3 | 35100 | 5.8 | 2.3333 | Yes
205767517 | Water Loop | ClimateMaster | TSH/V/D036C |  | 33400 | 17 | 40400 | 5.6 | 2.7833 | Yes
205767518 | Water Loop | ClimateMaster | TSH/V/D036C*K |  | 33500 | 18.1 | 39900 | 5.9 | 2.7917 | Yes
205767519 | Water Loop | ClimateMaster | TSH/V/D042C |  | 38500 | 17.2 | 46300 | 5.6 | 3.2083 | Yes
205767520 | Water Loop | ClimateMaster | TSH/V/D042C*K |  | 39400 | 19.6 | 45100 | 6 | 3.2833 | Yes
205767521 | Water Loop | ClimateMaster | TSH/V/D048C*K |  | 48900 | 17.2 | 57700 | 5.2 | 4.075 | Yes
205767523 | Water Loop | ClimateMaster | TSH/V/D060C*K |  | 63200 | 17.2 | 73200 | 5.4 | 5.2667 | Yes
217903468 | Water Loop | WaterFurnace | V5R036*D0**1* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903469 | Water Loop | WaterFurnace | V5R036*D0**4* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903470 | Water Loop | WaterFurnace | V5R036*D0**5* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903471 | Water Loop | WaterFurnace | V5R036*D3**1* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903472 | Water Loop | WaterFurnace | V5R036*D3**4* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
217903473 | Water Loop | WaterFurnace | V5R036*D3**5* |  | 34900 | 17.2 | 41600 | 5.9 | 2.9083 | No
9063207 | Water Loop | DAIKIN | WVFC1030*K***01 |  | 30000 | 17 | 33400 | 5.2 | 2.5 | No
216625770 | Water Loop | GeoSmart Energy | S5A(V/H)024*S0**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625771 | Water Loop | GeoSmart Energy | S5A(V/H)024*S0**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625772 | Water Loop | GeoSmart Energy | S5A(V/H)024*S2**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625773 | Water Loop | GeoSmart Energy | S5A(V/H)024*S2**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625774 | Water Loop | GeoSmart Energy | S5A(V/H)024*S3**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625775 | Water Loop | GeoSmart Energy | S5A(V/H)024*S3**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625776 | Water Loop | GeoSmart Energy | S5A(V/H)024*S4**1 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625777 | Water Loop | GeoSmart Energy | S5A(V/H)024*S4**4 |  | 24500 | 17.5 | 30000 | 5.4 | 2.0417 | No
216625778 | Water Loop | GeoSmart Energy | S5A(V/H)030*D0**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625779 | Water Loop | GeoSmart Energy | S5A(V/H)030*D0**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625780 | Water Loop | GeoSmart Energy | S5A(V/H)030*D2**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625781 | Water Loop | GeoSmart Energy | S5A(V/H)030*D2**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625782 | Water Loop | GeoSmart Energy | S5A(V/H)030*D3**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625783 | Water Loop | GeoSmart Energy | S5A(V/H)030*D3**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625784 | Water Loop | GeoSmart Energy | S5A(V/H)030*D4**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625785 | Water Loop | GeoSmart Energy | S5A(V/H)030*D4**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625786 | Water Loop | GeoSmart Energy | S5A(V/H)030*S0**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625787 | Water Loop | GeoSmart Energy | S5A(V/H)030*S0**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625788 | Water Loop | GeoSmart Energy | S5A(V/H)030*S2**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625789 | Water Loop | GeoSmart Energy | S5A(V/H)030*S2**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625790 | Water Loop | GeoSmart Energy | S5A(V/H)030*S3**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625791 | Water Loop | GeoSmart Energy | S5A(V/H)030*S3**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625792 | Water Loop | GeoSmart Energy | S5A(V/H)030*S4**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625793 | Water Loop | GeoSmart Energy | S5A(V/H)030*S4**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625794 | Water Loop | GeoSmart Energy | S5A(V/H)036*D0**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625795 | Water Loop | GeoSmart Energy | S5A(V/H)036*D0**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625796 | Water Loop | GeoSmart Energy | S5A(V/H)036*D0**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625797 | Water Loop | GeoSmart Energy | S5A(V/H)036*D2**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625798 | Water Loop | GeoSmart Energy | S5A(V/H)036*D2**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625799 | Water Loop | GeoSmart Energy | S5A(V/H)036*D2**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625800 | Water Loop | GeoSmart Energy | S5A(V/H)036*D3**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625801 | Water Loop | GeoSmart Energy | S5A(V/H)036*D3**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625802 | Water Loop | GeoSmart Energy | S5A(V/H)036*D3**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625803 | Water Loop | GeoSmart Energy | S5A(V/H)036*D4**1 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625804 | Water Loop | GeoSmart Energy | S5A(V/H)036*D4**2 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625805 | Water Loop | GeoSmart Energy | S5A(V/H)036*D4**4 |  | 36400 | 17.9 | 43300 | 6.1 | 3.0333 | No
216625806 | Water Loop | GeoSmart Energy | S5A(V/H)036*S0**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625807 | Water Loop | GeoSmart Energy | S5A(V/H)036*S0**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625808 | Water Loop | GeoSmart Energy | S5A(V/H)036*S0**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625809 | Water Loop | GeoSmart Energy | S5A(V/H)036*S2**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625810 | Water Loop | GeoSmart Energy | S5A(V/H)036*S2**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625811 | Water Loop | GeoSmart Energy | S5A(V/H)036*S2**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625812 | Water Loop | GeoSmart Energy | S5A(V/H)036*S3**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625813 | Water Loop | GeoSmart Energy | S5A(V/H)036*S3**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625814 | Water Loop | GeoSmart Energy | S5A(V/H)036*S3**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625815 | Water Loop | GeoSmart Energy | S5A(V/H)036*S4**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
207335399 | Water Loop | GeoSmart Energy | GT049**1*(1,2,4)*K |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207335407 | Water Loop | GeoSmart Energy | GS030**1*(0,3)*J |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | Yes
207335408 | Water Loop | GeoSmart Energy | GS030**1*(1,4)*J |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | Yes
207335409 | Water Loop | GeoSmart Energy | GS036**1*(0,3)*K |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | Yes
207335514 | Water Loop | GeoSmart Energy | GS042**1*(1,2,4)*K |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | Yes
207335573 | Water Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****J |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | Yes
207335575 | Water Loop | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*K |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | Yes
207335580 | Water Loop | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,4)*K |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207335581 | Water Loop | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,4)*K |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207335585 | Water Loop | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*J |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207335586 | Water Loop | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*J |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207335590 | Water Loop | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*K |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207335591 | Water Loop | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*K |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
202211051 | Water Loop | WaterFurnace | URD049*3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202211052 | Water Loop | WaterFurnace | URD049*3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202211053 | Water Loop | WaterFurnace | URD049*3*5 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
202262237 | Water Loop | 5 SERIES INDOOR SPLITS | NSZ036J1 | SAH036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
206726691 | Water Loop | WaterFurnace | UVV/UVH024**3*1 |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
206726692 | Water Loop | WaterFurnace | UVV/UVH024**4*1 |  | 23500 | 18.7 | 29300 | 5.9 | 1.9583 | No
206726812 | Water Loop | GEOCOMFORT | GBS018 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | Yes
206726813 | Water Loop | GEOCOMFORT | GBS018 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | Yes
206726814 | Water Loop | HYDRON MODULE | HBS018 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | Yes
206726815 | Water Loop | HYDRON MODULE | HBS018 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | Yes
206726816 | Water Loop | TETCO | TBS018 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | Yes
206726817 | Water Loop | TETCO | TBS018 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | Yes
206726818 | Water Loop | GEOCOMFORT | GBS018*2 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
206726819 | Water Loop | GEOCOMFORT | GBS018*2 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | No
206726820 | Water Loop | HYDRON MODULE | HBS018*2 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
206726821 | Water Loop | HYDRON MODULE | HBS018*2 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | No
206726822 | Water Loop | TETCO | TBS018*2 | EED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
206726823 | Water Loop | TETCO | TBS018*2 | EAD018 | 20700 | 17.7 | 23300 | 6 | 1.725 | No
217735426 | Water Loop | DAIKIN | WSSH024J1*B*T |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217735427 | Water Loop | DAIKIN | WSSH024J1*B*C |  | 24500 | 17.65 | 28000 | 5.68 | 2.0417 | No
217735428 | Water Loop | DAIKIN | WSSH030J1*B*T |  | 29500 | 18.14 | 34500 | 5.64 | 2.4583 | No
217735429 | Water Loop | DAIKIN | WSSH030J1*B*C |  | 29500 | 18.14 | 34500 | 5.64 | 2.4583 | No
217735430 | Water Loop | DAIKIN | WSSH036J1*B*T |  | 39000 | 18.2 | 44600 | 5.07 | 3.25 | No
217735431 | Water Loop | DAIKIN | WSSH036J1*B*C |  | 39000 | 18.2 | 44600 | 5.07 | 3.25 | No
217735432 | Water Loop | DAIKIN | WSSH042J1*B*T |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217735433 | Water Loop | DAIKIN | WSSH042J1*B*C |  | 42600 | 18.03 | 47000 | 5.29 | 3.55 | No
217735434 | Water Loop | DAIKIN | WSTH024J1*B*C |  | 24500 | 17.18 | 26100 | 5.19 | 2.0417 | No
217037827 | Water Loop | GeoSmart Energy | S5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
211127895 | Water Loop | WaterFurnace | NVV/NVH036D1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
211127898 | Water Loop | GEOSTAR | 141/142D036**1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
215746922 | Water Loop | TRANE | GSK120A3 |  | 127028 | 17.5 | 156912 | 6 | 10.5857 | No
215746923 | Water Loop | TRANE | GSK036A4 |  | 40281 | 19.2 | 47492 | 6.06 | 3.3567 | No
215746924 | Water Loop | TRANE | GSK036AW |  | 40281 | 19.2 | 47492 | 6.06 | 3.3567 | No
215746925 | Water Loop | TRANE | GSK048A4 |  | 53537 | 17.6 | 62760 | 5.79 | 4.4614 | No
215746926 | Water Loop | TRANE | GSK048AW |  | 53537 | 17.6 | 62760 | 5.79 | 4.4614 | No
215746927 | Water Loop | TRANE | GSK060A4 |  | 64919 | 17.4 | 76308 | 5.61 | 5.4099 | No
215746928 | Water Loop | TRANE | GSK060AW |  | 64919 | 17.4 | 76308 | 5.61 | 5.4099 | No
215746929 | Water Loop | TRANE | GSK072A4 |  | 84370 | 18.1 | 92045 | 5.75 | 7.0308 | No
215746930 | Water Loop | TRANE | GSK072AW |  | 84370 | 18.1 | 92045 | 5.75 | 7.0308 | No
215746931 | Water Loop | TRANE | GSK090A4 |  | 99665 | 17.8 | 109831 | 5.66 | 8.3054 | No
215746932 | Water Loop | TRANE | GSK090AW |  | 99665 | 17.8 | 109831 | 5.66 | 8.3054 | No
215746935 | Water Loop | TRANE | GSK120A4 |  | 127028 | 17.5 | 156912 | 6 | 10.5857 | No
215746936 | Water Loop | TRANE | GSK120AW |  | 127028 | 17.5 | 156912 | 6 | 10.5857 | No
215748227 | Water Loop | ClimateMaster | SMT(S,M)24A*Q |  | 25000 | 17.6 | 28000 | 5.1 | 2.0833 | No
215748230 | Water Loop | ClimateMaster | SMT(S,M)30A*Q |  | 30000 | 17 | 35500 | 5.3 | 2.5 | No
8735903 | Water Loop | GEOCOMFORT | GVS042*****1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | Yes
8735904 | Water Loop | HYDRON MODULE | HVS042*****1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | Yes
8735905 | Water Loop | TETCO | TVS042*****1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | Yes
8735906 | Water Loop | GEOCOMFORT | GVS042*2***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
8735907 | Water Loop | HYDRON MODULE | HVS042*2***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
8735908 | Water Loop | TETCO | TVS042*2***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
8735909 | Water Loop | GEOCOMFORT | GVS042*3***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
8735910 | Water Loop | HYDRON MODULE | HVS042*3***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
8735911 | Water Loop | TETCO | TVS042*3***1 |  | 42900 | 18.3 | 47800 | 5.9 | 3.575 | No
207177466 | Water Loop | TRANE | EXVG018A |  | 18800 | 17.6 | 23600 | 5.7 | 1.5667 | No
207177467 | Water Loop | TRANE | EXVG0187 |  | 18800 | 17.6 | 23600 | 5.7 | 1.5667 | No
207177468 | Water Loop | TRANE | EXVG024A |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
207177469 | Water Loop | TRANE | EXVG024B |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
207177470 | Water Loop | TRANE | EXVG0244 |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
207177471 | Water Loop | TRANE | EXVG0247 |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
207177472 | Water Loop | TRANE | EXVG030A |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
207177473 | Water Loop | TRANE | EXVG030B |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
207177474 | Water Loop | TRANE | EXVG0304 |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
207177475 | Water Loop | TRANE | EXVG0307 |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
207177476 | Water Loop | TRANE | EXVG036A |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
207177477 | Water Loop | TRANE | EXVG036B |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
207177478 | Water Loop | TRANE | EXVG0364 |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
207177479 | Water Loop | TRANE | EXVG0367 |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
207177480 | Water Loop | TRANE | EXVG042A |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
207177481 | Water Loop | TRANE | EXVG042B |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
207177482 | Water Loop | TRANE | EXVG0424 |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
207177483 | Water Loop | TRANE | EXVG048A |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
207177484 | Water Loop | TRANE | EXVG048B |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
207177485 | Water Loop | TRANE | EXVG0484 |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
207177486 | Water Loop | TRANE | EXVG060A |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
207177487 | Water Loop | TRANE | EXVG060B |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
207177488 | Water Loop | TRANE | EXVG0604 |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
207177489 | Water Loop | TRANE | EXVG070A |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
207177490 | Water Loop | TRANE | EXVG070B |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
207177491 | Water Loop | TRANE | EXVG0704 |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
207177496 | Water Loop | TRANE | DXVG036A |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
207177497 | Water Loop | TRANE | DXVG036B |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
207177498 | Water Loop | TRANE | DXVG0364 |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
207177499 | Water Loop | TRANE | DXVG0367 |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
207177500 | Water Loop | TRANE | DXVG048A |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
207177501 | Water Loop | TRANE | DXVG048B |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
207177502 | Water Loop | TRANE | DXVG0484 |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
207177503 | Water Loop | TRANE | DXVG060A |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
207177504 | Water Loop | TRANE | DXVG060B |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
207177505 | Water Loop | TRANE | DXVG0604 |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
207177506 | Water Loop | TRANE | DXVG070A |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
207177507 | Water Loop | TRANE | DXVG070B |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
207177508 | Water Loop | TRANE | DXVG0704 |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
211594132 | Water Loop | TRANE | EXHG018A |  | 18800 | 17.6 | 23600 | 5.7 | 1.5667 | No
211594133 | Water Loop | TRANE | EXHG024A |  | 24600 | 17.4 | 32100 | 5.7 | 2.05 | No
211594134 | Water Loop | TRANE | EXHG030A |  | 31400 | 17.8 | 38400 | 5.8 | 2.6167 | No
211594135 | Water Loop | TRANE | EXHG036A |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
211594136 | Water Loop | TRANE | EXHG042A |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
211594137 | Water Loop | TRANE | EXHG048A |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
211594138 | Water Loop | TRANE | EXHG060A |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
211594139 | Water Loop | TRANE | EXHG070A |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
211594213 | Water Loop | TRANE | DXHG036A |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
211594214 | Water Loop | TRANE | DXHG048A |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
211594215 | Water Loop | TRANE | DXHG060A |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
211594216 | Water Loop | TRANE | DXHG070A |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
203383899 | Water Loop | FHP | EP042-1HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203383900 | Water Loop | FHP | EP042-3HZ*******B |  | 38400 | 17.15 | 42400 | 5.8 | 3.2 | No
203383901 | Water Loop | FHP | EP042-4HZ*******B |  | 38400 | 17.15 | 42000 | 5.8 | 3.2 | No
207335253 | Water Loop | GEOSTAR | 161/162K049**1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207335398 | Water Loop | GeoSmart Energy | GT038**1*(1,2,4)*K |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
202330563 | Water Loop | AAON, Inc. | M2-006-2-H-BCAC-V0-10-000-A |  | 66700 | 18.2 | 57200 | 4.9 | 5.5583 | No
202330567 | Water Loop | AAON, Inc. | M2-006-3-H-BCAC-V0-10-000-A |  | 66700 | 18.2 | 57200 | 4.9 | 5.5583 | No
206598629 | Water Loop | GeoSmart Energy | VI036**1*(1,2)** |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
206598632 | Water Loop | YORK BY JOHNSON CONTROLS | YAFV036**1*(1,2)** |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | Yes
9910449 | Water Loop | GEOCOMFORT | GZS018*****1B |  | 19900 | 17.3 | 22600 | 5.4 | 1.6583 | Yes
4947178 | Water Loop | TRANE | VSVE0241 |  | 24600 | 18.44 | 30300 | 6.1 | 2.05 | No
4947179 | Water Loop | TRANE | VSVE0242 |  | 24600 | 18.44 | 30300 | 6.1 | 2.05 | No
4947180 | Water Loop | TRANE | VSVE0244 |  | 24600 | 18.44 | 30300 | 6.1 | 2.05 | No
5220663 | Water Loop | DAIKIN | WGSV/WGSH015B*E |  | 15300 | 18.1 | 19100 | 5.9 | 1.275 | No
6502006 | Water Loop | GEOSTAR | GBV/GBH072**4*1 |  | 70100 | 17 | 88000 | 4.8 | 5.8417 | No
6674620 | Water Loop | BOSCH | LM024-1CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
6674621 | Water Loop | BOSCH | LM024-3CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
6674622 | Water Loop | BOSCH | LM024-2CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
6674623 | Water Loop | BOSCH | LM024-4CF/HZ/VT*-*****A |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
6676515 | Water Loop | BOSCH | LM036-1VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
6676516 | Water Loop | BOSCH | LM036-3VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
6676518 | Water Loop | BOSCH | LM036-2VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
6676519 | Water Loop | BOSCH | LM036-4VT/CF/HZ*-*****A |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
216772568 | Water Loop | Enertech | EVS018* |  | 21300 | 20.5 | 23700 | 6.3 | 1.775 | Yes
216772569 | Water Loop | Enertech | EVT024* |  | 24650 | 17.5 | 29100 | 5.6 | 2.0542 | Yes
217735438 | Water Loop | DAIKIN | WSTH036J1*B*C |  | 38000 | 18.06 | 42900 | 5.25 | 3.1667 | No
217735440 | Water Loop | DAIKIN | WSTV024J1*B*C |  | 24300 | 17.24 | 28000 | 5.7 | 2.025 | No
217735444 | Water Loop | DAIKIN | WSTV036J1*B*C |  | 38100 | 18.08 | 41100 | 5.08 | 3.175 | No
216625816 | Water Loop | GeoSmart Energy | S5A(V/H)036*S4**2 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625817 | Water Loop | GeoSmart Energy | S5A(V/H)036*S4**4 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
216625828 | Water Loop | GeoSmart Energy | S5A(V/H)042*S0**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625829 | Water Loop | GeoSmart Energy | S5A(V/H)042*S0**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625830 | Water Loop | GeoSmart Energy | S5A(V/H)042*S0**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625831 | Water Loop | GeoSmart Energy | S5A(V/H)042*S2**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625832 | Water Loop | GeoSmart Energy | S5A(V/H)042*S3**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625833 | Water Loop | GeoSmart Energy | S5A(V/H)042*S3**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625834 | Water Loop | GeoSmart Energy | S5A(V/H)042*S3**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625835 | Water Loop | GeoSmart Energy | S5A(V/H)042*S4**1 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625836 | Water Loop | GeoSmart Energy | S5A(V/H)042*S4**2 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
216625837 | Water Loop | GeoSmart Energy | S5A(V/H)042*S4**4 |  | 42000 | 18.4 | 49000 | 6 | 3.5 | No
5220675 | Water Loop | DAIKIN | WGSV/WGSH030B*E |  | 30000 | 17.3 | 33600 | 5.8 | 2.5 | No
5220676 | Water Loop | DAIKIN | WGSV/WGSH030B*F |  | 30000 | 17.3 | 33600 | 5.8 | 2.5 | No
5220677 | Water Loop | DAIKIN | WGSV/WGSH030B*J |  | 30000 | 17.3 | 33600 | 5.8 | 2.5 | No
5220678 | Water Loop | DAIKIN | WGSV/WGSH030B*K |  | 30000 | 17.3 | 33600 | 5.8 | 2.5 | No
5220681 | Water Loop | DAIKIN | WGSV/WGSH036B*E |  | 37300 | 19.2 | 40800 | 6 | 3.1083 | No
5220682 | Water Loop | DAIKIN | WGSV/WGSH036B*F |  | 37300 | 19.2 | 40800 | 6 | 3.1083 | No
5220683 | Water Loop | DAIKIN | WGSV/WGSH036B*J |  | 37300 | 19.2 | 40800 | 6 | 3.1083 | No
5220684 | Water Loop | DAIKIN | WGSV/WGSH036B*K |  | 37300 | 19.2 | 40800 | 6 | 3.1083 | No
5220686 | Water Loop | DAIKIN | WGSV/WGSH042B*E |  | 43900 | 17.5 | 48600 | 5.4 | 3.6583 | No
5220687 | Water Loop | DAIKIN | WGSV/WGSH042B*F |  | 43900 | 17.5 | 48600 | 5.4 | 3.6583 | No
5220688 | Water Loop | DAIKIN | WGSV/WGSH042B*K |  | 43900 | 17.5 | 48600 | 5.4 | 3.6583 | No
5220690 | Water Loop | DAIKIN | WGSV/WGSH048B*E |  | 50500 | 17.2 | 57100 | 5.4 | 4.2083 | No
5220691 | Water Loop | DAIKIN | WGSV/WGSH048B*F |  | 50500 | 17.2 | 57100 | 5.4 | 4.2083 | No
5220693 | Water Loop | DAIKIN | WGSV/WGSH048B*K |  | 50500 | 17.2 | 57100 | 5.4 | 4.2083 | No
5220700 | Water Loop | DAIKIN | WGSV/WGSH060B*E |  | 63700 | 17.4 | 74200 | 5.2 | 5.3083 | No
5220701 | Water Loop | DAIKIN | WGSV/WGSH060B*F |  | 63700 | 17.4 | 74200 | 5.2 | 5.3083 | No
5220702 | Water Loop | DAIKIN | WGSV/WGSH060B*K |  | 63700 | 17.4 | 74200 | 5.2 | 5.3083 | No
7415878 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7416559 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7416782 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7416889 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7417060 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7417146 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7417329 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7417419 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
7417586 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7417698 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7417776 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7417867 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7417918 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7417992 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7418047 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7418154 | Water Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
7418360 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7418435 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7418635 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*1 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
7418715 | Water Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*4 |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
207349409 | Water Loop | WaterFurnace | NBV/NBH072**4*1 |  | 70100 | 17 | 88000 | 4.8 | 5.8417 | No
4218842 | Water Loop | DAIKIN | WVFC1030*E***01 |  | 30000 | 17 | 33400 | 5.2 | 2.5 | No
4218843 | Water Loop | DAIKIN | WVFC1030*F***01 |  | 30000 | 17 | 33400 | 5.2 | 2.5 | No
4218844 | Water Loop | DAIKIN | WVFC1030*J***01 |  | 30000 | 17 | 33400 | 5.2 | 2.5 | No
214771931 | Water Loop | TRANE | EXVK009A |  | 8700 | 18.1 | 10700 | 6.4 | 0.725 | No
214771932 | Water Loop | TRANE | EXVK012A |  | 11400 | 17.1 | 14300 | 5.9 | 0.95 | No
214771934 | Water Loop | TRANE | EXVK018A |  | 18900 | 17.5 | 23000 | 5.43 | 1.575 | No
214771935 | Water Loop | TRANE | EXVK024A |  | 25300 | 18.1 | 32000 | 5.55 | 2.1083 | No
214771936 | Water Loop | TRANE | EXVK030A |  | 30200 | 17.9 | 37500 | 5.74 | 2.5167 | No
9910752 | Water Loop | GEOCOMFORT | GZS060*****1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | Yes
9910753 | Water Loop | HYDRON MODULE | HZS060*****1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | Yes
9910754 | Water Loop | TETCO | TZS060*****1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | Yes
9910755 | Water Loop | GEOCOMFORT | GZS060*2***1B |  | 59300 | 17 | 74700 | 5.3 | 4.9417 | No
215285739 | Water Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)024A |  | 25300 | 17 | 29000 | 5.7 | 2.1083 | Yes
215285740 | Water Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)036A |  | 37500 | 17 | 43100 | 5.3 | 3.125 | Yes
215285741 | Water Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)048A |  | 48000 | 17.2 | 60200 | 5.4 | 4 | Yes
211594253 | Water Loop | TRANE | EXHG0364 |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
211594254 | Water Loop | TRANE | EXHG0367 |  | 35500 | 17.6 | 43100 | 5.8 | 2.9583 | No
211594255 | Water Loop | TRANE | EXHG042B |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
211594256 | Water Loop | TRANE | EXHG0424 |  | 38400 | 18 | 48000 | 6.4 | 3.2 | No
211594257 | Water Loop | TRANE | EXHG048B |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
211594258 | Water Loop | TRANE | EXHG0484 |  | 45400 | 17.7 | 55600 | 6.1 | 3.7833 | No
211594259 | Water Loop | TRANE | EXHG060B |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
211594260 | Water Loop | TRANE | EXHG0604 |  | 55700 | 17.5 | 69000 | 5.9 | 4.6417 | No
211594261 | Water Loop | TRANE | EXHG070B |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
211594262 | Water Loop | TRANE | EXHG0704 |  | 63800 | 17.3 | 82100 | 5.4 | 5.3167 | No
211594266 | Water Loop | TRANE | DXHG036B |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
211594267 | Water Loop | TRANE | DXHG0364 |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
211594268 | Water Loop | TRANE | DXHG0367 |  | 33000 | 17.3 | 40900 | 5.9 | 2.75 | No
211594269 | Water Loop | TRANE | DXHG048B |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
211594270 | Water Loop | TRANE | DXHG0484 |  | 45200 | 17.9 | 55200 | 6.1 | 3.7667 | No
211594271 | Water Loop | TRANE | DXHG060B |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
211594272 | Water Loop | TRANE | DXHG0604 |  | 52100 | 17.6 | 63900 | 6 | 4.3417 | No
211594273 | Water Loop | TRANE | DXHG070B |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
211594274 | Water Loop | TRANE | DXHG0704 |  | 64400 | 17.3 | 82700 | 5.4 | 5.3667 | No
216687114 | Water Loop | WaterFurnace | W5SS036BD1 | W5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
216687119 | Water Loop | WaterFurnace | W5SZ036BD1 | W5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
216687732 | Water Loop | GEOSTAR | G5SS036BD1 | G5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
216687737 | Water Loop | GEOSTAR | G5SZ036BD1 | G5BM036BN1**2 | 35300 | 17.1 | 41800 | 5.6 | 2.9417 | Yes
7167538 | Water Loop | CARRIER | 50PTD/H/V024***3/CA |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7167539 | Water Loop | CARRIER | 50PTD/H/V024***5/EA |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7167540 | Water Loop | CARRIER | 50PTD/H/V024***4/DA |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7167541 | Water Loop | CARRIER | 50PTD/H/V024***6/FA |  | 25500 | 17.4 | 29200 | 5.6 | 2.125 | No
7167542 | Water Loop | CARRIER | 50PTD/H/V036***3/CA |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7167543 | Water Loop | CARRIER | 50PTD/H/V036***5/EA |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7167544 | Water Loop | CARRIER | 50PTD/H/V036***4/DA |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
7167545 | Water Loop | CARRIER | 50PTD/H/V036***6/FA |  | 38100 | 17.45 | 42800 | 5.1 | 3.175 | No
216014181 | Water Loop | RHEEM | RPVV/H/D036D |  | 37700 | 17.9 | 45700 | 5.8 | 3.1417 | Yes
216054107 | Water Loop | WaterFurnace | W5TV036BD1**2 |  | 36000 | 17.9 | 42300 | 5.6 | 3 | Yes
217967018 | Water Loop | TRANE | VSHK024A |  | 24500 | 18.9 | 32000 | 6.7 | 2.0417 | No
217967019 | Water Loop | TRANE | VSVK024A |  | 25100 | 20.4 | 30500 | 6.6 | 2.0917 | No
217967021 | Water Loop | TRANE | VSVK033A |  | 33300 | 17 | 39900 | 6.1 | 2.775 | No
217967022 | Water Loop | TRANE | VSHK042A |  | 40300 | 17.9 | 50400 | 6.4 | 3.3583 | No
217967023 | Water Loop | TRANE | VSVK042A |  | 42900 | 18.8 | 54100 | 6.3 | 3.575 | No
6501900 | Water Loop | GEOSTAR | GBV/GBH024**0*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501901 | Water Loop | GEOSTAR | GBV/GBH024**0*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501903 | Water Loop | GEOSTAR | GBV/GBH024**2*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501904 | Water Loop | GEOSTAR | GBV/GBH024**2*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501906 | Water Loop | GEOSTAR | GBV/GBH024**3*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501907 | Water Loop | GEOSTAR | GBV/GBH024**3*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501909 | Water Loop | GEOSTAR | GBV/GBH024**4*1 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501910 | Water Loop | GEOSTAR | GBV/GBH024**4*4 |  | 24800 | 17 | 30000 | 5.3 | 2.0667 | No
6501918 | Water Loop | GEOSTAR | GBV/GBH030**0*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
6501919 | Water Loop | GEOSTAR | GBV/GBH030**0*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501920 | Water Loop | GEOSTAR | GBV/GBH030**0*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501921 | Water Loop | GEOSTAR | GBV/GBH030**2*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
6501922 | Water Loop | GEOSTAR | GBV/GBH030**2*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501923 | Water Loop | GEOSTAR | GBV/GBH030**2*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501924 | Water Loop | GEOSTAR | GBV/GBH030**3*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
6501925 | Water Loop | GEOSTAR | GBV/GBH030**3*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501926 | Water Loop | GEOSTAR | GBV/GBH030**3*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501927 | Water Loop | GEOSTAR | GBV/GBH030**4*0 |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
6501928 | Water Loop | GEOSTAR | GBV/GBH030**4*1 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501929 | Water Loop | GEOSTAR | GBV/GBH030**4*4 |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
6501931 | Water Loop | GEOSTAR | GBV/GBH036**0*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501932 | Water Loop | GEOSTAR | GBV/GBH036**0*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501934 | Water Loop | GEOSTAR | GBV/GBH036**2*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501935 | Water Loop | GEOSTAR | GBV/GBH036**2*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501937 | Water Loop | GEOSTAR | GBV/GBH036**3*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501938 | Water Loop | GEOSTAR | GBV/GBH036**3*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501940 | Water Loop | GEOSTAR | GBV/GBH036**4*1 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501941 | Water Loop | GEOSTAR | GBV/GBH036**4*4 |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
6501942 | Water Loop | GEOSTAR | GBV/GBH038**0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501943 | Water Loop | GEOSTAR | GBV/GBH038**0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501944 | Water Loop | GEOSTAR | GBV/GBH038**2*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501945 | Water Loop | GEOSTAR | GBV/GBH038**2*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
6501946 | Water Loop | GEOSTAR | GBV/GBH038**3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
215399856 | Water Loop | DAIKIN | WSSV015A1*B*T |  | 16100 | 19.51 | 18600 | 5.82 | 1.3417 | No
215399857 | Water Loop | DAIKIN | WSSV015J1*B*T |  | 16100 | 18.01 | 18600 | 5.72 | 1.3417 | No
215399860 | Water Loop | DAIKIN | WSSV015A1*B*C |  | 16100 | 19.51 | 18600 | 5.82 | 1.3417 | No
215399861 | Water Loop | DAIKIN | WSSV015J1*B*C |  | 16100 | 18.01 | 18600 | 5.72 | 1.3417 | No
215399864 | Water Loop | DAIKIN | WSSV019J1*B*T |  | 19600 | 17.18 | 23500 | 5.23 | 1.6333 | No
215399866 | Water Loop | DAIKIN | WSSV019J1*B*C |  | 19600 | 17.18 | 23500 | 5.23 | 1.6333 | No
215399868 | Water Loop | DAIKIN | WSSV042J1*B*T |  | 42570 | 18.17 | 47124 | 5.38 | 3.5475 | No
215399869 | Water Loop | DAIKIN | WSSV042K3*B*T |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
215399872 | Water Loop | DAIKIN | WSSV042J1*B*C |  | 42570 | 18.17 | 47124 | 5.38 | 3.5475 | No
215399873 | Water Loop | DAIKIN | WSSV042K3*B*C |  | 42140 | 17.99 | 46648 | 5.32 | 3.5117 | No
215399876 | Water Loop | DAIKIN | WSSV048K3*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215399877 | Water Loop | DAIKIN | WSSV048L3*B*T |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215399880 | Water Loop | DAIKIN | WSSV048K3*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215399881 | Water Loop | DAIKIN | WSSV048L3*B*C |  | 50600 | 17.57 | 59100 | 5.74 | 4.2167 | No
215399884 | Water Loop | DAIKIN | WSSV060K3*B*T |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
215399886 | Water Loop | DAIKIN | WSSV060K3*B*C |  | 64000 | 17.23 | 78000 | 5.25 | 5.3333 | No
209156974 | Water Loop | AE Air | WSS6006*6* |  | 8000 | 17 | 8800 | 5.4 | 0.66667 | No
209156993 | Water Loop | AE Air | WSS6006*7* |  | 8000 | 17 | 8800 | 5.4 | 0.66667 | No
205782239 | Water Loop | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
205782243 | Water Loop | GeoSmart Energy | GSZ036*1*J | SRAA036* | 29100 | 17.4 | 35600 | 5.8 | 2.425 | Yes
205788279 | Water Loop | Johnson Controls | JSH/V/D024C*K B |  | 23900 | 17.9 | 30400 | 6.1 | 1.9917 | No
205788280 | Water Loop | SKYMARK | JSH/V/D024C*K C |  | 23900 | 17.9 | 30400 | 6.1 | 1.9917 | No
205788283 | Water Loop | Johnson Controls | JSH/V/D036C B |  | 33400 | 17 | 40400 | 5.6 | 2.7833 | No
205788284 | Water Loop | SKYMARK | JSH/V/D036C C |  | 33400 | 17 | 40400 | 5.6 | 2.7833 | No
205788285 | Water Loop | Johnson Controls | JSH/V/D036C*K B |  | 33500 | 18.1 | 39900 | 5.9 | 2.7917 | No
205788286 | Water Loop | SKYMARK | JSH/V/D036C*K C |  | 33500 | 18.1 | 39900 | 5.9 | 2.7917 | No
205788287 | Water Loop | Johnson Controls | JSH/V/D042C B |  | 38500 | 17.2 | 46300 | 5.6 | 3.2083 | No
205788288 | Water Loop | SKYMARK | JSH/V/D042C C |  | 38500 | 17.2 | 46300 | 5.6 | 3.2083 | No
205788289 | Water Loop | Johnson Controls | JSH/V/D042C*K B |  | 39400 | 19.6 | 45100 | 6 | 3.2833 | Yes
205788290 | Water Loop | SKYMARK | JSH/V/D042C*K C |  | 39400 | 19.6 | 45100 | 6 | 3.2833 | Yes
214772087 | Water Loop | TRANE | EXVK042B |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214772088 | Water Loop | TRANE | EXVK0424 |  | 42000 | 17.8 | 48800 | 5.93 | 3.5 | No
214772089 | Water Loop | TRANE | EXVK048B |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214772090 | Water Loop | TRANE | EXVK0484 |  | 45300 | 17.5 | 51800 | 5.83 | 3.775 | No
214772091 | Water Loop | TRANE | EXVK060B |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214772092 | Water Loop | TRANE | EXVK0604 |  | 60600 | 17 | 72100 | 5.39 | 5.05 | No
214772093 | Water Loop | TRANE | EXVK070B |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
214772094 | Water Loop | TRANE | EXVK0704 |  | 63400 | 17.6 | 77000 | 5.5 | 5.2833 | No
214772095 | Water Loop | TRANE | DXVK024A |  | 25400 | 18.9 | 31100 | 5.8 | 2.1167 | No
214772096 | Water Loop | TRANE | DXVK036A |  | 32100 | 17.9 | 41800 | 6.1 | 2.675 | No
214772097 | Water Loop | TRANE | DXVK048A |  | 44800 | 17.7 | 53700 | 6.1 | 3.7333 | No
214772098 | Water Loop | TRANE | DXVK060A |  | 54500 | 18.5 | 67000 | 6.2 | 4.5417 | No
213710618 | Water Loop | DAIKIN | WSSH015A1*B*T |  | 16100 | 19.7 | 18000 | 5.76 | 1.3417 | No
213710619 | Water Loop | DAIKIN | WSSH015A1*B*C |  | 16100 | 19.7 | 18000 | 5.76 | 1.3417 | No
213710626 | Water Loop | DAIKIN | WSSH015J1*B*T |  | 16100 | 18.2 | 18000 | 5.7 | 1.3417 | No
213710627 | Water Loop | DAIKIN | WSSH015J1*B*C |  | 16100 | 18.2 | 18000 | 5.7 | 1.3417 | No
213710636 | Water Loop | DAIKIN | WSSH019J1*B*T |  | 19900 | 17.7 | 23300 | 5.3 | 1.6583 | No
213710637 | Water Loop | DAIKIN | WSSH019J1*B*C |  | 19900 | 17.7 | 23300 | 5.3 | 1.6583 | No
213711957 | Water Loop | DAIKIN | WSSH007E1*B*T |  | 7100 | 18.7 | 8100 | 6 | 0.59167 | No
213711959 | Water Loop | DAIKIN | WSSH009E1*B*T |  | 9100 | 18 | 11200 | 5.6 | 0.75833 | No
213711963 | Water Loop | DAIKIN | WSSH015E1*B*T |  | 16100 | 19.95 | 18000 | 5.76 | 1.3417 | No
213711964 | Water Loop | DAIKIN | WSSH015E1*B*C |  | 16100 | 19.95 | 18000 | 5.76 | 1.3417 | No
213711966 | Water Loop | DAIKIN | WSSH019E1*B*T |  | 19900 | 18 | 23300 | 5.3 | 1.6583 | No
213711967 | Water Loop | DAIKIN | WSSH019E1*B*C |  | 19900 | 18 | 23300 | 5.3 | 1.6583 | No
213711969 | Water Loop | DAIKIN | WSSH024E1*B*T |  | 24500 | 18.1 | 28000 | 5.8 | 2.0417 | No
213711970 | Water Loop | DAIKIN | WSSH024E1*B*C |  | 24500 | 18.1 | 28000 | 5.8 | 2.0417 | No
213711972 | Water Loop | DAIKIN | WSSH030E1*B*T |  | 29500 | 19.3 | 34500 | 6 | 2.4583 | No
213711974 | Water Loop | DAIKIN | WSSH030E1*B*C |  | 29500 | 19.3 | 34500 | 6 | 2.4583 | No
213711975 | Water Loop | DAIKIN | WSSH036E1*B*T |  | 39000 | 19.3 | 44600 | 5.2 | 3.25 | No
213711976 | Water Loop | DAIKIN | WSSH036E1*B*C |  | 39000 | 19.3 | 44600 | 5.2 | 3.25 | No
213711978 | Water Loop | DAIKIN | WSSH042E1*B*T |  | 42600 | 18.4 | 47000 | 5.4 | 3.55 | No
213711979 | Water Loop | DAIKIN | WSSH042E1*B*C |  | 42600 | 18.4 | 47000 | 5.4 | 3.55 | No
213711981 | Water Loop | DAIKIN | WSSH048E1*B*T |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
213711982 | Water Loop | DAIKIN | WSSH048E1*B*C |  | 48300 | 17.5 | 57000 | 5 | 4.025 | No
213711984 | Water Loop | DAIKIN | WSSH060E1*B*T |  | 60872 | 17.4 | 78027 | 5.72 | 5.0727 | No
213711986 | Water Loop | DAIKIN | WSSH060E1*B*C |  | 60872 | 17.4 | 78027 | 5.72 | 5.0727 | No
213714593 | Water Loop | DAIKIN | WSSH070E1*B*T |  | 70700 | 17.29 | 83100 | 4.81 | 5.8917 | No
213714595 | Water Loop | DAIKIN | WSSH070E1*B*C |  | 70700 | 17.29 | 83100 | 4.81 | 5.8917 | No
5699505 | Water Loop | TRANE | VSVE0421 |  | 44100 | 18.25 | 54700 | 5.95 | 3.675 | No
5699525 | Water Loop | TRANE | VSVE0422 |  | 44100 | 18.25 | 54700 | 5.95 | 3.675 | No
5699526 | Water Loop | TRANE | VSVE0424 |  | 44100 | 18.25 | 54700 | 5.95 | 3.675 | No
5699628 | Water Loop | TRANE | VSHE0241 |  | 25100 | 18.3 | 30300 | 6.44 | 2.0917 | No
5699631 | Water Loop | TRANE | VSHE0242 |  | 25100 | 18.3 | 30300 | 6.44 | 2.0917 | No
5699633 | Water Loop | TRANE | VSHE0244 |  | 25100 | 18.3 | 30300 | 6.44 | 2.0917 | No
5699639 | Water Loop | TRANE | VSHE0421 |  | 42600 | 18.6 | 51800 | 6.7 | 3.55 | No
5699644 | Water Loop | TRANE | VSHE0422 |  | 42600 | 18.6 | 51800 | 6.7 | 3.55 | No
5699650 | Water Loop | TRANE | VSHE0424 |  | 42600 | 18.6 | 51800 | 6.7 | 3.55 | No
217754509 | Water Loop | DAIKIN | WSTV036E1*B*C |  | 38100 | 18.45 | 41100 | 5.18 | 3.175 | No
217754510 | Water Loop | DAIKIN | WSTV036F1*B*C |  | 38100 | 18.08 | 41100 | 5.08 | 3.175 | No
217754513 | Water Loop | DAIKIN | WSTV042E1*B*C |  | 43500 | 17.3 | 50000 | 5.06 | 3.625 | No
217754517 | Water Loop | DAIKIN | WSTV048E1*B*C |  | 50800 | 17.62 | 58500 | 5.52 | 4.2333 | No
217754518 | Water Loop | DAIKIN | WSTV048F1*B*C |  | 50800 | 17.27 | 58500 | 5.41 | 4.2333 | No
217754521 | Water Loop | DAIKIN | WSTV060E1*B*C |  | 60500 | 17.3 | 74700 | 5.5 | 5.0417 | No
217754537 | Water Loop | DAIKIN | WSMH024F1*C/S*T |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
217754538 | Water Loop | DAIKIN | WSMH024K1*C/S*T |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
217754541 | Water Loop | DAIKIN | WSMH024F1*C/S*C |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
217754542 | Water Loop | DAIKIN | WSMH024K1*C/S*C |  | 24800 | 17.06 | 30700 | 5.46 | 2.0667 | No
217754549 | Water Loop | DAIKIN | WSMH030F1*C/S*T |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
217754550 | Water Loop | DAIKIN | WSMH030K1*C/S*T |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
217754553 | Water Loop | DAIKIN | WSMH030F1*C/S*C |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
217754554 | Water Loop | DAIKIN | WSMH030K1*C/S*C |  | 28300 | 17.25 | 35300 | 5.59 | 2.3583 | No
213502523 | Water Loop | DAIKIN | WSMH015A1*C/S*T |  | 15500 | 17.8 | 19900 | 5.9 | 1.2917 | No
213502524 | Water Loop | DAIKIN | WSMH015A1*C/S*C |  | 15500 | 17.8 | 19900 | 5.9 | 1.2917 | No
213502529 | Water Loop | DAIKIN | WSMH015E1*C/S*T |  | 15500 | 17.8 | 20000 | 5.9 | 1.2917 | No
213502530 | Water Loop | DAIKIN | WSMH015E1*C/S*C |  | 15500 | 17.8 | 20000 | 5.9 | 1.2917 | No
213502535 | Water Loop | DAIKIN | WSMH015J1*C/S*T |  | 15400 | 17 | 20000 | 5.8 | 1.2833 | No
213502536 | Water Loop | DAIKIN | WSMH015J1*C/S*C |  | 15400 | 17 | 20000 | 5.8 | 1.2833 | No
213502541 | Water Loop | DAIKIN | WSMH019E1*C/S*T |  | 19700 | 17 | 24200 | 5.2 | 1.6417 | No
213502542 | Water Loop | DAIKIN | WSMH019E1*C/S*C |  | 19700 | 17 | 24200 | 5.2 | 1.6417 | No
213502547 | Water Loop | DAIKIN | WSMH019J1*C/S*T |  | 19700 | 17 | 24200 | 5.1 | 1.6417 | No
213502548 | Water Loop | DAIKIN | WSMH019J1*C/S*C |  | 19700 | 17 | 24200 | 5.1 | 1.6417 | No
213502553 | Water Loop | DAIKIN | WSMH024E1*C/S*T |  | 24800 | 17.5 | 30700 | 5.6 | 2.0667 | No
213502554 | Water Loop | DAIKIN | WSMH024E1*C/S*C |  | 24800 | 17.5 | 30700 | 5.6 | 2.0667 | No
213502559 | Water Loop | DAIKIN | WSMH030E1*C/S*T |  | 28300 | 17.6 | 35300 | 5.7 | 2.3583 | No
213502560 | Water Loop | DAIKIN | WSMH030E1*C/S*C |  | 28300 | 17.6 | 35300 | 5.7 | 2.3583 | No
213502565 | Water Loop | DAIKIN | WSMH036E1*C/S*T |  | 36500 | 17.2 | 48300 | 5.4 | 3.0417 | No
213502566 | Water Loop | DAIKIN | WSMH036E1*C/S*C |  | 36500 | 17.2 | 48300 | 5.4 | 3.0417 | No
213502571 | Water Loop | DAIKIN | WSCH042E1*C/S*T |  | 39500 | 17 | 51400 | 5.4 | 3.2917 | No
213502572 | Water Loop | DAIKIN | WSCH042E1*C/S*C |  | 39500 | 17 | 51400 | 5.4 | 3.2917 | No
216625648 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D3**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625649 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D3**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625650 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D4**1 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625651 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D4**4 |  | 30800 | 17.3 | 38600 | 5.6 | 2.5667 | No
216625652 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S0**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625653 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S0**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625654 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S2**1 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
216625655 | Water Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S2**4 |  | 30000 | 17.5 | 36000 | 5.3 | 2.5 | No
5317193 | Water Loop | WaterFurnace | NBV/NBH038**0*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317194 | Water Loop | WaterFurnace | NBV/NBH038**3*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317195 | Water Loop | WaterFurnace | NBV/NBH038**2*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317196 | Water Loop | WaterFurnace | NBV/NBH038**4*1 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317197 | Water Loop | WaterFurnace | NBV/NBH038**0*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317198 | Water Loop | WaterFurnace | NBV/NBH038**3*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317199 | Water Loop | WaterFurnace | NBV/NBH038**4*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317200 | Water Loop | WaterFurnace | NBV/NBH038**2*4 |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
5317201 | Water Loop | WaterFurnace | NBV/NBH049**0*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317202 | Water Loop | WaterFurnace | NBV/NBH049**3*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317203 | Water Loop | WaterFurnace | NBV/NBH049**4*4 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317205 | Water Loop | WaterFurnace | NBV/NBH049**0*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317206 | Water Loop | WaterFurnace | NBV/NBH049**3*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317207 | Water Loop | WaterFurnace | NBV/NBH049**4*1 |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5317332 | Water Loop | WaterFurnace | NBV/NBH072**4*1 |  | 70100 | 17 | 88000 | 4.8 | 5.8417 | No
215268734 | Water Loop | WaterFurnace | V5A(V/H)036*S2**1 |  | 36000 | 18.8 | 39000 | 5.8 | 3 | No
207312172 | Water Loop | WaterFurnace | NDV/NDH038K1*(1,2,4) |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | Yes
207312173 | Water Loop | WaterFurnace | NDV/NDH049K1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | Yes
207312225 | Water Loop | WaterFurnace | NSV/NSH030J1*(1,4) |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | Yes
207312226 | Water Loop | WaterFurnace | NSV/NSH036K1*(1,2,4) |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | Yes
207312227 | Water Loop | WaterFurnace | NSV/NSH042K1*(1,2,4) |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | Yes
207312265 | Water Loop | WaterFurnace | NSV/NSH030J1*(0,3) |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | Yes
203495469 | Water Loop | GEOSTAR | 101/102J049**1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
8560938 | Water Loop | GEOCOMFORT | GVS015 |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | Yes
8560939 | Water Loop | HYDRON MODULE | HVS015 |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | Yes
8560940 | Water Loop | TETCO | TVS015 |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | Yes
8560941 | Water Loop | GEOCOMFORT | GVS015*A |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | No
8560942 | Water Loop | HYDRON MODULE | HVS015*A |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | No
8560943 | Water Loop | TETCO | TVS015*A |  | 15100 | 17.5 | 17900 | 6 | 1.2583 | No
8560946 | Water Loop | GEOCOMFORT | GVS015*****1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | Yes
8560947 | Water Loop | HYDRON MODULE | HVS015*****1 |  | 15200 | 18.8 | 17700 | 6.4 | 1.2667 | Yes
10581109 | Water Loop | 5 SERIES | NDP038H1*(1,2) |  | 36500 | 17 | 41900 | 5.4 | 3.0417 | No
204031802 | Water Loop | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,2,4)*J |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207178494 | Water Loop | GEOSTAR | 161/162J049**1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
207178527 | Water Loop | GEOSTAR | 161/162J038**1*(1,2,4)***** |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202443468 | Water Loop | YORK BY JOHNSON CONTROLS | YAFS036**1*(1,2,4)*J |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
202443469 | Water Loop | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*J |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
8103479 | Water Loop | TRANE | DXHF0241 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
8105907 | Water Loop | TRANE | DXHF0242 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
8105909 | Water Loop | TRANE | DXHF0243 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
8105911 | Water Loop | TRANE | DXHF0244 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
8105912 | Water Loop | TRANE | DXHF0247 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
6581203 | Water Loop | YORK BY JOHNSON CONTROLS | YAFS022**1*(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
204344184 | Water Loop | 7 SERIES | NVV/NVH036B1*(1,2) |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
5696567 | Water Loop | 5 SERIES | NSV/NSH022G1*(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
5708463 | Water Loop | AMERICAN STANDARD | A1GX022***1**(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
5708493 | Water Loop | TRANE/AMERICAN STANDARD | T1GX022***1**(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
5708550 | Water Loop | GEOSTAR | 101/102A022**1*(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
5708623 | Water Loop | GeoSmart Energy | GS022**1*(0,3) |  | 21000 | 17.5 | 22600 | 5.6 | 1.75 | No
4217883 | Water Loop | DAIKIN | WCCH4015*E*04* |  | 16000 | 17.6 | 18100 | 5.6 | 1.3333 | No
4217885 | Water Loop | DAIKIN | WCCH4015*J*04* |  | 15600 | 17.6 | 17200 | 5.6 | 1.3 | No
203363069 | Water Loop | WILLIAMS | EW010A1D*A |  | 30000 | 17 | 34800 | 5.5 | 2.5 | No
205536344 | Water Loop | AAON, Inc. | WV-072-2-0-DCAC-C0-10-200-A |  | 81000 | 17 | 96200 | 5.4 | 6.75 | No
205536348 | Water Loop | AAON, Inc. | WV-072-3-0-DCAC-C0-10-200-A |  | 81000 | 17 | 96200 | 5.4 | 6.75 | No
8789591 | Water Loop | GEOSTAR | 101/102H030**1*(0,3)***** |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
8789592 | Water Loop | GeoSmart Energy | GS030**1*(0,3)********H |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
8789593 | Water Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(0,3)****H |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
8789596 | Water Loop | GEOSTAR | 101/102H030**1*(1,4)***** |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
8789597 | Water Loop | GeoSmart Energy | GS030**1*(1,4)********H |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
8105913 | Water Loop | TRANE | DXHF0248 |  | 26200 | 17.7 | 31700 | 5.4 | 2.1833 | No
205993156 | Water Loop | GEOCOMFORT | GBT024 | GAD024 | 24100 | 17.5 | 29400 | 5 | 2.0083 | No
205993158 | Water Loop | HYDRON MODULE | HBT024 | HAD024 | 24100 | 17.5 | 29400 | 5 | 2.0083 | No
204452547 | Water Loop | GeoSmart Energy | VI036**1*(1,2)* |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
204457696 | Water Loop | YORK BY JOHNSON CONTROLS | YAFV036**1*(1,2)* |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
204474784 | Water Loop | GEOSTAR | 141/142B036**1*(1,2) |  | 32000 | 18 | 50000 | 5.3 | 2.6667 | No
9063208 | Water Loop | DAIKIN | WVFC1030*K***04 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
203363090 | Water Loop | WILLIAMS | EW010H1D*A |  | 30000 | 17 | 34800 | 5.5 | 2.5 | No
214855068 | Water Loop | WHALEN | CASH*036AD**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855069 | Water Loop | WHALEN | CASH*036AJ**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855070 | Water Loop | WHALEN | CASH*036AM**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855071 | Water Loop | WHALEN | CASV*036AB**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855072 | Water Loop | WHALEN | CASV*036AD**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855073 | Water Loop | WHALEN | CASV*036AJ**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855074 | Water Loop | WHALEN | CASV*036AM**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
214855067 | Water Loop | WHALEN | CASH*036AB**B**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
207200556 | Water Loop | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
207200557 | Water Loop | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
205993121 | Water Loop | HYDRON MODULE | HBS018*2 | HED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
205993122 | Water Loop | HYDRON MODULE | HBS018*2 | HAD018 | 21100 | 18.3 | 23300 | 6 | 1.7583 | No
205993123 | Water Loop | TETCO | TBS018*2 | TED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
205993124 | Water Loop | TETCO | TBS018*2 | TAD018 | 21100 | 18.3 | 23300 | 6 | 1.7583 | No
8105973 | Water Loop | TRANE | DXVF0481 |  | 49500 | 17.1 | 61100 | 5.5 | 4.125 | No
8105974 | Water Loop | TRANE | DXVF0482 |  | 49500 | 17.1 | 61100 | 5.5 | 4.125 | No
8105975 | Water Loop | TRANE | DXVF0483 |  | 49500 | 17.1 | 61100 | 5.5 | 4.125 | No
8105976 | Water Loop | TRANE | DXVF0484 |  | 49500 | 17.1 | 61100 | 5.5 | 4.125 | No
8105977 | Water Loop | TRANE | DXVF0488 |  | 49500 | 17.1 | 61100 | 5.5 | 4.125 | No
5343143 | Water Loop | DAIKIN | WVFC1030*E***04 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
8560787 | Water Loop | 5 SERIES | NSV/NSH030H1*(0,3) |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
202330279 | Water Loop | AAON, Inc. | WH-015-1-H-ACAC-C0-10-200-A |  | 14200 | 17 | 17900 | 6.3 | 1.1833 | No
202330280 | Water Loop | AAON, Inc. | WH-015-A-H-ACAC-C0-10-200-A |  | 14200 | 17 | 17900 | 6.3 | 1.1833 | No
5613676 | Water Loop | GEOSTAR | 141/142A048**1*1 |  | 41000 | 17.6 | 67000 | 5 | 3.4167 | No
202607208 | Water Loop | WHALEN | VP-A-1004-*DD |  | 30000 | 17 | 34800 | 5.5 | 2.5 | No
202330771 | Water Loop | WHALEN | CASH*036AJ**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
6580833 | Water Loop | YORK BY JOHNSON CONTROLS | YAFV048**1*1 |  | 41000 | 17.6 | 67000 | 5 | 3.4167 | No
203362374 | Water Loop | WHALEN | VP-H-1004-*DD |  | 30000 | 17 | 34800 | 5.5 | 2.5 | No
8789598 | Water Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****H |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
8105926 | Water Loop | TRANE | DXHF0481 |  | 51200 | 17.2 | 62400 | 5.4 | 4.2667 | No
8105927 | Water Loop | TRANE | DXHF0482 |  | 51200 | 17.2 | 62400 | 5.4 | 4.2667 | No
8105928 | Water Loop | TRANE | DXHF0483 |  | 51200 | 17.2 | 62400 | 5.4 | 4.2667 | No
8105929 | Water Loop | TRANE | DXHF0484 |  | 51200 | 17.2 | 62400 | 5.4 | 4.2667 | No
8105930 | Water Loop | TRANE | DXHF0488 |  | 51200 | 17.2 | 62400 | 5.4 | 4.2667 | No
8105965 | Water Loop | TRANE | DXVF0247 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
8105966 | Water Loop | TRANE | DXVF0248 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
214855043 | Water Loop | WHALEN | CASH*015AB**B**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
214855044 | Water Loop | WHALEN | CASH*015AD**B**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
214855045 | Water Loop | WHALEN | CASV*015AB**B**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
214855046 | Water Loop | WHALEN | CASV*015AD**B**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
205993113 | Water Loop | GEOCOMFORT | GBS018 | GED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
202443457 | Water Loop | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202443459 | Water Loop | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
202443460 | Water Loop | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
202443465 | Water Loop | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,2,4)*J |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202330772 | Water Loop | WHALEN | CASV*036AJ**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330773 | Water Loop | WHALEN | CASH*036AM**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330774 | Water Loop | WHALEN | CASV*036AM**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
5295957 | Water Loop | TRANE | EXHF0368 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
5295958 | Water Loop | TRANE | EXHF0364 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
214855047 | Water Loop | WHALEN | CASH*018AB**B**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
214855048 | Water Loop | WHALEN | CASH*018AD**B**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
214855049 | Water Loop | WHALEN | CASV*018AB**B**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
214855050 | Water Loop | WHALEN | CASV*018AD**B**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
202330746 | Water Loop | WHALEN | CASH*036AB**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330747 | Water Loop | WHALEN | CASV*036AB**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330748 | Water Loop | WHALEN | CASH*036AD**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
202330749 | Water Loop | WHALEN | CASV*036AD**A**(D,E) |  | 36000 | 17 | 43000 | 5 | 3 | No
206315253 | Water Loop | WHALEN | CASH*018AB**A**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
206315254 | Water Loop | WHALEN | CASV*018AB**A**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
206315255 | Water Loop | WHALEN | CASH*018AD**A**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
206315256 | Water Loop | WHALEN | CASV*018AD**A**(G,E) |  | 18000 | 17 | 21600 | 5.6 | 1.5 | No
205993164 | Water Loop | HYDRON MODULE | HBT024*2 | HAD024 | 24100 | 17.5 | 29400 | 5 | 2.0083 | No
205993166 | Water Loop | TETCO | TBT024*2 | TAD024 | 24100 | 17.5 | 29400 | 5 | 2.0083 | No
8560801 | Water Loop | 5 SERIES | NSV/NSH030H1*(1,4) |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
5440741 | Water Loop | 7 SERIES | NVV/NVH048A1*1 |  | 41000 | 17.6 | 67000 | 5 | 3.4167 | No
202923075 | Water Loop | GEOSTAR | 101/102J038**1*(1,2,4)***** |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
203113882 | Water Loop | GEOSTAR | 101/102J036**1*(1,2,4)***** |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
202350095 | Water Loop | 5 SERIES | NSV/NSH036J1*(1,2,4) |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
202350096 | Water Loop | 5 SERIES | NSV/NSH042J1*(1,2,4) |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
202350098 | Water Loop | 5 SERIES | NDV/NDH038J1*(1,2,4) |  | 36500 | 17 | 43300 | 5.5 | 3.0417 | No
202330359 | Water Loop | AAON, Inc. | WV-016-1-H-ACAC-C0-10-200-A |  | 14000 | 17.5 | 18400 | 5.1 | 1.1667 | No
202330360 | Water Loop | AAON, Inc. | WV-016-A-H-ACAC-C0-10-200-A |  | 14000 | 17.5 | 18400 | 5.1 | 1.1667 | No
206315249 | Water Loop | WHALEN | CASH*015AB**A**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
206315250 | Water Loop | WHALEN | CASV*015AB**A**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
206315251 | Water Loop | WHALEN | CASH*015AD**A**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
206315252 | Water Loop | WHALEN | CASV*015AD**A**(G,E) |  | 15000 | 17 | 18000 | 5.6 | 1.25 | No
206199262 | Water Loop | RHEEM | RPVV/H/D026D |  | 25000 | 17.4 | 31400 | 6 | 2.0833 | No
10581114 | Water Loop | YORK BY JOHNSON CONTROLS | YAPT038**1*(1,2)******H |  | 36500 | 17 | 41900 | 5.4 | 3.0417 | No
207200571 | Water Loop | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 32300 | 18.8 | 36500 | 5.7 | 2.6917 | No
205993160 | Water Loop | TETCO | TBT024 | TAD024 | 24100 | 17.5 | 29400 | 5 | 2.0083 | No
205993162 | Water Loop | GEOCOMFORT | GBT024*2 | GAD024 | 24100 | 17.5 | 29400 | 5 | 2.0083 | No
10268233 | Water Loop | GEOCOMFORT | GBT048 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
10268234 | Water Loop | HYDRON MODULE | HBT048 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
10268235 | Water Loop | TETCO | TBT048 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
10268236 | Water Loop | GEOCOMFORT | GBT048*2 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
10268237 | Water Loop | HYDRON MODULE | HBT048*2 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
10268238 | Water Loop | TETCO | TBT048*2 | MPD060 | 49200 | 17 | 54000 | 5.1 | 4.1 | No
207200624 | Water Loop | GeoSmart Energy | VI048**1*1 |  | 41000 | 17.6 | 67000 | 5 | 3.4167 | No
5612204 | Water Loop | GeoSmart Energy | VI048**1*1 |  | 41000 | 17.6 | 67000 | 5 | 3.4167 | No
203466716 | Water Loop | 5 SERIES | NDV/NDH049J1*(1,2,4) |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
203490410 | Water Loop | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 49100 | 17.2 | 59000 | 5.5 | 4.0917 | No
5343144 | Water Loop | DAIKIN | WVFC1030*F***04 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
5343145 | Water Loop | DAIKIN | WVFC1030*J***04 |  | 29900 | 17 | 33400 | 5.4 | 2.4917 | No
5295953 | Water Loop | TRANE | EXHF0361 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
5295954 | Water Loop | TRANE | EXHF0362 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
5295955 | Water Loop | TRANE | EXHF0367 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
5295956 | Water Loop | TRANE | EXHF0363 |  | 34600 | 17 | 42700 | 5.4 | 2.8833 | No
8105950 | Water Loop | TRANE | DXVF0241 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
8105955 | Water Loop | TRANE | DXVF0242 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
8105956 | Water Loop | TRANE | DXVF0243 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
8105960 | Water Loop | TRANE | DXVF0244 |  | 25700 | 17.7 | 31300 | 5.3 | 2.1417 | No
207200572 | Water Loop | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
207200617 | Water Loop | GeoSmart Energy | VI036**1*(1,2)* |  | 32300 | 17.7 | 51000 | 5.3 | 2.6917 | No
207200563 | Water Loop | GeoSmart Energy | GS030**1*(0,3)*H |  | 26800 | 17.9 | 32900 | 5.3 | 2.2333 | No
207200564 | Water Loop | GeoSmart Energy | GS030**1*(1,4)*H |  | 27000 | 18.9 | 32900 | 5.6 | 2.25 | No
203113887 | Water Loop | GEOSTAR | 101/102J042**1*(1,2,4)***** |  | 39000 | 18.6 | 45600 | 5.8 | 3.25 | No
207334459 | Water Loop | WaterFurnace | NDP038H1*(1,2) |  | 36500 | 17 | 41900 | 5.4 | 3.0417 | No
205993114 | Water Loop | GEOCOMFORT | GBS018 | GAD018 | 21100 | 18.3 | 23300 | 6 | 1.7583 | No
205993115 | Water Loop | HYDRON MODULE | HBS018 | HED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
205993116 | Water Loop | HYDRON MODULE | HBS018 | HAD018 | 21100 | 18.3 | 23300 | 6 | 1.7583 | No
205993117 | Water Loop | TETCO | TBS018 | TED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
205993118 | Water Loop | TETCO | TBS018 | TAD018 | 21100 | 18.3 | 23300 | 6 | 1.7583 | No
205993119 | Water Loop | GEOCOMFORT | GBS018*2 | GED018 | 20900 | 18 | 23400 | 6 | 1.7417 | No
205993120 | Water Loop | GEOCOMFORT | GBS018*2 | GAD018 | 21100 | 18.3 | 23300 | 6 | 1.7583 | No
10581119 | Water Loop | GEOSTAR | 107H038**1*(1,2) |  | 36500 | 17 | 41900 | 5.4 | 3.0417 | No

## Commercial Ground Water HP
AHRI Certified Reference Number | Equipment Type | Outdoor Unit Brand Name | Outdoor Unit Model Number | Indoor Unit Model Number | Full Load Cooling Capacity (Btuh) | EER | Full Load Heating Capacity (Btuh) | COP | Tonnage | Tax Credit (IRA) Eligibility
216057517 | Ground Water | GEOCOMFORT | GYT072* |  | 75400 | 21.7 | 70400 | 4.5 | 6.2833 | Yes
216065302 | Ground Water | GEOCOMFORT | GWS036* |  | 35600 | 22.9 | 38300 | 4.1 | 2.9667 | Yes
216065303 | Ground Water | GEOCOMFORT | GWS048* |  | 52500 | 22.9 | 58700 | 4.2 | 4.375 | Yes
216065306 | Ground Water | GEOCOMFORT | GWT048* |  | 52700 | 21.2 | 61100 | 4.2 | 4.3917 | Yes
216128491 | Ground Water | GEOSTAR | G5TV036BD1**2 |  | 41400 | 26.9 | 35700 | 5.1 | 3.45 | Yes
216128493 | Ground Water | GEOSTAR | G5TV048BD1**2 |  | 52500 | 24.5 | 47400 | 4.7 | 4.375 | Yes
216128495 | Ground Water | GEOSTAR | G5TV060BD1**2 |  | 67900 | 23.9 | 56000 | 4.6 | 5.6583 | Yes
216128497 | Ground Water | GEOSTAR | G5TV072BD1**2 |  | 77700 | 23 | 70700 | 4.5 | 6.475 | Yes
216411469 | Ground Water | ClimateMaster | SJ/PN024A | SAN024A | 24700 | 25.2 | 22500 | 4.8 | 2.0583 | Yes
216411470 | Ground Water | ClimateMaster | SJ/PN036A | SAN036A | 41800 | 25 | 33700 | 4.7 | 3.4833 | Yes
216411471 | Ground Water | ClimateMaster | SJ/PN048A | SAN048A | 51900 | 22.2 | 46000 | 4.4 | 4.325 | Yes
216411472 | Ground Water | ClimateMaster | SJ/PN060A | SAN060A | 65000 | 22.9 | 55100 | 4.3 | 5.4167 | Yes
216419856 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
216419857 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
216419860 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
216419863 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
216419865 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
216419867 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
216419868 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
216419871 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
216419879 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
216419880 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
216419882 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
216419883 | Ground Water | Whalen | WC(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
216419898 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
216419899 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
216419902 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
216419904 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
4219424 | Ground Water | NORDIC | R45HACW-P-1T-*-SDE** |  | 38500 | 21.3 | 35700 | 4.3 | 3.2083 | Yes
4219425 | Ground Water | NORDIC | R55HACW-P-1T-*-SDE** |  | 50200 | 22.5 | 47200 | 4.5 | 4.1833 | Yes
4219426 | Ground Water | NORDIC | R65HACW-P-1T-*-SDE** |  | 62600 | 21.5 | 58700 | 4.5 | 5.2167 | Yes
4219434 | Ground Water | NORDIC | TF55HACW-P-1T-*-SDE** |  | 51100 | 22.5 | 47100 | 4.4 | 4.2583 | Yes
4219443 | Ground Water | NORDIC | RS45HACW-P-1T-* | AH-45-P-1-***** | 38500 | 21.3 | 35700 | 4.3 | 3.2083 | Yes
4219444 | Ground Water | NORDIC | RS55HACW-P-1T-* | AH-55-P-1-***** | 50200 | 22.5 | 47200 | 4.5 | 4.1833 | Yes
4219445 | Ground Water | NORDIC | RS65HACW-P-1T-* | AH-65-P-1-***** | 62600 | 21.5 | 58700 | 4.5 | 5.2167 | Yes
4230749 | Ground Water | DAIKIN | WCCW4024*E*01* |  | 29600 | 22.8 | 23500 | 4.2 | 2.4667 | No
4230751 | Ground Water | DAIKIN | WCCW4024*F*01* |  | 0 | 22.8 | 23500 | 4.2 | 0 | No
4230753 | Ground Water | DAIKIN | WCCW4024*J*01* |  | 29600 | 22.8 | 23500 | 4.2 | 2.4667 | No
4230922 | Ground Water | DAIKIN | WCCW4024*K*01* |  | 29600 | 22.8 | 23500 | 4.2 | 2.4667 | No
214838955 | Ground Water | BOSCH | CL042-1HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214838956 | Ground Water | BOSCH | CL042-1VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214838957 | Ground Water | BOSCH | CL042-3HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214838958 | Ground Water | BOSCH | CL042-3VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214838959 | Ground Water | BOSCH | CL042-4HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214838960 | Ground Water | BOSCH | CL042-4VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
205312040 | Ground Water | GEOSTAR | ZBV/ZBH070**0*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
205312041 | Ground Water | GEOSTAR | ZBV/ZBH070**3*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
205312042 | Ground Water | GEOSTAR | ZBV/ZBH070**4*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
9100357 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**0*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100358 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**0*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100359 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**2*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100361 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**3*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100362 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**3*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100364 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**4*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100365 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**4*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
9100367 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**0*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100368 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**0*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100370 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**3*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100371 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**3*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100373 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**4*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100374 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**4*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
9100377 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**0*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100378 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**0*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100380 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**3*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100381 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**3*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100383 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**4*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100384 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**4*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
9100390 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**0*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100391 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**0*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100393 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**3*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100394 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**3*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100396 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**4*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100397 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**4*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
9100400 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**0*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9100401 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**0*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9100403 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**3*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9100404 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**3*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9100417 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**4*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
9100431 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**4*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
217897421 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
217897422 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
217897425 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
217897426 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
217897427 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
217897428 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
217897429 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
217897430 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
217897433 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
217897434 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
217897447 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
217897448 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
217897449 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
214776161 | Ground Water | TRANE | GETK009 |  | 9500 | 23.6 | 8600 | 4.13 | 0.79167 | No
214776167 | Ground Water | TRANE | GETK0091-5 |  | 9700 | 27 | 8400 | 4.44 | 0.80833 | No
202146983 | Ground Water | HYDRON MODULE | HZS030*2***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202146984 | Ground Water | TETCO | TZS030 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | Yes
202146985 | Ground Water | TETCO | TZS030*2 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146986 | Ground Water | TETCO | TZS030*3 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146987 | Ground Water | TETCO | TZS030*4 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146988 | Ground Water | TETCO | TZS030*A |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146989 | Ground Water | TETCO | TZS030*****1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | Yes
202146990 | Ground Water | TETCO | TZS030*2***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202146991 | Ground Water | GEOCOMFORT | GZS036 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | Yes
202146992 | Ground Water | GEOCOMFORT | GZS036*2 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202146993 | Ground Water | GEOCOMFORT | GZS036*3 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202146994 | Ground Water | GEOCOMFORT | GZS036*4 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202146995 | Ground Water | GEOCOMFORT | GZS036*A |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202146996 | Ground Water | GEOCOMFORT | GZS036*****1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | Yes
202146997 | Ground Water | GEOCOMFORT | GZS036*2***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202146998 | Ground Water | GEOCOMFORT | GZS036*3***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202146999 | Ground Water | GEOCOMFORT | GZS036*A***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147000 | Ground Water | HYDRON MODULE | HZS036 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | Yes
202147001 | Ground Water | HYDRON MODULE | HZS036*2 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147002 | Ground Water | HYDRON MODULE | HZS036*3 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147003 | Ground Water | HYDRON MODULE | HZS036*4 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147004 | Ground Water | HYDRON MODULE | HZS036*A |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147005 | Ground Water | HYDRON MODULE | HZS036*****1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | Yes
202147006 | Ground Water | HYDRON MODULE | HZS036*2***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147007 | Ground Water | HYDRON MODULE | HZS036*3***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147008 | Ground Water | HYDRON MODULE | HZS036*A***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147009 | Ground Water | TETCO | TZS036 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | Yes
214823486 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048BD1**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | Yes
214823487 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060BD1**2 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | Yes
214823488 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072BD1**2 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | Yes
214837733 | Ground Water | BOSCH | EC072-1VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837734 | Ground Water | BOSCH | EC072-3VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837735 | Ground Water | BOSCH | EC072-4VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837736 | Ground Water | BOSCH | EC096-1VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214837737 | Ground Water | BOSCH | EC096-3VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214837738 | Ground Water | BOSCH | EC096-4VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214837742 | Ground Water | CARRIER | 50H/VQP072***3C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837743 | Ground Water | CARRIER | 50H/VQP072***5C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837744 | Ground Water | CARRIER | 50H/VQP072***6C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214837745 | Ground Water | CARRIER | 50H/VQP096***3C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214837746 | Ground Water | CARRIER | 50H/VQP096***5C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214837747 | Ground Water | CARRIER | 50H/VQP096***6C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
216621309 | Ground Water | GEOSTAR | G5A(V/H)009*R0**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216621310 | Ground Water | GEOSTAR | G5A(V/H)012*R0**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
216621311 | Ground Water | GEOSTAR | G5A(V/H)015*R0**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216621312 | Ground Water | GEOSTAR | G5A(V/H)018*R0**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216621313 | Ground Water | GEOSTAR | G5A(V/H)024*S0**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216621314 | Ground Water | GEOSTAR | G5A(V/H)030*S0**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216621315 | Ground Water | GEOSTAR | G5A(V/H)036*S0**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216621316 | Ground Water | GEOSTAR | G5A(V/H)042*S0**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216621317 | Ground Water | GEOSTAR | G5A(V/H)048*S0**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216621318 | Ground Water | GEOSTAR | G5A(V/H)060*S0**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216621319 | Ground Water | GEOSTAR | G5A(V/H)072*S0**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216621323 | Ground Water | GEOSTAR | G5A(V/H)018*D0**1 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216621324 | Ground Water | GEOSTAR | G5A(V/H)018*D0**4 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216621325 | Ground Water | GEOSTAR | G5A(V/H)024*D0**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621326 | Ground Water | GEOSTAR | G5A(V/H)024*D2**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621327 | Ground Water | GEOSTAR | G5A(V/H)024*D3**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621328 | Ground Water | GEOSTAR | G5A(V/H)024*D4**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621329 | Ground Water | GEOSTAR | G5A(V/H)024*D0**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621330 | Ground Water | GEOSTAR | G5A(V/H)024*D2**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621331 | Ground Water | GEOSTAR | G5A(V/H)024*D3**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621332 | Ground Water | GEOSTAR | G5A(V/H)024*D4**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216621333 | Ground Water | GEOSTAR | G5A(V/H)030*D0**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216621334 | Ground Water | GEOSTAR | G5A(V/H)030*D3**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216621335 | Ground Water | GEOSTAR | G5A(V/H)030*D0**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216621336 | Ground Water | GEOSTAR | G5A(V/H)030*D3**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216621337 | Ground Water | GEOSTAR | G5A(V/H)036*D0**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621338 | Ground Water | GEOSTAR | G5A(V/H)036*D3**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
9009366 | Ground Water | FHP | ES025-2CF/HZ/VT*-*****A |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
9009369 | Ground Water | FHP | ES035-1CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9009382 | Ground Water | FHP | ES035-3CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9009391 | Ground Water | FHP | ES035-4CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9011292 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**0*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
9032337 | Ground Water | HYDROTECH | HRCC09*-2 |  | 11500 | 23.9 | 8800 | 4.1 | 0.95833 | No
9032648 | Ground Water | HYDROTECH | HRCX18*-6 |  | 20000 | 22.5 | 16000 | 4.1 | 1.6667 | Yes
9033424 | Ground Water | HYDROTECH | HRCX09*-6 |  | 11500 | 26.5 | 8800 | 4.5 | 0.95833 | Yes
9033758 | Ground Water | HYDROTECH | HRCX24*-6 |  | 26000 | 26.5 | 22000 | 4.4 | 2.1667 | Yes
9033759 | Ground Water | HYDROTECH | HRCX12*-6 |  | 13000 | 25 | 10500 | 4.1 | 1.0833 | Yes
208450079 | Ground Water | AE Air | HRCX18*-6 |  | 20000 | 22.5 | 16000 | 4.1 | 1.6667 | Yes
208450080 | Ground Water | AE Air | HRCX09*-6 |  | 11500 | 26.5 | 8800 | 4.5 | 0.95833 | Yes
208450081 | Ground Water | AE Air | HRCX24*-6 |  | 26000 | 26.5 | 22000 | 4.4 | 2.1667 | Yes
208450082 | Ground Water | AE Air | HRCX12*-6 |  | 13000 | 25 | 10500 | 4.1 | 1.0833 | Yes
208450083 | Ground Water | AE Air | HRCX30*-6 |  | 30000 | 23.5 | 25000 | 4.1 | 2.5 | Yes
208450084 | Ground Water | AE Air | HRCX36*-6 |  | 35500 | 21.6 | 31500 | 4.1 | 2.9583 | Yes
217212057 | Ground Water | FHP | CP024-4HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212059 | Ground Water | FHP | CP024-4HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
217212060 | Ground Water | FHP | CP024-4VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212061 | Ground Water | FHP | CP024-4VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
217212062 | Ground Water | FHP | CP036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
217212064 | Ground Water | FHP | CP036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
217212065 | Ground Water | FHP | CP036-2VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
217212066 | Ground Water | FHP | CP036-2VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
217212067 | Ground Water | FHP | CP036-3VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
217212068 | Ground Water | FHP | CP036-3VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
217212070 | Ground Water | FHP | CP036-4VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
217212071 | Ground Water | FHP | CP036-4VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
217212072 | Ground Water | FHP | CP048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
217212073 | Ground Water | FHP | CP048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
217212074 | Ground Water | FHP | CP048-3VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
217212076 | Ground Water | FHP | CP048-3VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
217212077 | Ground Water | FHP | CP048-4VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
202667081 | Ground Water | BOSCH-GEO | BP042-1VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
202679205 | Ground Water | BOSCH-GEO | SM036-1CSC-*****B | SM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | Yes
202679208 | Ground Water | BOSCH | SM036-1CSC-*****B | SM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | Yes
202729320 | Ground Water | HEIL | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
202729321 | Ground Water | ARCOAIRE | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202729322 | Ground Water | KEEPRITE | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202729323 | Ground Water | TEMPSTAR | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202729324 | Ground Water | COMFORTMAKER | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202729325 | Ground Water | DAY & NIGHT | HB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202729332 | Ground Water | HEIL | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
202729333 | Ground Water | ARCOAIRE | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202729334 | Ground Water | KEEPRITE | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202729335 | Ground Water | TEMPSTAR | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202729336 | Ground Water | COMFORTMAKER | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202729337 | Ground Water | DAY & NIGHT | HB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202732300 | Ground Water | BOSCH | BP042-1VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732301 | Ground Water | CARRIER | GB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
202732302 | Ground Water | BRYANT | GB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732303 | Ground Water | ARCOAIRE | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
202732304 | Ground Water | HEIL | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732305 | Ground Water | KEEPRITE | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732306 | Ground Water | TEMPSTAR | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732307 | Ground Water | COMFORTMAKER | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732308 | Ground Water | DAY & NIGHT | HB042V******1**1 |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | Yes
202732913 | Ground Water | BOSCH-GEO | SM036-1CSN-*****B | SM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | Yes
202732914 | Ground Water | BOSCH-GEO | BP018-1HZ*******C |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
202732915 | Ground Water | BOSCH | SM036-1CSN-*****B | SM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | Yes
202732916 | Ground Water | BOSCH | BP018-1HZ*******C |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732917 | Ground Water | CARRIER | GB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
202732918 | Ground Water | BRYANT | GB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732919 | Ground Water | HEIL | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
202732920 | Ground Water | ARCOAIRE | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732921 | Ground Water | KEEPRITE | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732922 | Ground Water | TEMPSTAR | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732923 | Ground Water | COMFORTMAKER | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732924 | Ground Water | DAY & NIGHT | HB018H******1**2 |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | Yes
202732934 | Ground Water | TRANE | GWSC036H3 |  | 46200 | 23.29 | 38800 | 4.12 | 3.85 | No
202732935 | Ground Water | TRANE | GWSC036H4 |  | 46200 | 23.29 | 38800 | 4.12 | 3.85 | No
202732936 | Ground Water | TRANE | GWSC036HW |  | 46200 | 23.29 | 38800 | 4.12 | 3.85 | No
202732937 | Ground Water | TRANE | GWSC048H3 |  | 59700 | 25.72 | 50000 | 4.56 | 4.975 | No
202732938 | Ground Water | TRANE | GWSC048H4 |  | 59700 | 25.72 | 50000 | 4.56 | 4.975 | No
202732939 | Ground Water | TRANE | GWSC048HW |  | 59700 | 25.72 | 50000 | 4.56 | 4.975 | No
202732940 | Ground Water | TRANE | GWSC060H3 |  | 68300 | 22.57 | 61900 | 4.33 | 5.6917 | No
202732941 | Ground Water | TRANE | GWSC060H4 |  | 68300 | 22.57 | 61900 | 4.33 | 5.6917 | No
202732942 | Ground Water | TRANE | GWSC060HW |  | 68300 | 22.57 | 61900 | 4.33 | 5.6917 | No
207337469 | Ground Water | GEOSTAR | 103H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337470 | Ground Water | GEOSTAR | 103H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337471 | Ground Water | GEOSTAR | 163H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337472 | Ground Water | GEOSTAR | 163H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337473 | Ground Water | GEOSTAR | 104H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337474 | Ground Water | GEOSTAR | 104H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337475 | Ground Water | GEOSTAR | 164H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337476 | Ground Water | GEOSTAR | 164H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207337477 | Ground Water | GEOSTAR | 103J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337478 | Ground Water | GEOSTAR | 103J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337479 | Ground Water | GEOSTAR | 163J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337480 | Ground Water | GEOSTAR | 163J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337481 | Ground Water | GEOSTAR | 104J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337482 | Ground Water | GEOSTAR | 104J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337483 | Ground Water | GEOSTAR | 164J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337484 | Ground Water | GEOSTAR | 164J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207337485 | Ground Water | GEOSTAR | 103J049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337486 | Ground Water | GEOSTAR | 103J049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337487 | Ground Water | GEOSTAR | 163J049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337488 | Ground Water | GEOSTAR | 163J049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337489 | Ground Water | GEOSTAR | 104H049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337490 | Ground Water | GEOSTAR | 104H049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337491 | Ground Water | GEOSTAR | 164H049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337492 | Ground Water | GEOSTAR | 164H049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207337493 | Ground Water | GEOSTAR | 103J064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337494 | Ground Water | GEOSTAR | 103J064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337495 | Ground Water | GEOSTAR | 163J064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337496 | Ground Water | GEOSTAR | 163J064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337497 | Ground Water | GEOSTAR | 104H064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337498 | Ground Water | GEOSTAR | 104H064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337499 | Ground Water | GEOSTAR | 164H064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337500 | Ground Water | GEOSTAR | 164H064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207337501 | Ground Water | GEOSTAR | 103H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337502 | Ground Water | GEOSTAR | 103H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337503 | Ground Water | GEOSTAR | 163H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337504 | Ground Water | GEOSTAR | 163H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337505 | Ground Water | GEOSTAR | 104H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337506 | Ground Water | GEOSTAR | 104H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337507 | Ground Water | GEOSTAR | 164H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337508 | Ground Water | GEOSTAR | 164H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207337509 | Ground Water | GEOSTAR | 103H022**1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
207337510 | Ground Water | GEOSTAR | 103H022**1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
207337511 | Ground Water | GEOSTAR | 103H030**1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
207337512 | Ground Water | GEOSTAR | 103H030**1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
207337513 | Ground Water | GEOSTAR | 103J036**1 | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | No
207337514 | Ground Water | GEOSTAR | 103J036**1 | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | No
207337515 | Ground Water | GEOSTAR | 103J042**1 | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | No
207337516 | Ground Water | GEOSTAR | 103J042**1 | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | No
207337517 | Ground Water | GEOSTAR | 103H048**1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
6501947 | Ground Water | GEOSTAR | GBV/GBH038**3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501948 | Ground Water | GEOSTAR | GBV/GBH038**4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501949 | Ground Water | GEOSTAR | GBV/GBH038**4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501950 | Ground Water | GEOSTAR | GBV/GBH042**0*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
215224027 | Ground Water | BOSCH | CF007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224028 | Ground Water | BOSCH | CF007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224029 | Ground Water | BOSCH | CF009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224030 | Ground Water | BOSCH | CF009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224031 | Ground Water | BOSCH | CF012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224032 | Ground Water | BOSCH | CF012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224033 | Ground Water | BOSCH | CF015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224034 | Ground Water | BOSCH | CF015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
215224035 | Ground Water | BOSCH | CF018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224036 | Ground Water | BOSCH | CF018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
215224037 | Ground Water | BOSCH | CF007-2VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224038 | Ground Water | BOSCH | CF007-2VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224039 | Ground Water | BOSCH | CF009-2VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224040 | Ground Water | BOSCH | CF009-2VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224041 | Ground Water | BOSCH | CF012-2VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224042 | Ground Water | BOSCH | CF012-2VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224043 | Ground Water | BOSCH | CF015-2VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224044 | Ground Water | BOSCH | CF015-2VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
215224045 | Ground Water | BOSCH | CF018-2VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224046 | Ground Water | BOSCH | CF018-2VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
216743648 | Ground Water | BOSCH | CP048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216743649 | Ground Water | BOSCH | CP048-3VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216743650 | Ground Water | BOSCH | CP048-4VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216743651 | Ground Water | BOSCH-GEO | RP048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216743652 | Ground Water | BOSCH | CP048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216743653 | Ground Water | BOSCH | CP048-3VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216743654 | Ground Water | BOSCH | CP048-4VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216743655 | Ground Water | BOSCH-GEO | RP060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216743656 | Ground Water | BOSCH | CP060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216743657 | Ground Water | BOSCH | CP060-3VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216743658 | Ground Water | BOSCH | CP060-4VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216743659 | Ground Water | BOSCH-GEO | RP060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216743660 | Ground Water | BOSCH | CP060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216743661 | Ground Water | BOSCH | CP060-3VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216743662 | Ground Water | BOSCH | CP060-4VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216743663 | Ground Water | BOSCH-GEO | RP070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
216743664 | Ground Water | BOSCH | CP070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743665 | Ground Water | BOSCH | CP070-3VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743666 | Ground Water | BOSCH | CP070-4VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743667 | Ground Water | BOSCH-GEO | RP070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
216743668 | Ground Water | BOSCH | CP070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216743669 | Ground Water | BOSCH | CP070-3VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216743670 | Ground Water | BOSCH | CP070-4VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216743671 | Ground Water | BOSCH-GEO | RP070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
216743672 | Ground Water | BOSCH | CP070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743673 | Ground Water | BOSCH | CP070-3HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743674 | Ground Water | BOSCH | CP070-4HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216743675 | Ground Water | BOSCH-GEO | RP070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
216743676 | Ground Water | BOSCH | CP070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216743677 | Ground Water | BOSCH | CP070-3HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216743678 | Ground Water | BOSCH | CP070-4HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216759673 | Ground Water | WaterFurnace | W7SZ030BV1**F | W7BM030BN1**2 | 35800 | 27.8 | 40700 | 4.5 | 2.9833 | Yes
216759674 | Ground Water | WaterFurnace | W7SZ042BV1**F | W7BM042BN1**2 | 44400 | 28.8 | 51300 | 4.4 | 3.7 | Yes
216759816 | Ground Water | WaterFurnace | W5SS024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
205312006 | Ground Water | GEOSTAR | ZBV/ZBH042**0*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
214067547 | Ground Water | GeoSmart Energy | GBV/GBH024**3*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
214067548 | Ground Water | GeoSmart Energy | GBV/GBH024**3*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214067549 | Ground Water | GeoSmart Energy | GBV/GBH024**3*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214067550 | Ground Water | GeoSmart Energy | GBV/GBH024**4*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
214067551 | Ground Water | GeoSmart Energy | GBV/GBH024**4*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214067552 | Ground Water | GeoSmart Energy | GBV/GBH024**4*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214067553 | Ground Water | GeoSmart Energy | GBV/GBH026**3*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214067554 | Ground Water | GeoSmart Energy | GBV/GBH026**3*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214067555 | Ground Water | GeoSmart Energy | GBV/GBH026**4*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214067556 | Ground Water | GeoSmart Energy | GBV/GBH026**4*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214067557 | Ground Water | GeoSmart Energy | GBV/GBH030**3*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
214067558 | Ground Water | GeoSmart Energy | GBV/GBH030**3*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214067559 | Ground Water | GeoSmart Energy | GBV/GBH030**3*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214067560 | Ground Water | GeoSmart Energy | GBV/GBH030**4*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
214067561 | Ground Water | GeoSmart Energy | GBV/GBH030**4*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214067562 | Ground Water | GeoSmart Energy | GBV/GBH030**4*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214067563 | Ground Water | GeoSmart Energy | GBV/GBH036**3*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
214067564 | Ground Water | GeoSmart Energy | GBV/GBH036**3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214067565 | Ground Water | GeoSmart Energy | GBV/GBH036**3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214067566 | Ground Water | GeoSmart Energy | GBV/GBH036**4*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
214067567 | Ground Water | GeoSmart Energy | GBV/GBH036**4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214067568 | Ground Water | GeoSmart Energy | GBV/GBH036**4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214067569 | Ground Water | GeoSmart Energy | GBV/GBH038**3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214067570 | Ground Water | GeoSmart Energy | GBV/GBH038**3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214067571 | Ground Water | GeoSmart Energy | GBV/GBH038**4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214067572 | Ground Water | GeoSmart Energy | GBV/GBH038**4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214067573 | Ground Water | GeoSmart Energy | GBV/GBH042**3*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
214067574 | Ground Water | GeoSmart Energy | GBV/GBH042**3*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214067575 | Ground Water | GeoSmart Energy | GBV/GBH042**3*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214067576 | Ground Water | GeoSmart Energy | GBV/GBH042**4*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
214067577 | Ground Water | GeoSmart Energy | GBV/GBH042**4*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214067578 | Ground Water | GeoSmart Energy | GBV/GBH042**4*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214067579 | Ground Water | GeoSmart Energy | GBV/GBH042**5*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
214067580 | Ground Water | GeoSmart Energy | GBV/GBH048**4*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
214067581 | Ground Water | GeoSmart Energy | GBV/GBH048**4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214067582 | Ground Water | GeoSmart Energy | GBV/GBH048**4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214067583 | Ground Water | GeoSmart Energy | GBV/GBH048**5*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
214067584 | Ground Water | GeoSmart Energy | GBV/GBH049**3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214067585 | Ground Water | GeoSmart Energy | GBV/GBH049**3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214067586 | Ground Water | GeoSmart Energy | GBV/GBH049**4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214067587 | Ground Water | GeoSmart Energy | GBV/GBH049**4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214067588 | Ground Water | GeoSmart Energy | GBV/GBH060**3*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
214067589 | Ground Water | GeoSmart Energy | GBV/GBH060**3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214067590 | Ground Water | GeoSmart Energy | GBV/GBH060**3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214067591 | Ground Water | GeoSmart Energy | GBV/GBH060**4*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
214067592 | Ground Water | GeoSmart Energy | GBV/GBH060**4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214067593 | Ground Water | GeoSmart Energy | GBV/GBH060**4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214067594 | Ground Water | GeoSmart Energy | GBV/GBH060**5*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
214067595 | Ground Water | GeoSmart Energy | GBV/GBH064**3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214067596 | Ground Water | GeoSmart Energy | GBV/GBH064**3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214067597 | Ground Water | GeoSmart Energy | GBV/GBH064**4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214067598 | Ground Water | GeoSmart Energy | GBV/GBH064**4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214067600 | Ground Water | GeoSmart Energy | GBV/GBH070**3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214067601 | Ground Water | GeoSmart Energy | GBV/GBH070**3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7519567 | Ground Water | GEOCOMFORT | GVS030*3 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519568 | Ground Water | HYDRON MODULE | HVS030*3 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519569 | Ground Water | TETCO | TVS030*3 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519570 | Ground Water | GEOCOMFORT | GVS030*4 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519571 | Ground Water | HYDRON MODULE | HVS030*4 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519572 | Ground Water | TETCO | TVS030*4 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519573 | Ground Water | GEOCOMFORT | GVS036*A |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519574 | Ground Water | HYDRON MODULE | HVS036*A |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519575 | Ground Water | TETCO | TVS036*A |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519576 | Ground Water | GEOCOMFORT | GVS036*2 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519577 | Ground Water | HYDRON MODULE | HVS036*2 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519578 | Ground Water | TETCO | TVS036*2 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519579 | Ground Water | GEOCOMFORT | GVS036*3 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519580 | Ground Water | HYDRON MODULE | HVS036*3 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519581 | Ground Water | TETCO | TVS036*3 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519582 | Ground Water | GEOCOMFORT | GVS036*4 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519583 | Ground Water | HYDRON MODULE | HVS036*4 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519584 | Ground Water | TETCO | TVS036*4 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | No
7519727 | Ground Water | GEOCOMFORT | GVS024*****1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | Yes
7519748 | Ground Water | HYDRON MODULE | HVS024*****1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | Yes
7519756 | Ground Water | TETCO | TVS024*****1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | Yes
7519769 | Ground Water | GEOCOMFORT | GVS024*A***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519770 | Ground Water | HYDRON MODULE | HVS024*A***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519771 | Ground Water | TETCO | TVS024*A***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519772 | Ground Water | GEOCOMFORT | GVS024*2***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519773 | Ground Water | HYDRON MODULE | HVS024*2***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519774 | Ground Water | TETCO | TVS024*2***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519775 | Ground Water | GEOCOMFORT | GVS024*3***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519776 | Ground Water | HYDRON MODULE | HVS024*3***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7519777 | Ground Water | TETCO | TVS024*3***1 |  | 29400 | 29.5 | 24000 | 5.1 | 2.45 | No
7520238 | Ground Water | GEOCOMFORT | GVS030*****1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | Yes
7520239 | Ground Water | HYDRON MODULE | HVS030*****1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | Yes
7520240 | Ground Water | TETCO | TVS030*****1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | Yes
7520241 | Ground Water | GEOCOMFORT | GVS030*2***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520242 | Ground Water | HYDRON MODULE | HVS030*2***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520243 | Ground Water | TETCO | TVS030*2***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520244 | Ground Water | TETCO | TVS030*3***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520245 | Ground Water | HYDRON MODULE | HVS030*3***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520246 | Ground Water | GEOCOMFORT | GVS030*A***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520247 | Ground Water | HYDRON MODULE | HVS030*A***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520248 | Ground Water | TETCO | TVS030*A***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520249 | Ground Water | GEOCOMFORT | GVS030*3***1 |  | 34000 | 27.5 | 29200 | 5.1 | 2.8333 | No
7520250 | Ground Water | GEOCOMFORT | GVS036*****1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | Yes
7520251 | Ground Water | HYDRON MODULE | HVS036*****1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | Yes
7520252 | Ground Water | TETCO | TVS036*****1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | Yes
7520253 | Ground Water | GEOCOMFORT | GVS036*2***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520254 | Ground Water | HYDRON MODULE | HVS036*2***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520255 | Ground Water | TETCO | TVS036*2***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520256 | Ground Water | GEOCOMFORT | GVS036*3***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520257 | Ground Water | HYDRON MODULE | HVS036*3***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520258 | Ground Water | TETCO | TVS036*3***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520259 | Ground Water | GEOCOMFORT | GVS036*A***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520260 | Ground Water | HYDRON MODULE | HVS036*A***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7520261 | Ground Water | TETCO | TVS036*A***1 |  | 41600 | 25.5 | 36900 | 4.8 | 3.4667 | No
7523956 | Ground Water | GEOCOMFORT | GVS018*****1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | Yes
7523957 | Ground Water | HYDRON MODULE | HVS018*****1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | Yes
203254607 | Ground Water | BRYANT | GB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254608 | Ground Water | ARCOAIRE | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203254609 | Ground Water | HEIL | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254610 | Ground Water | KEEPRITE | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254611 | Ground Water | TEMPSTAR | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254612 | Ground Water | COMFORTMAKER | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254614 | Ground Water | DAY & NIGHT | HB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203254620 | Ground Water | BRYANT | GC024V/C**N***1*X1 |  | 29000 | 23.7 | 23500 | 4.6 | 2.4167 | Yes
203254624 | Ground Water | BRYANT | GC024H**C***1*X1 |  | 29000 | 25.75 | 23500 | 5 | 2.4167 | Yes
203254626 | Ground Water | BRYANT | GC024H**N***1*X1 |  | 29000 | 24.1 | 23500 | 5 | 2.4167 | Yes
203254744 | Ground Water | CARRIER | GC024V/C**N***1**1 |  | 29000 | 23.7 | 23500 | 4.6 | 2.4167 | Yes
203254748 | Ground Water | CARRIER | GC024H**C***1**1 |  | 29000 | 25.75 | 23500 | 5 | 2.4167 | Yes
203254752 | Ground Water | CARRIER | GC024H**N***1**1 |  | 29000 | 24.1 | 23500 | 5 | 2.4167 | Yes
203260718 | Ground Water | BOSCH-GEO | SM024-1VT/CFC******A |  | 29000 | 24.7 | 23500 | 4.3 | 2.4167 | Yes
203260866 | Ground Water | CARRIER | GC024V/C**C***1**1 + UI |  | 29000 | 24.7 | 23500 | 4.3 | 2.4167 | Yes
203260867 | Ground Water | BRYANT | GC024V/C**C***1*X1 + UI |  | 29000 | 24.7 | 23500 | 4.3 | 2.4167 | Yes
215268677 | Ground Water | WaterFurnace | V5A(V/H)015*R0**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
215268678 | Ground Water | WaterFurnace | V5A(V/H)015*R2**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
215268679 | Ground Water | WaterFurnace | V5A(V/H)018*R2**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
215268680 | Ground Water | WaterFurnace | V5A(V/H)018*R0**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
215268681 | Ground Water | WaterFurnace | V5A(V/H)018*R2**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
215268682 | Ground Water | WaterFurnace | V5A(V/H)024*S2**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268683 | Ground Water | WaterFurnace | V5A(V/H)024*S3**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268684 | Ground Water | WaterFurnace | V5A(V/H)024*S4**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268685 | Ground Water | WaterFurnace | V5A(V/H)024*S0**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268686 | Ground Water | WaterFurnace | V5A(V/H)024*S2**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268687 | Ground Water | WaterFurnace | V5A(V/H)024*S3**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268688 | Ground Water | WaterFurnace | V5A(V/H)024*S4**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268689 | Ground Water | WaterFurnace | V5A(V/H)030*S3**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268690 | Ground Water | WaterFurnace | V5A(V/H)030*S0**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268691 | Ground Water | WaterFurnace | V5A(V/H)030*S3**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268692 | Ground Water | WaterFurnace | V5A(V/H)036*S3**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268693 | Ground Water | WaterFurnace | V5A(V/H)036*S0**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268694 | Ground Water | WaterFurnace | V5A(V/H)036*S3**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268695 | Ground Water | WaterFurnace | V5A(V/H)036*S0**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268696 | Ground Water | WaterFurnace | V5A(V/H)036*S3**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268697 | Ground Water | WaterFurnace | V5A(V/H)042*S3**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268698 | Ground Water | WaterFurnace | V5A(V/H)042*S0**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268699 | Ground Water | WaterFurnace | V5A(V/H)042*S3**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268700 | Ground Water | WaterFurnace | V5A(V/H)042*S0**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268701 | Ground Water | WaterFurnace | V5A(V/H)042*S3**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268702 | Ground Water | WaterFurnace | V5A(V/H)048*S3**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268703 | Ground Water | WaterFurnace | V5A(V/H)048*S0**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268704 | Ground Water | WaterFurnace | V5A(V/H)048*S3**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268705 | Ground Water | WaterFurnace | V5A(V/H)048*S0**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268706 | Ground Water | WaterFurnace | V5A(V/H)048*S3**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268707 | Ground Water | WaterFurnace | V5A(V/H)060*S3**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268708 | Ground Water | WaterFurnace | V5A(V/H)060*S0**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268709 | Ground Water | WaterFurnace | V5A(V/H)060*S3**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268710 | Ground Water | WaterFurnace | V5A(V/H)072*S3**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268711 | Ground Water | WaterFurnace | V5A(V/H)072*S0**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268712 | Ground Water | WaterFurnace | V5A(V/H)072*S3**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268713 | Ground Water | WaterFurnace | V5A(V/H)030*S2**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268714 | Ground Water | WaterFurnace | V5A(V/H)030*S4**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268715 | Ground Water | WaterFurnace | V5A(V/H)030*S2**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268716 | Ground Water | WaterFurnace | V5A(V/H)030*S4**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
215268717 | Ground Water | WaterFurnace | V5A(V/H)036*S4**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268718 | Ground Water | WaterFurnace | V5A(V/H)036*S2**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268719 | Ground Water | WaterFurnace | V5A(V/H)036*S4**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268720 | Ground Water | WaterFurnace | V5A(V/H)036*S2**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268721 | Ground Water | WaterFurnace | V5A(V/H)036*S4**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268722 | Ground Water | WaterFurnace | V5A(V/H)042*S4**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268723 | Ground Water | WaterFurnace | V5A(V/H)042*S2**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268724 | Ground Water | WaterFurnace | V5A(V/H)042*S4**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268725 | Ground Water | WaterFurnace | V5A(V/H)042*S4**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268726 | Ground Water | WaterFurnace | V5A(V/H)048*S4**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268727 | Ground Water | WaterFurnace | V5A(V/H)048*S2**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268728 | Ground Water | WaterFurnace | V5A(V/H)048*S4**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268729 | Ground Water | WaterFurnace | V5A(V/H)048*S4**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268730 | Ground Water | WaterFurnace | V5A(V/H)060*S4**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268731 | Ground Water | WaterFurnace | V5A(V/H)060*S4**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268732 | Ground Water | WaterFurnace | V5A(V/H)072*S4**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
217351675 | Ground Water | BOSCH | RP048-1CSC-*****A | BIVA-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | Yes
217351676 | Ground Water | BOSCH | RP048-1CSN-*****A | BIVA-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | Yes
217351677 | Ground Water | BOSCH | RP060-1CSC-*****A | BIVA-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | Yes
217351678 | Ground Water | BOSCH | RP060-1CSN-*****A | BIVA-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | Yes
217351679 | Ground Water | BOSCH | RP024-1CSC-*****A | BMAC2430BBTA | 27400 | 23.2 | 23800 | 5 | 2.2833 | Yes
217351680 | Ground Water | BOSCH | RP024-1CSN-*****A | BMAC2430BBTA | 27600 | 24.3 | 23800 | 5.1 | 2.3 | Yes
217351681 | Ground Water | BOSCH | RP036-1CSC-*****A | BMAC3036BBTA | 39600 | 21.5 | 37800 | 4.8 | 3.3 | Yes
217351682 | Ground Water | BOSCH | RP036-1CSN-*****A | BMAC3036BBTA | 40200 | 22.2 | 38800 | 5 | 3.35 | Yes
217351683 | Ground Water | BOSCH | RP048-1CSC-*****A | BMAC4248CBTA | 52000 | 21.6 | 45400 | 4.5 | 4.3333 | Yes
217351684 | Ground Water | BOSCH | RP048-1CSN-*****A | BMAC4248CBTA | 53400 | 22.5 | 46600 | 4.7 | 4.45 | Yes
217351686 | Ground Water | BOSCH | RP060-1CSN-*****A | BMAC4860CBTA | 63200 | 21.1 | 59400 | 4.5 | 5.2667 | Yes
217351687 | Ground Water | BOSCH | TW025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351689 | Ground Water | BOSCH | TW049-1***-*****C |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351692 | Ground Water | FHP | CP024-1CSC-*****A | BIVA-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | No
217351693 | Ground Water | FHP | CP024-1CSN-*****A | BIVA-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | No
217351694 | Ground Water | FHP | CP036-1CSC-*****A | BIVA-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | No
217351695 | Ground Water | FHP | CP036-1CSN-*****A | BIVA-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | No
214776192 | Ground Water | TRANE | GETK0187-5 |  | 19400 | 21.6 | 19000 | 4.47 | 1.6167 | No
214776193 | Ground Water | TRANE | GETK0242-5 |  | 26300 | 24 | 24700 | 4.56 | 2.1917 | No
214776194 | Ground Water | TRANE | GETK0247-5 |  | 26300 | 24 | 24700 | 4.56 | 2.1917 | No
214776195 | Ground Water | TRANE | GETK0362-5 |  | 41700 | 22.6 | 37200 | 4.26 | 3.475 | No
214776196 | Ground Water | TRANE | GETK0367-5 |  | 41700 | 22.6 | 37200 | 4.26 | 3.475 | No
214796343 | Ground Water | WaterFurnace | W5A(V/H)024BD1**2 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | Yes
214796344 | Ground Water | WaterFurnace | W5A(V/H)030BD1**2 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | Yes
214796345 | Ground Water | WaterFurnace | W5A(V/H)036BD1**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | Yes
214796346 | Ground Water | WaterFurnace | W5A(V/H)042BD1**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | Yes
214796347 | Ground Water | WaterFurnace | W5A(V/H)048BD1**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | Yes
214796667 | Ground Water | WaterFurnace | W5A(V/H)018BD1**2 |  | 20800 | 27 | 18900 | 5 | 1.7333 | Yes
214796668 | Ground Water | WaterFurnace | W5A(V/H)060BD1**2 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | Yes
214796669 | Ground Water | WaterFurnace | W5A(V/H)072BD1**2 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | Yes
214810491 | Ground Water | GEOSTAR | G5A(V/H)018BD1**2 |  | 20800 | 27 | 18900 | 5 | 1.7333 | Yes
214810492 | Ground Water | GEOSTAR | G5A(V/H)024BD1**2 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | Yes
214810493 | Ground Water | GEOSTAR | G5A(V/H)030BD1**2 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | Yes
214810494 | Ground Water | GEOSTAR | G5A(V/H)036BD1**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | Yes
214810495 | Ground Water | GEOSTAR | G5A(V/H)042BD1**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | Yes
214810496 | Ground Water | GEOSTAR | G5A(V/H)048BD1**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | Yes
214810497 | Ground Water | GEOSTAR | G5A(V/H)060BD1**2 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | Yes
214810498 | Ground Water | GEOSTAR | G5A(V/H)072BD1**2 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | Yes
214823444 | Ground Water | GeoSmart Energy | S5A(V/H)018BD1**2 |  | 20800 | 27 | 18900 | 5 | 1.7333 | Yes
214823445 | Ground Water | GeoSmart Energy | S5A(V/H)024BD1**2 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | Yes
214823446 | Ground Water | GeoSmart Energy | S5A(V/H)030BD1**2 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | Yes
214823447 | Ground Water | GeoSmart Energy | S5A(V/H)036BD1**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | Yes
214823448 | Ground Water | GeoSmart Energy | S5A(V/H)042BD1**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | Yes
214823449 | Ground Water | GeoSmart Energy | S5A(V/H)048BD1**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | Yes
214823450 | Ground Water | GeoSmart Energy | S5A(V/H)060BD1**2 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | Yes
214823451 | Ground Water | GeoSmart Energy | S5A(V/H)072BD1**2 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | Yes
214823480 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)018BD1**2 |  | 20800 | 27 | 18900 | 5 | 1.7333 | Yes
214823481 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024BD1**2 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | Yes
214823482 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030BD1**2 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | Yes
215429158 | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215429159 | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215429160 | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215429161 | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215429162 | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
215429163 | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
215429170 | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215429171 | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215429172 | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215429173 | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215429174 | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
215429175 | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
215743134 | Ground Water | TRANE | GECK006 |  | 9300 | 21.7 | 8100 | 4.5 | 0.775 | No
215743135 | Ground Water | TRANE | GECK009 |  | 9500 | 23 | 8400 | 4.5 | 0.79167 | No
215743136 | Ground Water | TRANE | GECK012 |  | 13300 | 23.2 | 11600 | 4.3 | 1.1083 | No
215832292 | Ground Water | AE Air | WSH6012D* |  | 13000 | 23 | 11000 | 4.6 | 1.0833 | No
215832293 | Ground Water | AE Air | WSH6018D* |  | 20400 | 25 | 16000 | 4.3 | 1.7 | No
215832294 | Ground Water | AE Air | WSH6024D* |  | 28000 | 25 | 21400 | 4.3 | 2.3333 | No
215832295 | Ground Water | AE Air | WSH6030D* |  | 32400 | 24 | 26000 | 4.2 | 2.7 | No
215832296 | Ground Water | AE Air | WSH6036D* |  | 39000 | 23.2 | 35000 | 4.1 | 3.25 | No
215832297 | Ground Water | AE Air | WSH6042D* |  | 45500 | 23.3 | 38000 | 4.3 | 3.7917 | No
215832298 | Ground Water | AE Air | WSH6048D* |  | 52500 | 23.6 | 45500 | 4.2 | 4.375 | No
215832299 | Ground Water | AE Air | WSH6060D* |  | 64000 | 23.5 | 51000 | 4.3 | 5.3333 | No
215832300 | Ground Water | AE Air | WSH6072D* |  | 78000 | 21.8 | 68000 | 4.1 | 6.5 | No
202921913 | Ground Water | BOSCH | EP036-3HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921914 | Ground Water | BOSCH | EP036-4HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921915 | Ground Water | BOSCH-GEO | BP036-1HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921952 | Ground Water | FHP | EP036-1HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921953 | Ground Water | FHP | EP036-3HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921954 | Ground Water | FHP | EP036-4HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202921956 | Ground Water | BOSCH | BP036-1HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202921957 | Ground Water | FHP | EP036-1VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921958 | Ground Water | FHP | EP036-3VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921959 | Ground Water | FHP | EP036-4VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921960 | Ground Water | BOSCH | BP036-1VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922686 | Ground Water | CARRIER | 50PSH036***3/CA |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202922689 | Ground Water | CARRIER | 50PSH036***5/EA |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202922692 | Ground Water | CARRIER | 50PSH036***6/FA |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202922695 | Ground Water | CARRIER | GB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202922697 | Ground Water | BRYANT | GB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922700 | Ground Water | HEIL | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
202922703 | Ground Water | ARCOAIRE | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922706 | Ground Water | KEEPRITE | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922708 | Ground Water | TEMPSTAR | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922711 | Ground Water | COMFORTMAKER | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922714 | Ground Water | DAY & NIGHT | HB036H******1**1 |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | Yes
202922716 | Ground Water | CARRIER | 50PSV036***3/CA |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202922719 | Ground Water | CARRIER | 50PSV036***5/EA |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202922722 | Ground Water | CARRIER | 50PSV036***6/FA |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202922725 | Ground Water | CARRIER | GB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202922728 | Ground Water | BRYANT | GB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922731 | Ground Water | HEIL | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202922734 | Ground Water | ARCOAIRE | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922737 | Ground Water | KEEPRITE | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922740 | Ground Water | TEMPSTAR | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922742 | Ground Water | COMFORTMAKER | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
202922745 | Ground Water | DAY & NIGHT | HB036V******1**1 |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | Yes
7418803 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
7418887 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7418965 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7419110 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**5*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
7419218 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**0*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
7419321 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7419403 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7419473 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**3*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
7419527 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7419618 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7419681 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**4*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
7419733 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7419797 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7420917 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**5*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
7421327 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
7421397 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
7421438 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
7421969 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
7421970 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
7421971 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
7421972 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421973 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421974 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
7421975 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421976 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421977 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
7421980 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421989 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
7421999 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**5*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
7422020 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422043 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422058 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
217531660 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)006A |  | 7600 | 30 | 6200 | 4.8 | 0.63333 | Yes
217531661 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)009A |  | 10500 | 28 | 9000 | 4.6 | 0.875 | Yes
217531662 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)012A |  | 13700 | 28.3 | 12200 | 4.3 | 1.1417 | Yes
217531663 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)018A |  | 22000 | 28.1 | 18900 | 4.9 | 1.8333 | Yes
215223342 | Ground Water | WaterFurnace | V5C(C/W/S)015**0**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
216743615 | Ground Water | BOSCH | CA009-1***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216743616 | Ground Water | BOSCH | CA009-2***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216743617 | Ground Water | BOSCH-GEO | RP024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216743618 | Ground Water | BOSCH | CP024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743619 | Ground Water | BOSCH | CP024-2VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743620 | Ground Water | BOSCH | CP024-3VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743621 | Ground Water | BOSCH | CP024-4VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743622 | Ground Water | BOSCH-GEO | RP024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216743623 | Ground Water | BOSCH | CP024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216743624 | Ground Water | BOSCH | CP024-2VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216743625 | Ground Water | BOSCH | CP024-3VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216743626 | Ground Water | BOSCH | CP024-4VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216743627 | Ground Water | BOSCH-GEO | RP024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216743628 | Ground Water | BOSCH | CP024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743629 | Ground Water | BOSCH | CP024-2HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743630 | Ground Water | BOSCH | CP024-3HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743631 | Ground Water | BOSCH | CP024-4HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216743632 | Ground Water | BOSCH-GEO | RP024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216743633 | Ground Water | BOSCH | CP024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216743634 | Ground Water | BOSCH | CP024-2HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216743635 | Ground Water | BOSCH | CP024-3HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216743636 | Ground Water | BOSCH | CP024-4HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216743637 | Ground Water | BOSCH-GEO | RP036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216743638 | Ground Water | BOSCH | CP036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216743639 | Ground Water | BOSCH | CP036-2VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216743640 | Ground Water | BOSCH | CP036-3VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216743641 | Ground Water | BOSCH | CP036-4VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216743642 | Ground Water | BOSCH-GEO | RP036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216743643 | Ground Water | BOSCH | CP036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216743644 | Ground Water | BOSCH | CP036-2VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216743645 | Ground Water | BOSCH | CP036-3VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216743646 | Ground Water | BOSCH | CP036-4VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216743647 | Ground Water | BOSCH-GEO | RP048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
5295966 | Ground Water | WaterFurnace | NBV/NBH018**2*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
5295968 | Ground Water | WaterFurnace | NBV/NBH018**0*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
5295969 | Ground Water | WaterFurnace | NBV/NBH018**0*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
5295980 | Ground Water | WaterFurnace | NBV/NBH024**0*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
5295981 | Ground Water | WaterFurnace | NBV/NBH024**3*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
5295982 | Ground Water | WaterFurnace | NBV/NBH024**4*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
5295983 | Ground Water | WaterFurnace | NBV/NBH024**2*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
5295984 | Ground Water | WaterFurnace | NBV/NBH024**0*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295985 | Ground Water | WaterFurnace | NBV/NBH024**3*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295986 | Ground Water | WaterFurnace | NBV/NBH024**2*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295987 | Ground Water | WaterFurnace | NBV/NBH024**4*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295988 | Ground Water | WaterFurnace | NBV/NBH024**4*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295989 | Ground Water | WaterFurnace | NBV/NBH024**3*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295990 | Ground Water | WaterFurnace | NBV/NBH024**0*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295991 | Ground Water | WaterFurnace | NBV/NBH024**2*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
5295992 | Ground Water | WaterFurnace | NBV/NBH030**0*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
5295993 | Ground Water | WaterFurnace | NBV/NBH030**3*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
5295994 | Ground Water | WaterFurnace | NBV/NBH030**4*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
5295995 | Ground Water | WaterFurnace | NBV/NBH030**2*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
5295996 | Ground Water | WaterFurnace | NBV/NBH030**0*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5295997 | Ground Water | WaterFurnace | NBV/NBH030**2*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
207348682 | Ground Water | WaterFurnace | URS060*0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348683 | Ground Water | WaterFurnace | URS060*0*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348684 | Ground Water | WaterFurnace | URS060*3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348685 | Ground Water | WaterFurnace | URS060*3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348686 | Ground Water | WaterFurnace | URS060*3*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348687 | Ground Water | WaterFurnace | URS060*4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348688 | Ground Water | WaterFurnace | URS060*4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348689 | Ground Water | WaterFurnace | URS060*4*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207348707 | Ground Water | WaterFurnace | URD038*0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348708 | Ground Water | WaterFurnace | URD038*0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348709 | Ground Water | WaterFurnace | URD038*0*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348710 | Ground Water | WaterFurnace | URD038*3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348711 | Ground Water | WaterFurnace | URD038*3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348712 | Ground Water | WaterFurnace | URD038*3*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348713 | Ground Water | WaterFurnace | URD038*4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348714 | Ground Water | WaterFurnace | URD038*4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348715 | Ground Water | WaterFurnace | URD038*4*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207348716 | Ground Water | WaterFurnace | URD049*0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348717 | Ground Water | WaterFurnace | URD049*0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348718 | Ground Water | WaterFurnace | URD049*0*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348719 | Ground Water | WaterFurnace | URD049*3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348720 | Ground Water | WaterFurnace | URD049*3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348721 | Ground Water | WaterFurnace | URD049*3*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348722 | Ground Water | WaterFurnace | URD049*4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348723 | Ground Water | WaterFurnace | URD049*4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348724 | Ground Water | WaterFurnace | URD049*4*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207348725 | Ground Water | WaterFurnace | URD064*0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348726 | Ground Water | WaterFurnace | URD064*0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348727 | Ground Water | WaterFurnace | URD064*0*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348728 | Ground Water | WaterFurnace | URD064*3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348729 | Ground Water | WaterFurnace | URD064*3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348730 | Ground Water | WaterFurnace | URD064*3*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348731 | Ground Water | WaterFurnace | URD064*4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348732 | Ground Water | WaterFurnace | URD064*4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348733 | Ground Water | WaterFurnace | URD064*4*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207348734 | Ground Water | WaterFurnace | URD072*0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348735 | Ground Water | WaterFurnace | URD072*0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348736 | Ground Water | WaterFurnace | URD072*0*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348737 | Ground Water | WaterFurnace | URD072*3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348738 | Ground Water | WaterFurnace | URD072*3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348739 | Ground Water | WaterFurnace | URD072*3*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348740 | Ground Water | WaterFurnace | URD072*4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348741 | Ground Water | WaterFurnace | URD072*4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207348742 | Ground Water | WaterFurnace | URD072*4*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
215811946 | Ground Water | HYDROTECH | WSV6009D* |  | 11000 | 26 | 8800 | 4.3 | 0.91667 | No
215811947 | Ground Water | AE Air | WSV6009D* |  | 11000 | 26 | 8800 | 4.3 | 0.91667 | No
215811948 | Ground Water | HYDROTECH | WSV6012D* |  | 13500 | 26 | 11000 | 4.1 | 1.125 | No
215811950 | Ground Water | AE Air | WSV6012D* |  | 13500 | 26 | 11000 | 4.1 | 1.125 | No
215811951 | Ground Water | HYDROTECH | WSV6018D* |  | 20000 | 21.1 | 16000 | 4.1 | 1.6667 | No
215811952 | Ground Water | AE Air | WSV6018D* |  | 20000 | 21.1 | 16000 | 4.1 | 1.6667 | No
215811953 | Ground Water | HYDROTECH | WSV6024D* |  | 24000 | 23 | 22000 | 4.1 | 2 | No
215811954 | Ground Water | AE Air | WSV6024D* |  | 24000 | 23 | 22000 | 4.1 | 2 | No
215811955 | Ground Water | HYDROTECH | WSV6030D* |  | 30000 | 22.5 | 24000 | 4.1 | 2.5 | No
215811957 | Ground Water | AE Air | WSV6030D* |  | 30000 | 22.5 | 24000 | 4.1 | 2.5 | No
215811958 | Ground Water | HYDROTECH | WSV6036D* |  | 39000 | 22 | 35000 | 4.1 | 3.25 | No
215811959 | Ground Water | AE Air | WSV6036D* |  | 39000 | 22 | 35000 | 4.1 | 3.25 | No
215811960 | Ground Water | HYDROTECH | WSV6042D* |  | 44000 | 24 | 37000 | 4.3 | 3.6667 | No
215811961 | Ground Water | AE Air | WSV6042D* |  | 44000 | 24 | 37000 | 4.3 | 3.6667 | No
215811962 | Ground Water | HYDROTECH | WSV6048D* |  | 55000 | 23 | 38000 | 4.1 | 4.5833 | No
215811964 | Ground Water | AE Air | WSV6048D* |  | 55000 | 23 | 38000 | 4.1 | 4.5833 | No
215815841 | Ground Water | HYDROTECH | WSV6060D* |  | 67000 | 23.8 | 53500 | 4.3 | 5.5833 | No
215815842 | Ground Water | AE Air | WSV6060D* |  | 67000 | 23.8 | 53500 | 4.3 | 5.5833 | No
215815843 | Ground Water | HYDROTECH | WSV6072D* |  | 77000 | 22.1 | 63500 | 4.1 | 6.4167 | No
215815844 | Ground Water | AE Air | WSV6072D* |  | 77000 | 22.1 | 63500 | 4.1 | 6.4167 | No
215415780 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)024A*VB |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415781 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)024A*VC |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415784 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)030A*VB |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415785 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)030A*VC |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415788 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)036A*VB |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415789 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)036A*VC |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415792 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)042A*VB |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415793 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)042A*VC |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415794 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)048A*B |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415795 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)048A*C |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415796 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)048A*VB |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415797 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)048A*VC |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415800 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)060A*VB |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
215415801 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)060A*VC |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
217014540 | Ground Water | KEEPRITE | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014541 | Ground Water | TEMPSTAR | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014542 | Ground Water | COMFORTMAKER | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014543 | Ground Water | DAY & NIGHT | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014544 | Ground Water | HEIL | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014545 | Ground Water | ARCOAIRE | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014546 | Ground Water | KEEPRITE | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014547 | Ground Water | TEMPSTAR | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014548 | Ground Water | COMFORTMAKER | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014549 | Ground Water | DAY & NIGHT | HCR72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014550 | Ground Water | HEIL | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014551 | Ground Water | ARCOAIRE | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014552 | Ground Water | KEEPRITE | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014553 | Ground Water | TEMPSTAR | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014554 | Ground Water | COMFORTMAKER | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014555 | Ground Water | DAY & NIGHT | HCR72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217037791 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS024BD1 | Y5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037792 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS036BD1 | Y5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037793 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS048BD1 | Y5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037794 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS060BD1 | Y5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037795 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS066BD1 | Y5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037796 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ024BD1 | Y5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037797 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ036BD1 | Y5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037798 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ048BD1 | Y5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037799 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ060BD1 | Y5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037800 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ066BD1 | Y5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037801 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037802 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037803 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037804 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037805 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SS066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037806 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037807 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037808 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037809 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037810 | Ground Water | YORK BY JOHNSON CONTROLS | Y5SZ066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037811 | Ground Water | GeoSmart Energy | S5SS024BD1 | S5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037812 | Ground Water | GeoSmart Energy | S5SS036BD1 | S5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037813 | Ground Water | GeoSmart Energy | S5SS048BD1 | S5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037814 | Ground Water | GeoSmart Energy | S5SS060BD1 | S5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037815 | Ground Water | GeoSmart Energy | S5SS066BD1 | S5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037816 | Ground Water | GeoSmart Energy | S5SZ024BD1 | S5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037817 | Ground Water | GeoSmart Energy | S5SZ036BD1 | S5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037818 | Ground Water | GeoSmart Energy | S5SZ048BD1 | S5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037819 | Ground Water | GeoSmart Energy | S5SZ060BD1 | S5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037820 | Ground Water | GeoSmart Energy | S5SZ066BD1 | S5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037821 | Ground Water | GeoSmart Energy | S5SS024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217037822 | Ground Water | GeoSmart Energy | S5SS036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037823 | Ground Water | GeoSmart Energy | S5SS048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037824 | Ground Water | GeoSmart Energy | S5SS060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037825 | Ground Water | GeoSmart Energy | S5SS066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
217037826 | Ground Water | GeoSmart Energy | S5SZ024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216802011 | Ground Water | CARRIER | 50WT*048***6*(A-H)** |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216802012 | Ground Water | CARRIER | 50WT*048***6*(J-R)** |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216802013 | Ground Water | CARRIER | 50WT*060***3*(A-H)** |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216802014 | Ground Water | CARRIER | 50WT*060***3*(J-R)** |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216802015 | Ground Water | CARRIER | 50WT*060***5*(A-H)** |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216802016 | Ground Water | CARRIER | 50WT*060***5*(J-R)** |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216802017 | Ground Water | CARRIER | 50WT*060***6*(A-H)** |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216802018 | Ground Water | CARRIER | 50WT*060***6*(J-R)** |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
216802019 | Ground Water | CARRIER | 50WT*070(G-K;N-R)**3*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802020 | Ground Water | CARRIER | 50WT*070(G-K;N-R)**3*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216802021 | Ground Water | CARRIER | 50WT*070(L/M/S/T)**3*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802022 | Ground Water | CARRIER | 50WT*070(L/M/S/T)**3*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216802023 | Ground Water | CARRIER | 50WT*070(G-K;N-R)**5*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802024 | Ground Water | CARRIER | 50WT*070(G-K;N-R)**5*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216802025 | Ground Water | CARRIER | 50WT*070(L/M/S/T)**5*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802026 | Ground Water | CARRIER | 50WT*070(L/M/S/T)**5*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216802027 | Ground Water | CARRIER | 50WT*070(G-K;N-R)**6*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802028 | Ground Water | CARRIER | 50WT*070(G-K;N-R)**6*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216802029 | Ground Water | CARRIER | 50WT*070(L/M/S/T)**6*(A-H)** |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
216802030 | Ground Water | CARRIER | 50WT*070(L/M/S/T)**6*(J-R)** |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
216979809 | Ground Water | CARRIER | GCA24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979810 | Ground Water | BRYANT | GCA24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979811 | Ground Water | CARRIER | GCA24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979812 | Ground Water | BRYANT | GCA24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979813 | Ground Water | CARRIER | GCA24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979814 | Ground Water | BRYANT | GCA24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979815 | Ground Water | CARRIER | GCA24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979816 | Ground Water | BRYANT | GCA24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979817 | Ground Water | CARRIER | GCA36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979818 | Ground Water | BRYANT | GCA36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979819 | Ground Water | CARRIER | GCA36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216979820 | Ground Water | BRYANT | GCA36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979821 | Ground Water | CARRIER | GCA48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979822 | Ground Water | BRYANT | GCA48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979823 | Ground Water | CARRIER | GCA48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979824 | Ground Water | BRYANT | GCA48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979825 | Ground Water | CARRIER | GCA60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979826 | Ground Water | BRYANT | GCA60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979827 | Ground Water | CARRIER | GCA60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979828 | Ground Water | BRYANT | GCA60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979837 | Ground Water | HEIL | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979838 | Ground Water | ARCOAIRE | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979839 | Ground Water | KEEPRITE | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979840 | Ground Water | TEMPSTAR | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979841 | Ground Water | COMFORTMAKER | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979842 | Ground Water | DAY & NIGHT | HCR24V**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979843 | Ground Water | HEIL | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979844 | Ground Water | ARCOAIRE | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979845 | Ground Water | KEEPRITE | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979846 | Ground Water | TEMPSTAR | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979847 | Ground Water | COMFORTMAKER | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979848 | Ground Water | DAY & NIGHT | HCR24V**N******1 |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
216979849 | Ground Water | HEIL | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979850 | Ground Water | ARCOAIRE | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979851 | Ground Water | KEEPRITE | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979852 | Ground Water | TEMPSTAR | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
963498 | Ground Water | WaterFurnace | NLH/NXH080**3 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
963499 | Ground Water | WaterFurnace | NLH/NXH080**4 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
963500 | Ground Water | WaterFurnace | NLH/NXH080**5 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
963501 | Ground Water | WaterFurnace | NLH/NXH095**3 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
963502 | Ground Water | WaterFurnace | NLH/NXH095**4 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
963503 | Ground Water | WaterFurnace | NLH/NXH095**5 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
963504 | Ground Water | WaterFurnace | NLH/NXH120**3 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
963505 | Ground Water | WaterFurnace | NLH/NXH120**4 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
963506 | Ground Water | WaterFurnace | NLH/NXH120**5 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
963507 | Ground Water | WaterFurnace | NLV/NXV080T*3 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
963508 | Ground Water | WaterFurnace | NLV/NXV080T*4 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
963509 | Ground Water | WaterFurnace | NLV/NXV080T*5 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
963510 | Ground Water | WaterFurnace | NLV/NXV095T*3 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
963511 | Ground Water | WaterFurnace | NLV/NXV095T*4 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
963512 | Ground Water | WaterFurnace | NLV/NXV095T*5 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
963513 | Ground Water | WaterFurnace | NLV/NXV120T*3 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
963514 | Ground Water | WaterFurnace | NLV/NXV120T*4 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
963515 | Ground Water | WaterFurnace | NLV/NXV120T*5 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
1483426 | Ground Water | BOSCH | BP012-1HZ/VT |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
1483428 | Ground Water | BOSCH | BP024-1HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
1483429 | Ground Water | BOSCH | BP030-1HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
3059231 | Ground Water | WaterFurnace | NCC/NCW/NCS/NCE15*2 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
3059237 | Ground Water | WaterFurnace | NCC/NCW/NCS/NCE15*0 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
3093286 | Ground Water | TRANE | GEHE072 |  | 83200 | 21.9 | 69100 | 4.2 | 6.9333 | No
3093289 | Ground Water | TRANE | GEVE072 |  | 84800 | 22.85 | 70200 | 4.18 | 7.0667 | No
3093290 | Ground Water | TRANE | GEVE090 |  | 98600 | 22.91 | 83600 | 4.1 | 8.2167 | No
3627926 | Ground Water | WaterFurnace | USV/USH015**0*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
3627927 | Ground Water | WaterFurnace | USV/USH015**2*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
202147710 | Ground Water | HYDRON MODULE | HZS042*3***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147711 | Ground Water | TETCO | TZS042*3***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147712 | Ground Water | GEOCOMFORT | GZS060*3***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202147713 | Ground Water | HYDRON MODULE | HZS060*3***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202147714 | Ground Water | TETCO | TZS060*3***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202211042 | Ground Water | WaterFurnace | URD038*0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211043 | Ground Water | WaterFurnace | URD038*0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211044 | Ground Water | WaterFurnace | URD038*0*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211045 | Ground Water | WaterFurnace | URD038*3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211046 | Ground Water | WaterFurnace | URD038*3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211047 | Ground Water | WaterFurnace | URD038*3*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202211048 | Ground Water | WaterFurnace | URD049*0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211049 | Ground Water | WaterFurnace | URD049*0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211050 | Ground Water | WaterFurnace | URD049*0*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
206726878 | Ground Water | GEOCOMFORT | GBT060 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | Yes
206726879 | Ground Water | HYDRON MODULE | HBT060 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | Yes
206726880 | Ground Water | TETCO | TBT060 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | Yes
206726881 | Ground Water | GEOCOMFORT | GBT060*2 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | No
206726882 | Ground Water | HYDRON MODULE | HBT060*2 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | No
206726883 | Ground Water | TETCO | TBT060*2 | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | No
206900466 | Ground Water | WaterFurnace | UDV084**4 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900467 | Ground Water | WaterFurnace | UDV096**4 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900469 | Ground Water | WaterFurnace | UDV084**3 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900470 | Ground Water | WaterFurnace | UDV084**5 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900471 | Ground Water | WaterFurnace | UDH084**3 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900472 | Ground Water | WaterFurnace | UDH084**4 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900473 | Ground Water | WaterFurnace | UDH084**5 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900474 | Ground Water | WaterFurnace | UDV096**3 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900475 | Ground Water | WaterFurnace | UDV096**5 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900553 | Ground Water | GEOSTAR | GDV084**3 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900554 | Ground Water | GEOSTAR | GDV084**4 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900555 | Ground Water | GEOSTAR | GDV084**5 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900556 | Ground Water | GEOSTAR | GDH084**3 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900557 | Ground Water | GEOSTAR | GDH084**4 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900558 | Ground Water | GEOSTAR | GDH084**5 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900559 | Ground Water | GEOSTAR | GDV096**3 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900560 | Ground Water | GEOSTAR | GDV096**4 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900561 | Ground Water | GEOSTAR | GDV096**5 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900571 | Ground Water | YORK BY JOHNSON CONTROLS | YDLV084**3 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900572 | Ground Water | YORK BY JOHNSON CONTROLS | YDLV084**4 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
217642990 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S0**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642991 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S3**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642992 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S3**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642993 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S4**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642994 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S4**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216419907 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
216419908 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
216419909 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
216419912 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
202146871 | Ground Water | TETCO | TZT030*3 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146872 | Ground Water | GEOCOMFORT | GZT036 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | Yes
202146873 | Ground Water | GEOCOMFORT | GZT036*2 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146874 | Ground Water | GEOCOMFORT | GZT036*3 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146875 | Ground Water | GEOCOMFORT | GZT036*A |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146876 | Ground Water | HYDRON MODULE | HZT036 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | Yes
202146877 | Ground Water | HYDRON MODULE | HZT036*2 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146878 | Ground Water | HYDRON MODULE | HZT036*3 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146879 | Ground Water | HYDRON MODULE | HZT036*A |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146880 | Ground Water | TETCO | TZT036 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | Yes
202146881 | Ground Water | TETCO | TZT036*2 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146882 | Ground Water | TETCO | TZT036*3 |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146883 | Ground Water | TETCO | TZT036*A |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | No
202146884 | Ground Water | GEOCOMFORT | GZT042 |  | 46000 | 23.4 | 40100 | 4.4 | 3.8333 | Yes
202146885 | Ground Water | GEOCOMFORT | GZT042*2 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146886 | Ground Water | GEOCOMFORT | GZT042*3 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146887 | Ground Water | HYDRON MODULE | HZT042 |  | 46000 | 23.4 | 40100 | 4.4 | 3.8333 | Yes
202146888 | Ground Water | HYDRON MODULE | HZT042*2 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146889 | Ground Water | HYDRON MODULE | HZT042*3 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146890 | Ground Water | TETCO | TZT042 |  | 46000 | 23.4 | 40100 | 4.4 | 3.8333 | Yes
202146891 | Ground Water | TETCO | TZT042*2 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146892 | Ground Water | TETCO | TZT042*3 |  | 46000 | 23.4 | 40100 | 4.3 | 3.8333 | No
202146893 | Ground Water | GEOCOMFORT | GZT048 |  | 52200 | 22.1 | 45900 | 4.4 | 4.35 | Yes
202146894 | Ground Water | GEOCOMFORT | GZT048*2 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146895 | Ground Water | GEOCOMFORT | GZT048*3 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146896 | Ground Water | GEOCOMFORT | GZT048*A |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146897 | Ground Water | HYDRON MODULE | HZT048 |  | 52200 | 22.1 | 45900 | 4.4 | 4.35 | Yes
202146898 | Ground Water | HYDRON MODULE | HZT048*2 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146899 | Ground Water | HYDRON MODULE | HZT048*3 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146900 | Ground Water | HYDRON MODULE | HZT048*A |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146901 | Ground Water | TETCO | TZT048 |  | 52200 | 22.1 | 45900 | 4.4 | 4.35 | Yes
202146902 | Ground Water | TETCO | TZT048*2 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146903 | Ground Water | TETCO | TZT048*3 |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202146904 | Ground Water | GEOCOMFORT | GZT060 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | Yes
202146905 | Ground Water | GEOCOMFORT | GZT060*2 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146906 | Ground Water | GEOCOMFORT | GZT060*3 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146907 | Ground Water | HYDRON MODULE | HZT060 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | Yes
202146908 | Ground Water | HYDRON MODULE | HZT060*2 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146909 | Ground Water | HYDRON MODULE | HZT060*3 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146910 | Ground Water | TETCO | TZT060 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | Yes
202146911 | Ground Water | TETCO | TZT060*2 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146912 | Ground Water | TETCO | TZT060*3 |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202146913 | Ground Water | GEOCOMFORT | GZS015 |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | Yes
202146914 | Ground Water | GEOCOMFORT | GZS015*A |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | No
202146915 | Ground Water | GEOCOMFORT | GZS015*****1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | Yes
202146916 | Ground Water | HYDRON MODULE | HZS015 |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | Yes
202146917 | Ground Water | HYDRON MODULE | HZS015*A |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | No
202146918 | Ground Water | HYDRON MODULE | HZS015*****1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | Yes
202146919 | Ground Water | TETCO | TZS015 |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | Yes
202146920 | Ground Water | TETCO | TZS015*A |  | 16100 | 24.4 | 14300 | 4.7 | 1.3417 | No
202146921 | Ground Water | TETCO | TZS015*****1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | Yes
202146922 | Ground Water | GEOCOMFORT | GZS017 |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | Yes
202146923 | Ground Water | GEOCOMFORT | GZS017*A |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | No
202146924 | Ground Water | GEOCOMFORT | GZS017*****1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | Yes
202146925 | Ground Water | GEOCOMFORT | GZS017*A***1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | No
202146926 | Ground Water | HYDRON MODULE | HZS017 |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | Yes
206438717 | Ground Water | BOSCH | EP007-1HZ/VT*-*****B |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438718 | Ground Water | BOSCH | EP007-2HZ/VT*-*****B |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438719 | Ground Water | BOSCH | EP009-1HZ/VT*-*****B |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438720 | Ground Water | BOSCH | EP009-2HZ/VT*-*****B |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438721 | Ground Water | BOSCH | EP012-0HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438722 | Ground Water | BOSCH | EP012-0HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438723 | Ground Water | BOSCH | EP012-0VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438724 | Ground Water | BOSCH | EP012-0VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
217351799 | Ground Water | ARCOAIRE | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351800 | Ground Water | ARCOAIRE | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351801 | Ground Water | ARCOAIRE | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351803 | Ground Water | ARCOAIRE | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351804 | Ground Water | ARCOAIRE | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351806 | Ground Water | ARCOAIRE | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351808 | Ground Water | ARCOAIRE | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351811 | Ground Water | COMFORTMAKER | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351812 | Ground Water | COMFORTMAKER | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351813 | Ground Water | COMFORTMAKER | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351814 | Ground Water | COMFORTMAKER | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351815 | Ground Water | COMFORTMAKER | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351816 | Ground Water | COMFORTMAKER | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351817 | Ground Water | COMFORTMAKER | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351819 | Ground Water | COMFORTMAKER | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351820 | Ground Water | COMFORTMAKER | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351822 | Ground Water | COMFORTMAKER | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351823 | Ground Water | COMFORTMAKER | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351824 | Ground Water | COMFORTMAKER | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351825 | Ground Water | COMFORTMAKER | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351826 | Ground Water | COMFORTMAKER | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351827 | Ground Water | COMFORTMAKER | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351828 | Ground Water | COMFORTMAKER | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351830 | Ground Water | COMFORTMAKER | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351831 | Ground Water | COMFORTMAKER | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351833 | Ground Water | COMFORTMAKER | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351835 | Ground Water | COMFORTMAKER | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351838 | Ground Water | DAY & NIGHT | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351839 | Ground Water | DAY & NIGHT | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351840 | Ground Water | DAY & NIGHT | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351841 | Ground Water | DAY & NIGHT | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351842 | Ground Water | DAY & NIGHT | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
7523958 | Ground Water | TETCO | TVS018*****1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | Yes
7523959 | Ground Water | GEOCOMFORT | GVS018*A***1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | No
7523960 | Ground Water | HYDRON MODULE | HVS018*A***1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | No
7523961 | Ground Water | TETCO | TVS018*A***1 |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | No
216714612 | Ground Water | GEOSTAR | G3A(V/H)015*R0**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
216714613 | Ground Water | GEOSTAR | G3A(V/H)015*R0**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
216714614 | Ground Water | GEOSTAR | G3A(V/H)015*R2**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
216714615 | Ground Water | GEOSTAR | G3A(V/H)015*R2**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
216714620 | Ground Water | GEOSTAR | G3A(V/H)024*S0**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714621 | Ground Water | GEOSTAR | G3A(V/H)024*S0**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714622 | Ground Water | GEOSTAR | G3A(V/H)024*S2**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714623 | Ground Water | GEOSTAR | G3A(V/H)024*S2**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714624 | Ground Water | GEOSTAR | G3A(V/H)024*S3**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714625 | Ground Water | GEOSTAR | G3A(V/H)024*S3**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714626 | Ground Water | GEOSTAR | G3A(V/H)024*S4**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216714627 | Ground Water | GEOSTAR | G3A(V/H)024*S4**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
216625872 | Ground Water | GeoSmart Energy | S5A(V/H)072*D3**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625873 | Ground Water | GeoSmart Energy | S5A(V/H)072*D3**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625874 | Ground Water | GeoSmart Energy | S5A(V/H)072*D4**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625875 | Ground Water | GeoSmart Energy | S5A(V/H)072*D4**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625876 | Ground Water | GeoSmart Energy | S5A(V/H)072*S0**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625877 | Ground Water | GeoSmart Energy | S5A(V/H)072*S0**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625878 | Ground Water | GeoSmart Energy | S5A(V/H)072*S3**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
202084059 | Ground Water | GEOCOMFORT | GZT024*2 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
202084060 | Ground Water | HYDRON MODULE | HZT024 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | Yes
202084061 | Ground Water | HYDRON MODULE | HZT024*2 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
202084062 | Ground Water | TETCO | TZT024 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | Yes
202084063 | Ground Water | TETCO | TZT024*2 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
202132024 | Ground Water | NORTHERN HEAT PUMP | N-D/H/V-A-038-* |  | 42000 | 22.89 | 42600 | 4.28 | 3.5 | No
202132025 | Ground Water | NORTHERN HEAT PUMP | N-D/H/V-A-050-* |  | 55400 | 22.21 | 57300 | 4.1 | 4.6167 | No
202132026 | Ground Water | NORTHERN HEAT PUMP | N-D/H/V-A-060-* |  | 65000 | 21.4 | 63500 | 4.1 | 5.4167 | No
202146863 | Ground Water | GEOCOMFORT | GZT030 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | Yes
202146864 | Ground Water | GEOCOMFORT | GZT030*2 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146865 | Ground Water | GEOCOMFORT | GZT030*3 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146866 | Ground Water | HYDRON MODULE | HZT030 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | Yes
202146867 | Ground Water | HYDRON MODULE | HZT030*2 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146868 | Ground Water | HYDRON MODULE | HZT030*3 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202146869 | Ground Water | TETCO | TZT030 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | Yes
202146870 | Ground Water | TETCO | TZT030*2 |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
206347324 | Ground Water | COMFORT-AIRE | HEV/H036D |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
206347325 | Ground Water | CENTURY | HEV/H036D |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
206347960 | Ground Water | HYDROTECH | WSS6006*6* |  | 8600 | 26 | 7200 | 4.5 | 0.71667 | No
206347961 | Ground Water | HYDROTECH | WSS6009*6* |  | 11200 | 26 | 8200 | 4.5 | 0.93333 | No
206347962 | Ground Water | HYDROTECH | WSS6012*6* |  | 13800 | 26 | 10400 | 4.5 | 1.15 | No
206347963 | Ground Water | HYDROTECH | WSS6015*6* |  | 18100 | 23.1 | 15500 | 4.3 | 1.5083 | No
206422417 | Ground Water | CENTURY | HBH/V015*W/K |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
206422418 | Ground Water | COMFORT-AIRE | HBH/V015*W/K |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
206422419 | Ground Water | CENTURY | HBH/V018*W/K |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
206438725 | Ground Water | BOSCH | EP012-1HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438726 | Ground Water | BOSCH | EP012-1HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438727 | Ground Water | BOSCH | EP012-1VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438728 | Ground Water | BOSCH | EP012-1VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438729 | Ground Water | BOSCH | EP012-2HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438730 | Ground Water | BOSCH | EP012-2HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438731 | Ground Water | BOSCH | EP012-2VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438732 | Ground Water | BOSCH | EP012-2VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438733 | Ground Water | BOSCH | EP015-2HZ/VT*-*****B |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438734 | Ground Water | BOSCH | EP030-1HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438735 | Ground Water | BOSCH | EP030-2HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438736 | Ground Water | BOSCH | EP030-3HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438737 | Ground Water | BOSCH | EP030-4HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438738 | Ground Water | BOSCH | EP060-3HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438739 | Ground Water | BOSCH | EP060-4HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438740 | Ground Water | BOSCH | EP070-3HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438741 | Ground Water | BOSCH | EP070-4HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438761 | Ground Water | BOSCH | EP012-1HZ/VT*-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438762 | Ground Water | BOSCH | EP015-1HZ/VT*-*****B |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438763 | Ground Water | BOSCH | EP060-1HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438764 | Ground Water | BOSCH | EP070-1HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
214839280 | Ground Water | BOSCH | RL042-1HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839281 | Ground Water | BOSCH | RL042-1VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839282 | Ground Water | BOSCH | RL042-3HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839283 | Ground Water | BOSCH | RL042-3VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839284 | Ground Water | BOSCH | RL042-4HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839285 | Ground Water | BOSCH | RL042-4VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214772066 | Ground Water | TRANE | GEVK0364 |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772067 | Ground Water | TRANE | GEVK0367 |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772068 | Ground Water | TRANE | GEVK042B |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214772069 | Ground Water | TRANE | GEVK0424 |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214772070 | Ground Water | TRANE | GEVK048B |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214772071 | Ground Water | TRANE | GEVK0484 |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214772072 | Ground Water | TRANE | GEVK060B |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214772073 | Ground Water | TRANE | GEVK0604 |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214772074 | Ground Water | TRANE | EXVK0097 |  | 9600 | 29.7 | 8500 | 5.16 | 0.8 | No
214772075 | Ground Water | TRANE | EXVK0127 |  | 12500 | 26.1 | 11500 | 4.98 | 1.0417 | No
214772076 | Ground Water | TRANE | EXVK0157 |  | 17100 | 24.6 | 15600 | 4.6 | 1.425 | No
214772077 | Ground Water | TRANE | EXVK0187 |  | 21100 | 29.6 | 18600 | 4.77 | 1.7583 | No
214772078 | Ground Water | TRANE | EXVK024B |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772079 | Ground Water | TRANE | EXVK0244 |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772080 | Ground Water | TRANE | EXVK0247 |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772081 | Ground Water | TRANE | EXVK030B |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772082 | Ground Water | TRANE | EXVK0304 |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772083 | Ground Water | TRANE | EXVK0307 |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772084 | Ground Water | TRANE | EXVK036B |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772085 | Ground Water | TRANE | EXVK0364 |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772086 | Ground Water | TRANE | EXVK0367 |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
216419920 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
216419921 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
216419922 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
216419924 | Ground Water | Whalen | WR(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
216419941 | Ground Water | Whalen | WZ(L/R/B/P/T/K)024A |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | Yes
216419942 | Ground Water | Whalen | WZ(L/R/B/P/T/K)030A |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | Yes
216419945 | Ground Water | Whalen | WZ(L/R/B/P/T/K)042A |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | Yes
216419946 | Ground Water | Whalen | WZ(L/R/B/P/T/K)048A |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | Yes
216419947 | Ground Water | Whalen | WZ(L/R/B/P/T/K)060A |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | Yes
216439574 | Ground Water | GeoSmart Energy | S5TV036BD1**2 |  | 41400 | 26.9 | 35700 | 5.1 | 3.45 | Yes
216439575 | Ground Water | GeoSmart Energy | S5TV048BD1**2 |  | 52500 | 24.5 | 47400 | 4.7 | 4.375 | Yes
216439576 | Ground Water | GeoSmart Energy | S5TV060BD1**2 |  | 67900 | 23.9 | 56000 | 4.6 | 5.6583 | Yes
216439577 | Ground Water | GeoSmart Energy | S5TV072BD1**2 |  | 77700 | 23 | 70700 | 4.5 | 6.475 | Yes
216508982 | Ground Water | ClimateMaster | SJ/PN024A | SKN024A | 24700 | 23.6 | 22800 | 4.6 | 2.0583 | Yes
216508983 | Ground Water | ClimateMaster | SJ/PN036A | SKN036A | 41000 | 23.6 | 33200 | 4.4 | 3.4167 | Yes
202146927 | Ground Water | HYDRON MODULE | HZS017*A |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | No
202146928 | Ground Water | HYDRON MODULE | HZS017*****1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | Yes
202146929 | Ground Water | HYDRON MODULE | HZS017*A***1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | No
202146930 | Ground Water | TETCO | TZS017 |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | Yes
202146931 | Ground Water | TETCO | TZS017*A |  | 19200 | 22.5 | 16900 | 4.5 | 1.6 | No
202146932 | Ground Water | TETCO | TZS017*****1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | Yes
202146933 | Ground Water | TETCO | TZS017*A***1 |  | 19400 | 24.9 | 16700 | 4.7 | 1.6167 | No
207323895 | Ground Water | WaterFurnace | NDS064H1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207323896 | Ground Water | WaterFurnace | NDZ072H1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
207323897 | Ground Water | WaterFurnace | NDZ072H1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
207323898 | Ground Water | WaterFurnace | NDS072H1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207323899 | Ground Water | WaterFurnace | NDS072H1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207323900 | Ground Water | WaterFurnace | NDS038J1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207323901 | Ground Water | WaterFurnace | NSZ022H1* | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
207323902 | Ground Water | WaterFurnace | NSZ030H1* | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
207323903 | Ground Water | WaterFurnace | NSZ036J1* | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
207323904 | Ground Water | WaterFurnace | NSZ042J1* | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
207323905 | Ground Water | WaterFurnace | NSZ048J1* | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
207323906 | Ground Water | WaterFurnace | NSZ048J1* | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
207323907 | Ground Water | WaterFurnace | NSZ060J1* | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
207323908 | Ground Water | WaterFurnace | NSZ060J1* | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
207323909 | Ground Water | WaterFurnace | NSZ070H1* | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
207323910 | Ground Water | WaterFurnace | NSZ022H1* | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
207323911 | Ground Water | WaterFurnace | NSZ030H1* | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
207323912 | Ground Water | WaterFurnace | NSZ036J1* | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
207323913 | Ground Water | WaterFurnace | NSZ042J1* | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
207323914 | Ground Water | WaterFurnace | NSZ070H1* | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
207324064 | Ground Water | WaterFurnace | NVV/NVH036C1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
207324066 | Ground Water | WaterFurnace | NVV/NVH060C1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | No
207335134 | Ground Water | GEOSTAR | 101/102J012**1*0***** |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
207335135 | Ground Water | GEOSTAR | 101/102J018**1*(1,4)***** |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | Yes
207335136 | Ground Water | GEOSTAR | 101/102J030**1*(1,4)***** |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | Yes
207335137 | Ground Water | GEOSTAR | 101/102K036**1*(1,2,4)***** |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | Yes
207335138 | Ground Water | GEOSTAR | 101/102K042**1*(1,2,4)***** |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | Yes
207335139 | Ground Water | GEOSTAR | 101/102K048**1*(1,2,4) |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | Yes
207335140 | Ground Water | GEOSTAR | 101/102K060**1*(1,4)****** |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | Yes
207335141 | Ground Water | GEOSTAR | 101/102J070**1*(1,4)***** |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | Yes
207335142 | Ground Water | GEOSTAR | 101/102J026**1*(1,4)***** |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335143 | Ground Water | GEOSTAR | 101/102K038**1*(1,2,4)***** |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207335144 | Ground Water | GEOSTAR | 101/102K049**1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335145 | Ground Water | GEOSTAR | 101/102K064**1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335146 | Ground Water | GEOSTAR | 101/102J072**1*(1,4)***** |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207335147 | Ground Water | GEOSTAR | 161/162K064**1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335247 | Ground Water | GEOSTAR | 101/102J022**1*(1,4)***** |  | 21900 | 27.5 | 21900 | 5 | 1.825 | Yes
207335249 | Ground Water | GEOSTAR | 161/162J026**1*(1,4)***** |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335251 | Ground Water | GEOSTAR | 161/162K038**1*(1,2,4)***** |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
215832281 | Ground Water | HYDROTECH | WSH6009D* |  | 10000 | 23 | 8000 | 4.2 | 0.83333 | No
215832282 | Ground Water | HYDROTECH | WSH6012D* |  | 13000 | 23 | 11000 | 4.6 | 1.0833 | No
215832283 | Ground Water | HYDROTECH | WSH6018D* |  | 20400 | 25 | 16000 | 4.3 | 1.7 | No
215832284 | Ground Water | HYDROTECH | WSH6024D* |  | 28000 | 25 | 21400 | 4.3 | 2.3333 | No
216625656 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S3**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625657 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S3**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625658 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S4**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625659 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S4**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625660 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625661 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625662 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625663 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625664 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625665 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625666 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625667 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625668 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625669 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625670 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625671 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625672 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625673 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625674 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625675 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625676 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625677 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625678 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625679 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625680 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625681 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625682 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625683 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625684 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D0**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625685 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D0**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625686 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D0**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625687 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D2**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625688 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D3**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625689 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D3**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625690 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D3**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625691 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D4**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625692 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D4**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625693 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D4**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625694 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625695 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625696 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625697 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S2**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625698 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625699 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625700 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625701 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625702 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625703 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
202330518 | Ground Water | AAON, Inc. | M2-003-2-H-BCBC-V0-10-000-A |  | 46200 | 25.5 | 38000 | 4.3 | 3.85 | No
202330522 | Ground Water | AAON, Inc. | M2-003-3-H-BCBC-V0-10-000-A |  | 46200 | 25.5 | 38000 | 4.3 | 3.85 | No
202330526 | Ground Water | AAON, Inc. | M2-003-4-H-BCBC-V0-10-000-A |  | 46200 | 25.5 | 38000 | 4.3 | 3.85 | No
202330529 | Ground Water | AAON, Inc. | M2-004-1-H-BCAC-V0-10-000-A |  | 55200 | 24.7 | 46300 | 4.3 | 4.6 | No
202330530 | Ground Water | AAON, Inc. | M2-004-1-H-BCBC-V0-10-000-A |  | 57500 | 26.1 | 46700 | 4.4 | 4.7917 | No
202330531 | Ground Water | AAON, Inc. | M2-004-1-H-DCAC-S0-10-000-A |  | 54200 | 23.5 | 45800 | 4.2 | 4.5167 | No
202330532 | Ground Water | AAON, Inc. | M2-004-1-H-DCBC-S0-10-000-A |  | 56200 | 23.9 | 46200 | 4.4 | 4.6833 | No
202330533 | Ground Water | AAON, Inc. | M2-004-2-H-BCAC-V0-10-000-A |  | 55200 | 24.7 | 46300 | 4.3 | 4.6 | No
202330534 | Ground Water | AAON, Inc. | M2-004-2-H-BCBC-V0-10-000-A |  | 57500 | 26.1 | 46700 | 4.4 | 4.7917 | No
202330535 | Ground Water | AAON, Inc. | M2-004-2-H-DCAC-S0-10-000-A |  | 54200 | 23.5 | 45800 | 4.2 | 4.5167 | No
202330536 | Ground Water | AAON, Inc. | M2-004-2-H-DCBC-S0-10-000-A |  | 56200 | 23.9 | 46200 | 4.4 | 4.6833 | No
202330537 | Ground Water | AAON, Inc. | M2-004-3-H-BCAC-V0-10-000-A |  | 55200 | 24.7 | 46300 | 4.3 | 4.6 | No
202330538 | Ground Water | AAON, Inc. | M2-004-3-H-BCBC-V0-10-000-A |  | 57500 | 26.1 | 46700 | 4.4 | 4.7917 | No
202330539 | Ground Water | AAON, Inc. | M2-004-3-H-DCAC-S0-10-000-A |  | 54200 | 23.5 | 45800 | 4.2 | 4.5167 | No
202330540 | Ground Water | AAON, Inc. | M2-004-3-H-DCBC-S0-10-000-A |  | 56200 | 23.9 | 46200 | 4.4 | 4.6833 | No
202330541 | Ground Water | AAON, Inc. | M2-004-4-H-BCAC-V0-10-000-A |  | 55200 | 24.7 | 46300 | 4.3 | 4.6 | No
215268741 | Ground Water | WaterFurnace | V5A(V/H)024*D0**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268742 | Ground Water | WaterFurnace | V5A(V/H)024*D2**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268743 | Ground Water | WaterFurnace | V5A(V/H)024*D3**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268744 | Ground Water | WaterFurnace | V5A(V/H)024*D4**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268745 | Ground Water | WaterFurnace | V5A(V/H)030*D0**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268746 | Ground Water | WaterFurnace | V5A(V/H)030*D3**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268747 | Ground Water | WaterFurnace | V5A(V/H)030*D0**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268748 | Ground Water | WaterFurnace | V5A(V/H)030*D3**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268749 | Ground Water | WaterFurnace | V5A(V/H)036*D0**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268750 | Ground Water | WaterFurnace | V5A(V/H)036*D3**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268751 | Ground Water | WaterFurnace | V5A(V/H)036*D0**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268752 | Ground Water | WaterFurnace | V5A(V/H)036*D3**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268753 | Ground Water | WaterFurnace | V5A(V/H)036*D0**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268754 | Ground Water | WaterFurnace | V5A(V/H)036*D3**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268755 | Ground Water | WaterFurnace | V5A(V/H)042*D0**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268756 | Ground Water | WaterFurnace | V5A(V/H)042*D3**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268757 | Ground Water | WaterFurnace | V5A(V/H)042*D0**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268758 | Ground Water | WaterFurnace | V5A(V/H)042*D3**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268759 | Ground Water | WaterFurnace | V5A(V/H)042*D0**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268760 | Ground Water | WaterFurnace | V5A(V/H)042*D3**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268761 | Ground Water | WaterFurnace | V5A(V/H)048*D0**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268762 | Ground Water | WaterFurnace | V5A(V/H)048*D3**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268763 | Ground Water | WaterFurnace | V5A(V/H)048*D0**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268764 | Ground Water | WaterFurnace | V5A(V/H)048*D3**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268765 | Ground Water | WaterFurnace | V5A(V/H)048*D0**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268766 | Ground Water | WaterFurnace | V5A(V/H)048*D3**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268767 | Ground Water | WaterFurnace | V5A(V/H)060*D0**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268768 | Ground Water | WaterFurnace | V5A(V/H)060*D3**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268769 | Ground Water | WaterFurnace | V5A(V/H)060*D0**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268770 | Ground Water | WaterFurnace | V5A(V/H)060*D3**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268771 | Ground Water | WaterFurnace | V5A(V/H)072*D0**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215268772 | Ground Water | WaterFurnace | V5A(V/H)072*D3**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215268773 | Ground Water | WaterFurnace | V5A(V/H)072*D0**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215268774 | Ground Water | WaterFurnace | V5A(V/H)072*D3**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215268775 | Ground Water | WaterFurnace | V5A(V/H)030*D2**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268776 | Ground Water | WaterFurnace | V5A(V/H)030*D4**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268777 | Ground Water | WaterFurnace | V5A(V/H)030*D2**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268778 | Ground Water | WaterFurnace | V5A(V/H)030*D4**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
215268779 | Ground Water | WaterFurnace | V5A(V/H)036*D2**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268780 | Ground Water | WaterFurnace | V5A(V/H)036*D4**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268781 | Ground Water | WaterFurnace | V5A(V/H)036*D2**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268782 | Ground Water | WaterFurnace | V5A(V/H)036*D4**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268783 | Ground Water | WaterFurnace | V5A(V/H)036*D2**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268784 | Ground Water | WaterFurnace | V5A(V/H)036*D4**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
215268785 | Ground Water | WaterFurnace | V5A(V/H)042*D4**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268786 | Ground Water | WaterFurnace | V5A(V/H)042*D2**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268787 | Ground Water | WaterFurnace | V5A(V/H)042*D4**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
215268788 | Ground Water | WaterFurnace | V5A(V/H)042*D4**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
217351731 | Ground Water | CARRIER | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351732 | Ground Water | CARRIER | GZ036SA*C******1 | F(T,G,E)5(A,B)***36*** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351733 | Ground Water | CARRIER | GZ036SA*N******1 | F(T,G,E)5(A,B)***36*** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351734 | Ground Water | CARRIER | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351735 | Ground Water | CARRIER | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351736 | Ground Water | CARRIER | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351738 | Ground Water | CARRIER | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351739 | Ground Water | CARRIER | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351741 | Ground Water | CARRIER | GZ024SA*C******1 | CAAMP2***AMA | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351742 | Ground Water | CARRIER | GZ024SA*N******1 | CAAMP2***AMA | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351743 | Ground Water | CARRIER | GZ036SA*C******1 | CAAMP3***AMA | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351744 | Ground Water | CARRIER | GZ036SA*N******1 | CAAMP3***AMA | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351745 | Ground Water | CARRIER | GZ048SA*C******1 | CAAMP4***AMA | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351746 | Ground Water | CARRIER | GZ048SA*N******1 | CAAMP4***AMA | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351747 | Ground Water | CARRIER | GZ060SA*C******1 | CAAMP6***AMA | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351749 | Ground Water | CARRIER | GZ072SA*C******1 | CAAMP6***AMA | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351750 | Ground Water | CARRIER | GZ072SA*N******1 | CAAMP6***AMA | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351752 | Ground Water | CARRIER | GW024WA********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351754 | Ground Water | CARRIER | GW048WA********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
215310991 | Ground Water | GeoSmart Energy | S7A(V/H)036BV1**2 |  | 38200 | 28.7 | 41900 | 4.7 | 3.1833 | Yes
215310992 | Ground Water | GeoSmart Energy | S7A(V/H)048BV1**2 |  | 49000 | 27.4 | 54500 | 4.2 | 4.0833 | Yes
215310994 | Ground Water | GeoSmart Energy | S7A(V/H)060BV1**2 |  | 60700 | 23.4 | 66000 | 4.3 | 5.0583 | Yes
217351843 | Ground Water | DAY & NIGHT | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351844 | Ground Water | DAY & NIGHT | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351846 | Ground Water | DAY & NIGHT | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351847 | Ground Water | DAY & NIGHT | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351849 | Ground Water | DAY & NIGHT | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351850 | Ground Water | DAY & NIGHT | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351851 | Ground Water | DAY & NIGHT | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351852 | Ground Water | DAY & NIGHT | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351853 | Ground Water | DAY & NIGHT | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351854 | Ground Water | DAY & NIGHT | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351855 | Ground Water | DAY & NIGHT | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351857 | Ground Water | DAY & NIGHT | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351858 | Ground Water | DAY & NIGHT | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351860 | Ground Water | DAY & NIGHT | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351862 | Ground Water | DAY & NIGHT | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351865 | Ground Water | HEIL | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351866 | Ground Water | HEIL | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351867 | Ground Water | HEIL | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351868 | Ground Water | HEIL | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351869 | Ground Water | HEIL | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351870 | Ground Water | HEIL | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351871 | Ground Water | HEIL | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351873 | Ground Water | HEIL | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351874 | Ground Water | HEIL | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351876 | Ground Water | HEIL | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351877 | Ground Water | HEIL | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351878 | Ground Water | HEIL | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351879 | Ground Water | HEIL | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351880 | Ground Water | HEIL | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
215224495 | Ground Water | FHP | CF018-2VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224496 | Ground Water | FHP | CF018-2VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
216801922 | Ground Water | BOSCH | WT025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801923 | Ground Water | BOSCH | WT025-3***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801932 | Ground Water | CARRIER | 50PSW025***3/CB |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801933 | Ground Water | CARRIER | 50PSW025***4/DB |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801934 | Ground Water | CARRIER | 50PSW025***5/EB |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801935 | Ground Water | CARRIER | 50PSW025***6/FB |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801983 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**3*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801984 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**3*(J-R)** |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216801985 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**3*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801986 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**3*(J-R)** |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216801987 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**4*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801988 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**4*(J-R)** |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216801989 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**4*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801990 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**4*(J-R)** |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216801991 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**5*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801992 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**5*(J-R)** |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216801993 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**5*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801994 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**5*(J-R)** |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216801995 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**6*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801996 | Ground Water | CARRIER | 50WT*024(G-K;N-R)**6*(J-R)** |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
216801997 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**6*(A-H)** |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
216801998 | Ground Water | CARRIER | 50WT*024(L/M/S/T)**6*(J-R)** |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
216801999 | Ground Water | CARRIER | 50WT*036***3*(A-H)** |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216802000 | Ground Water | CARRIER | 50WT*036***3*(J-R)** |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216802001 | Ground Water | CARRIER | 50WT*036***4*(A-H)** |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216802002 | Ground Water | CARRIER | 50WT*036***4*(J-R)** |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216802003 | Ground Water | CARRIER | 50WT*036***5*(A-H)** |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216802004 | Ground Water | CARRIER | 50WT*036***5*(J-R)** |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216802005 | Ground Water | CARRIER | 50WT*036***6*(A-H)** |  | 40500 | 24 | 37000 | 5 | 3.375 | No
216802006 | Ground Water | CARRIER | 50WT*036***6*(J-R)** |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | No
216802007 | Ground Water | CARRIER | 50WT*048***3*(A-H)** |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216802008 | Ground Water | CARRIER | 50WT*048***3*(J-R)** |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
216802009 | Ground Water | CARRIER | 50WT*048***5*(A-H)** |  | 53500 | 23 | 48000 | 5 | 4.4583 | No
216802010 | Ground Water | CARRIER | 50WT*048***5*(J-R)** |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
209180331 | Ground Water | HYDROTECH | WSV6036B* |  | 37000 | 22 | 35000 | 4.1 | 3.0833 | Yes
209180332 | Ground Water | HYDROTECH | WSV6042B* |  | 44000 | 24 | 38500 | 4.4 | 3.6667 | Yes
209180334 | Ground Water | HYDROTECH | WSV6048B* |  | 55500 | 23 | 47000 | 4.3 | 4.625 | Yes
212509301 | Ground Water | AE Air | WSH6060AN* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | No
215746915 | Ground Water | TRANE | GSK036A3 |  | 43925 | 29.6 | 39058 | 5.26 | 3.6604 | No
215746916 | Ground Water | TRANE | GSK048A3 |  | 57887 | 27.2 | 51760 | 5.05 | 4.8239 | No
215746918 | Ground Water | TRANE | GSK060A3 |  | 69939 | 26.2 | 62898 | 4.9 | 5.8282 | No
215746919 | Ground Water | TRANE | GSK072A3 |  | 91819 | 27.9 | 75524 | 4.96 | 7.6516 | No
215746920 | Ground Water | TRANE | GSK090A3 |  | 107813 | 26.6 | 91385 | 4.94 | 8.9844 | No
213154446 | Ground Water | GeoSmart Energy | GTS064*1******K | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
213154447 | Ground Water | GeoSmart Energy | GTS038*1******K | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
213154448 | Ground Water | GeoSmart Energy | GTS038*1******K | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
213154451 | Ground Water | GeoSmart Energy | YT048**1*4********C |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | Yes
213154454 | Ground Water | GeoSmart Energy | GTZ026*1******K | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
213154455 | Ground Water | GeoSmart Energy | GTZ026*1******K | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
213154456 | Ground Water | GeoSmart Energy | GTZ038*1******K | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
213154457 | Ground Water | GeoSmart Energy | GTZ038*1******K | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
213154458 | Ground Water | GeoSmart Energy | GTZ049*1******K | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
213154459 | Ground Water | GeoSmart Energy | GTZ049*1******K | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
213154460 | Ground Water | GeoSmart Energy | GTZ064*1******K | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
213154461 | Ground Water | GeoSmart Energy | GTZ064*1******K | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
213154462 | Ground Water | GeoSmart Energy | GTZ072*1******K | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
213154463 | Ground Water | GeoSmart Energy | GTZ072*1******K | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
213154464 | Ground Water | GeoSmart Energy | GS012**1*0********L |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | Yes
213154465 | Ground Water | GeoSmart Energy | GS018**1*1********L |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | Yes
213154466 | Ground Water | GeoSmart Energy | GS022**1*1********L |  | 21900 | 27.5 | 19500 | 5 | 1.825 | Yes
213154467 | Ground Water | GeoSmart Energy | GS030**1*1********L |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | Yes
213154468 | Ground Water | GeoSmart Energy | GS036**1*1********L |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | Yes
213154469 | Ground Water | GeoSmart Energy | GS042**1*1********L |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | Yes
213154470 | Ground Water | GeoSmart Energy | GS048**1*1********L |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | Yes
213154471 | Ground Water | GeoSmart Energy | GS060**1*1********L |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | Yes
213154472 | Ground Water | GeoSmart Energy | GS070**1*1********L |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | Yes
213154473 | Ground Water | GeoSmart Energy | GT026**1*1********L |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
213154474 | Ground Water | GeoSmart Energy | GT038**1*1********L |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
213154475 | Ground Water | GeoSmart Energy | GT049**1*1********L |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
213154476 | Ground Water | GeoSmart Energy | GT064**1*1********L |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
213154477 | Ground Water | GeoSmart Energy | GT072**1*1********L |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
216727177 | Ground Water | CARRIER | GZ024*******1**1 | FE*****36*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
216727179 | Ground Water | CARRIER | GZ036*******1**2 | FE*****48*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
216727183 | Ground Water | BRYANT | GZ024*******1**1 | FE*****36*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
216727185 | Ground Water | BRYANT | GZ036*******1**2 | FE*****48*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
8560948 | Ground Water | TETCO | TVS015*****1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | Yes
8560949 | Ground Water | GEOCOMFORT | GVS015*A***1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | No
8560950 | Ground Water | HYDRON MODULE | HVS015*A***1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | No
8560951 | Ground Water | TETCO | TVS015*A***1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | No
203363138 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**0*1* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363139 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**0*4* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363140 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**2*0* |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
203363141 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**2*1* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363142 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**2*4* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363143 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**3*0* |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
203363144 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**3*1* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363145 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**3*4* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363146 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**4*0* |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
203363147 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**4*1* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363148 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**4*4* |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
203363150 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**0*1* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363151 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**0*4* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363153 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**3*1* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363154 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**3*4* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363156 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**4*1* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363157 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH042**4*4* |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
203363170 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**0*1* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363171 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**0*4* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363173 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**3*1* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363174 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**3*4* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363176 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**4*1* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363177 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH060**4*4* |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
203363180 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**0*1* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203363181 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**0*4* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203363183 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**3*1* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203363184 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**3*4* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203363186 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**4*1* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
203363187 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH070**4*4* |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
211594118 | Ground Water | TRANE | GEHG006A |  | 8100 | 21.3 | 7500 | 4.1 | 0.675 | No
211594119 | Ground Water | TRANE | GEHG009A |  | 9600 | 23.8 | 9100 | 4.7 | 0.8 | No
211594120 | Ground Water | TRANE | GEHG012A |  | 13300 | 24.2 | 12400 | 4.6 | 1.1083 | No
211594121 | Ground Water | TRANE | GEHG015A |  | 16600 | 23 | 15400 | 4.3 | 1.3833 | No
211594122 | Ground Water | TRANE | GEHG018A |  | 19300 | 23.5 | 18400 | 4.4 | 1.6083 | No
216772574 | Ground Water | Enertech | EYT024* |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
216772575 | Ground Water | Enertech | EYT036* |  | 42300 | 27.9 | 35500 | 5.4 | 3.525 | Yes
216772576 | Ground Water | Enertech | EYT048* |  | 55200 | 24.9 | 46500 | 5 | 4.6 | Yes
216772579 | Ground Water | Enertech | EZT024* |  | 28200 | 25 | 23175 | 4.68 | 2.35 | Yes
216772580 | Ground Water | Enertech | EZT030* |  | 34550 | 23.2 | 30075 | 4.5 | 2.8792 | Yes
216772581 | Ground Water | Enertech | EZT036* |  | 39400 | 25.2 | 34775 | 4.6 | 3.2833 | Yes
216772582 | Ground Water | Enertech | EZT042* |  | 47250 | 24.6 | 40300 | 4.4 | 3.9375 | Yes
216772583 | Ground Water | Enertech | EZT048* |  | 52200 | 22.1 | 45900 | 4.4 | 4.35 | Yes
216772584 | Ground Water | Enertech | EZT060* |  | 62000 | 21.8 | 58500 | 4.25 | 5.1667 | Yes
216772585 | Ground Water | Enertech | EVS006* |  | 7625 | 25.9 | 6500 | 4.49 | 0.63542 | Yes
216772586 | Ground Water | Enertech | EVS015* |  | 18150 | 35.1 | 14400 | 5.4 | 1.5125 | Yes
216772587 | Ground Water | Enertech | EZS006* |  | 6900 | 22.9 | 6300 | 4.3 | 0.575 | Yes
216772588 | Ground Water | Enertech | EBT060* | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | Yes
216772590 | Ground Water | Enertech | EVT060* |  | 64200 | 22 | 58550 | 4.49 | 5.35 | Yes
216772591 | Ground Water | Enertech | EYT060* |  | 66900 | 23.8 | 60700 | 4.8 | 5.575 | Yes
216772592 | Ground Water | Enertech | EZS015* |  | 16000 | 26.3 | 14300 | 4.8 | 1.3333 | Yes
216772593 | Ground Water | Enertech | EZS017* |  | 18475 | 22.2 | 15950 | 4.38 | 1.5396 | Yes
216772594 | Ground Water | Enertech | EZS018* |  | 21500 | 30.1 | 17500 | 4.7 | 1.7917 | Yes
216772596 | Ground Water | Enertech | EYT072* |  | 75400 | 21.7 | 70400 | 4.5 | 6.2833 | Yes
216772598 | Ground Water | Enertech | EWS036* |  | 35600 | 22.9 | 38300 | 4.1 | 2.9667 | Yes
216772599 | Ground Water | Enertech | EWS048* |  | 52500 | 22.9 | 58700 | 4.2 | 4.375 | Yes
216772602 | Ground Water | Enertech | EWT048* |  | 52700 | 21.2 | 61100 | 4.2 | 4.3917 | Yes
216801023 | Ground Water | CARRIER | 50PEC09****3/CG |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216801024 | Ground Water | CARRIER | 50PEC09****4/DG |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216801031 | Ground Water | FHP | CA009-1***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216801032 | Ground Water | FHP | CA009-2***-******E |  | 9500 | 22.35 | 8150 | 4.45 | 0.79167 | No
216801911 | Ground Water | BOSCH | WT025-2***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801912 | Ground Water | BOSCH | WT025-4***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
216801918 | Ground Water | BOSCH-GEO | TW025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
216801920 | Ground Water | BOSCH-GEO | TW049-1***-*****C |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
202449795 | Ground Water | WaterFurnace | UBV/UBH042**0*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449796 | Ground Water | WaterFurnace | UBV/UBH042**3*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449797 | Ground Water | WaterFurnace | UBV/UBH042**4*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449798 | Ground Water | WaterFurnace | UBV/UBH042**0*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449799 | Ground Water | WaterFurnace | UBV/UBH042**3*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449800 | Ground Water | WaterFurnace | UBV/UBH042**4*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
202449816 | Ground Water | WaterFurnace | UBV/UBH060**0*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449817 | Ground Water | WaterFurnace | UBV/UBH060**3*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
214772106 | Ground Water | TRANE | GEHK0244 |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772107 | Ground Water | TRANE | GEHK0247 |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772108 | Ground Water | TRANE | GEHK030B |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772109 | Ground Water | TRANE | GEHK0304 |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772110 | Ground Water | TRANE | GEHK0307 |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772111 | Ground Water | TRANE | GEHK036B |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772112 | Ground Water | TRANE | GEHK0364 |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772113 | Ground Water | TRANE | GEHK0367 |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214772114 | Ground Water | TRANE | GEHK042B |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214772115 | Ground Water | TRANE | GEHK0424 |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214772116 | Ground Water | TRANE | GEHK048B |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214772117 | Ground Water | TRANE | GEHK0484 |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214772118 | Ground Water | TRANE | GEHK060B |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214772119 | Ground Water | TRANE | GEHK0604 |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214772120 | Ground Water | TRANE | EXHK0097 |  | 9600 | 29.7 | 8500 | 5.16 | 0.8 | No
214772121 | Ground Water | TRANE | EXHK0127 |  | 12500 | 26.1 | 11500 | 4.98 | 1.0417 | No
214772122 | Ground Water | TRANE | EXHK0157 |  | 17100 | 24.6 | 15600 | 4.6 | 1.425 | No
214772123 | Ground Water | TRANE | EXHK0187 |  | 21100 | 29.6 | 18600 | 4.77 | 1.7583 | No
214772124 | Ground Water | TRANE | EXHK024B |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772125 | Ground Water | TRANE | EXHK0244 |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772126 | Ground Water | TRANE | EXHK0247 |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214772127 | Ground Water | TRANE | EXHK030B |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772128 | Ground Water | TRANE | EXHK0304 |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772129 | Ground Water | TRANE | EXHK0307 |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214772130 | Ground Water | TRANE | EXHK036B |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772131 | Ground Water | TRANE | EXHK0364 |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772132 | Ground Water | TRANE | EXHK0367 |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214772133 | Ground Water | TRANE | EXHK042B |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214772134 | Ground Water | TRANE | EXHK0424 |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214772135 | Ground Water | TRANE | EXHK048B |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214772136 | Ground Water | TRANE | EXHK0484 |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214772137 | Ground Water | TRANE | EXHK060B |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214772138 | Ground Water | TRANE | EXHK0604 |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214772139 | Ground Water | TRANE | EXHK070B |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214772140 | Ground Water | TRANE | EXHK0704 |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214772141 | Ground Water | TRANE | DXHK024A |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772142 | Ground Water | TRANE | DXHK036A |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
202330572 | Ground Water | AAON, Inc. | M2-006-4-H-BCBC-V0-10-000-A |  | 75000 | 22.6 | 54000 | 4.1 | 6.25 | No
202350417 | Ground Water | AAON, Inc. | RN-009-2-0-BCAY-V0-10-000-A |  | 109000 | 25 | 93600 | 5 | 9.0833 | No
202350418 | Ground Water | AAON, Inc. | RN-009-3-0-BCAY-V0-10-000-A |  | 109000 | 25 | 93600 | 5 | 9.0833 | No
202350419 | Ground Water | AAON, Inc. | RN-009-4-0-BCAY-V0-10-000-A |  | 109000 | 25 | 93600 | 5 | 9.0833 | No
202350429 | Ground Water | AAON, Inc. | RN-011-2-0-BCAY-V0-10-000-A |  | 125000 | 21.5 | 117200 | 4.6 | 10.4167 | No
202350430 | Ground Water | AAON, Inc. | RN-011-3-0-BCAY-V0-10-000-A |  | 125000 | 21.5 | 117200 | 4.6 | 10.4167 | No
202350431 | Ground Water | AAON, Inc. | RN-011-4-0-BCAY-V0-10-000-A |  | 125000 | 21.5 | 117200 | 4.6 | 10.4167 | No
202350445 | Ground Water | AAON, Inc. | M2-007-2-H-ACBC-C0-10-000-A |  | 89700 | 22.1 | 65500 | 4.1 | 7.475 | No
202350447 | Ground Water | AAON, Inc. | M2-007-2-H-BCBC-V0-10-000-A |  | 80900 | 21.5 | 68400 | 4.1 | 6.7417 | No
202350449 | Ground Water | AAON, Inc. | M2-007-3-H-ACBC-C0-10-000-A |  | 89700 | 22.1 | 65500 | 4.1 | 7.475 | No
202350451 | Ground Water | AAON, Inc. | M2-007-3-H-BCBC-V0-10-000-A |  | 80900 | 21.5 | 68400 | 4.1 | 6.7417 | No
202350453 | Ground Water | AAON, Inc. | M2-007-4-H-ACBC-C0-10-000-A |  | 89700 | 22.1 | 65500 | 4.1 | 7.475 | No
202350455 | Ground Water | AAON, Inc. | M2-007-4-H-BCBC-V0-10-000-A |  | 80900 | 21.5 | 68400 | 4.1 | 6.7417 | No
215224293 | Ground Water | BOSCH-GEO | RF007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | Yes
215224294 | Ground Water | BOSCH-GEO | RF007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | Yes
215224295 | Ground Water | BOSCH-GEO | RF009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | Yes
215224296 | Ground Water | BOSCH-GEO | RF009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | Yes
215224297 | Ground Water | BOSCH-GEO | RF012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | Yes
215224298 | Ground Water | BOSCH-GEO | RF012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | Yes
215224299 | Ground Water | BOSCH-GEO | RF015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | Yes
215224300 | Ground Water | BOSCH-GEO | RF015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | Yes
215224301 | Ground Water | BOSCH-GEO | RF018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224302 | Ground Water | BOSCH-GEO | RF018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
217902632 | Ground Water | Johnson Controls | BWM060A*B |  | 58700 | 23.4 | 57900 | 4.1 | 4.8917 | No
217902633 | Ground Water | SKYMARK | BWM060A*C |  | 58700 | 23.4 | 57900 | 4.1 | 4.8917 | No
217903418 | Ground Water | WaterFurnace | V5R036*S0**1* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903419 | Ground Water | WaterFurnace | V5R036*S0**4* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903420 | Ground Water | WaterFurnace | V5R036*S0**5* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903421 | Ground Water | WaterFurnace | V5R048*S0**1* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903422 | Ground Water | WaterFurnace | V5R048*S0**4* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903423 | Ground Water | WaterFurnace | V5R048*S0**5* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903424 | Ground Water | WaterFurnace | V5R060*S0**1* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903425 | Ground Water | WaterFurnace | V5R060*S0**4* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903426 | Ground Water | WaterFurnace | V5R060*S0**5* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903427 | Ground Water | WaterFurnace | V5R072*S0**1* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903428 | Ground Water | WaterFurnace | V5R072*S0**4* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903429 | Ground Water | WaterFurnace | V5R072*S0**5* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903430 | Ground Water | WaterFurnace | V5R036*S3**1* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903431 | Ground Water | WaterFurnace | V5R036*S3**4* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903432 | Ground Water | WaterFurnace | V5R036*S3**5* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903433 | Ground Water | WaterFurnace | V5R036*S4**1* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903434 | Ground Water | WaterFurnace | V5R036*S4**4* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903435 | Ground Water | WaterFurnace | V5R036*S4**5* |  | 37400 | 27.8 | 30700 | 4.8 | 3.1167 | No
217903436 | Ground Water | WaterFurnace | V5R048*S3**1* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903437 | Ground Water | WaterFurnace | V5R048*S3**4* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903438 | Ground Water | WaterFurnace | V5R048*S3**5* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903439 | Ground Water | WaterFurnace | V5R048*S4**1* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903440 | Ground Water | WaterFurnace | V5R048*S4**4* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903441 | Ground Water | WaterFurnace | V5R048*S4**5* |  | 51360 | 25 | 46000 | 4.6 | 4.28 | No
217903442 | Ground Water | WaterFurnace | V5R060*S3**1* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903443 | Ground Water | WaterFurnace | V5R060*S3**4* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903444 | Ground Water | WaterFurnace | V5R060*S3**5* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903445 | Ground Water | WaterFurnace | V5R060*S4**1* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903446 | Ground Water | WaterFurnace | V5R060*S4**4* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903447 | Ground Water | WaterFurnace | V5R060*S4**5* |  | 65300 | 24 | 56800 | 4.5 | 5.4417 | No
217903448 | Ground Water | WaterFurnace | V5R072*S3**1* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903449 | Ground Water | WaterFurnace | V5R072*S3**4* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903450 | Ground Water | WaterFurnace | V5R072*S3**5* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903451 | Ground Water | WaterFurnace | V5R072*S4**1* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903452 | Ground Water | WaterFurnace | V5R072*S4**4* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903453 | Ground Water | WaterFurnace | V5R072*S4**5* |  | 73000 | 22.1 | 65300 | 4.2 | 6.0833 | No
217903454 | Ground Water | WaterFurnace | V5R036*D4**1* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903455 | Ground Water | WaterFurnace | V5R036*D4**4* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903456 | Ground Water | WaterFurnace | V5R036*D4**5* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903457 | Ground Water | WaterFurnace | V5R048*D4**1* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903458 | Ground Water | WaterFurnace | V5R048*D4**4* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903459 | Ground Water | WaterFurnace | V5R048*D4**5* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903460 | Ground Water | WaterFurnace | V5R060*D4**1* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
205754919 | Ground Water | Johnson Controls | JSH/V006A B |  | 7400 | 25.5 | 6300 | 4.4 | 0.61667 | No
205754920 | Ground Water | SKYMARK | JSH/V006A C |  | 7400 | 25.5 | 6300 | 4.4 | 0.61667 | No
205754921 | Ground Water | Johnson Controls | JSH/V009A B |  | 11100 | 25.2 | 9400 | 4.3 | 0.925 | No
205754922 | Ground Water | SKYMARK | JSH/V009A C |  | 11100 | 25.2 | 9400 | 4.3 | 0.925 | No
205767467 | Ground Water | ClimateMaster | QEV/H/D1860 |  | 48000 | 35.5 | 60000 | 4.3 | 4 | Yes
205767468 | Ground Water | ClimateMaster | TYV/H024B |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | No
205767470 | Ground Water | ClimateMaster | TYV/H036B |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | No
205767471 | Ground Water | ClimateMaster | TYV/H042 |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | No
205767473 | Ground Water | ClimateMaster | TEV/H/D026B |  | 28500 | 26.4 | 25800 | 5.3 | 2.375 | Yes
205767474 | Ground Water | ClimateMaster | TEV/H/D038B |  | 42100 | 26.1 | 37900 | 5.2 | 3.5083 | Yes
205767475 | Ground Water | ClimateMaster | TEV/H/D049B |  | 55000 | 25.3 | 46800 | 4.6 | 4.5833 | Yes
205767476 | Ground Water | ClimateMaster | TEV/H/D064B |  | 71500 | 24.4 | 63200 | 4.8 | 5.9583 | Yes
207200584 | Ground Water | GeoSmart Energy | GTS072*1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207200585 | Ground Water | GeoSmart Energy | GTZ072*1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207200586 | Ground Water | GeoSmart Energy | GSZ022*1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
207200587 | Ground Water | GeoSmart Energy | GSZ022*1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
207200588 | Ground Water | GeoSmart Energy | GSZ030*1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
207200589 | Ground Water | GeoSmart Energy | GSZ030*1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
207200590 | Ground Water | GeoSmart Energy | GSZ048*1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
207200591 | Ground Water | GeoSmart Energy | GSZ048*1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
207200592 | Ground Water | GeoSmart Energy | GSZ060*1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
207200593 | Ground Water | GeoSmart Energy | GSZ060*1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
207200594 | Ground Water | GeoSmart Energy | GSZ070*1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
207200595 | Ground Water | GeoSmart Energy | GTZ072*1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
207200596 | Ground Water | GeoSmart Energy | GSZ070*1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | Yes
207200597 | Ground Water | GeoSmart Energy | GTS072*1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207200598 | Ground Water | GeoSmart Energy | GSZ036*1*J | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
207200599 | Ground Water | GeoSmart Energy | GSZ042*1*J | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
207200600 | Ground Water | GeoSmart Energy | GTZ038*1*J | SAH038* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207200601 | Ground Water | GeoSmart Energy | GTZ049*1*J | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207200602 | Ground Water | GeoSmart Energy | GTZ049*1*J | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
207200603 | Ground Water | GeoSmart Energy | GTS064*1*J | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207200604 | Ground Water | GeoSmart Energy | GTS064*1*J | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
207200605 | Ground Water | GeoSmart Energy | GSZ036*1*J | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
207200606 | Ground Water | GeoSmart Energy | GSZ042*1*J | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | No
207200607 | Ground Water | GeoSmart Energy | GTZ038*1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207200608 | Ground Water | GeoSmart Energy | GTS038*1*J | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207200609 | Ground Water | GeoSmart Energy | GTS038*1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207200613 | Ground Water | GeoSmart Energy | QT038**1*(1,2)* |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
207200614 | Ground Water | GeoSmart Energy | VI036**1*(1,2)** |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
207200616 | Ground Water | GeoSmart Energy | VI060**1*1* |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
207216511 | Ground Water | GEOSTAR | GDV084**3 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
207216512 | Ground Water | GEOSTAR | GDV084**4 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
207216513 | Ground Water | GEOSTAR | GDV084**5 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
207216514 | Ground Water | GEOSTAR | GDH084**3 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
207216515 | Ground Water | GEOSTAR | GDH084**4 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
207216516 | Ground Water | GEOSTAR | GDH084**5 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
207216517 | Ground Water | GEOSTAR | GDV096**3 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
207216518 | Ground Water | GEOSTAR | GDV096**4 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
207216519 | Ground Water | GEOSTAR | GDV096**5 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
215832285 | Ground Water | HYDROTECH | WSH6030D* |  | 32400 | 24 | 26000 | 4.2 | 2.7 | No
215832286 | Ground Water | HYDROTECH | WSH6036D* |  | 39000 | 23.2 | 35000 | 4.1 | 3.25 | No
215832287 | Ground Water | HYDROTECH | WSH6042D* |  | 45500 | 23.3 | 38000 | 4.3 | 3.7917 | No
215832288 | Ground Water | HYDROTECH | WSH6048D* |  | 52500 | 23.6 | 45500 | 4.2 | 4.375 | No
215832289 | Ground Water | HYDROTECH | WSH6060D* |  | 64000 | 23.5 | 51000 | 4.3 | 5.3333 | No
215832290 | Ground Water | HYDROTECH | WSH6072D* |  | 78000 | 21.8 | 68000 | 4.1 | 6.5 | No
215832291 | Ground Water | AE Air | WSH6009D* |  | 10000 | 23 | 8000 | 4.2 | 0.83333 | No
216714636 | Ground Water | GEOSTAR | G3A(V/H)036*S0**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714637 | Ground Water | GEOSTAR | G3A(V/H)036*S0**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714638 | Ground Water | GEOSTAR | G3A(V/H)036*S2**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714639 | Ground Water | GEOSTAR | G3A(V/H)036*S2**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714640 | Ground Water | GEOSTAR | G3A(V/H)036*S3**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714641 | Ground Water | GEOSTAR | G3A(V/H)036*S3**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714642 | Ground Water | GEOSTAR | G3A(V/H)036*S4**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714643 | Ground Water | GEOSTAR | G3A(V/H)036*S4**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
216714644 | Ground Water | GEOSTAR | G3A(V/H)042*S0**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714645 | Ground Water | GEOSTAR | G3A(V/H)042*S0**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714646 | Ground Water | GEOSTAR | G3A(V/H)042*S3**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714647 | Ground Water | GEOSTAR | G3A(V/H)042*S3**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714648 | Ground Water | GEOSTAR | G3A(V/H)042*S4**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714649 | Ground Water | GEOSTAR | G3A(V/H)042*S4**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
216714656 | Ground Water | GEOSTAR | G3A(V/H)060*S0**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216714657 | Ground Water | GEOSTAR | G3A(V/H)060*S0**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216714658 | Ground Water | GEOSTAR | G3A(V/H)060*S3**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216714659 | Ground Water | GEOSTAR | G3A(V/H)060*S3**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216714660 | Ground Water | GEOSTAR | G3A(V/H)060*S4**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216714661 | Ground Water | GEOSTAR | G3A(V/H)060*S4**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
216569713 | Ground Water | GeoCool | GCHPV/H/D024BT**A*** |  | 28500 | 27.4 | 24500 | 4.8 | 2.375 | No
216569714 | Ground Water | GeoCool | GCHPV/H/D036BT**A*** |  | 41500 | 27.2 | 36600 | 4.9 | 3.4583 | No
216569715 | Ground Water | GeoCool | GCHPV/H/D048BT**A*** |  | 54800 | 26 | 48200 | 4.9 | 4.5667 | No
216569813 | Ground Water | GeoCool | GCHPV/H/D060BT**A*** |  | 69500 | 24 | 61600 | 4.9 | 5.7917 | No
202147039 | Ground Water | GEOCOMFORT | GZS048*4 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147040 | Ground Water | GEOCOMFORT | GZS048*****1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | Yes
202147041 | Ground Water | GEOCOMFORT | GZS048*2***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147042 | Ground Water | GEOCOMFORT | GZS048*3***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147043 | Ground Water | HYDRON MODULE | HZS048 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | Yes
202147044 | Ground Water | HYDRON MODULE | HZS048*2 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147045 | Ground Water | HYDRON MODULE | HZS048*3 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147046 | Ground Water | HYDRON MODULE | HZS048*4 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147047 | Ground Water | HYDRON MODULE | HZS048*****1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | Yes
202147048 | Ground Water | HYDRON MODULE | HZS048*2***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147049 | Ground Water | HYDRON MODULE | HZS048*3***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147050 | Ground Water | TETCO | TZS048 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | Yes
202147051 | Ground Water | TETCO | TZS048*2 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147052 | Ground Water | TETCO | TZS048*3 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147053 | Ground Water | TETCO | TZS048*4 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147054 | Ground Water | TETCO | TZS048*****1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | Yes
202147055 | Ground Water | TETCO | TZS048*2***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147056 | Ground Water | TETCO | TZS048*3***1 |  | 52900 | 22.6 | 45600 | 4.3 | 4.4083 | No
202147061 | Ground Water | GEOCOMFORT | GZS060*****1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | Yes
202147062 | Ground Water | GEOCOMFORT | GZS060*2***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202147067 | Ground Water | HYDRON MODULE | HZS060*****1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | Yes
202147068 | Ground Water | HYDRON MODULE | HZS060*2***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
9105364 | Ground Water | GEOCOMFORT | GVS006 |  | 7800 | 25.8 | 7000 | 4.6 | 0.65 | Yes
9105366 | Ground Water | HYDRON MODULE | HVS006 |  | 7800 | 25.8 | 7000 | 4.6 | 0.65 | Yes
9105367 | Ground Water | TETCO | TVS006 |  | 7800 | 25.8 | 7000 | 4.6 | 0.65 | Yes
9105368 | Ground Water | GEOCOMFORT | GVS006*A |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9105369 | Ground Water | HYDRON MODULE | HVS006*A |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9105370 | Ground Water | TETCO | TVS006*A |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9105371 | Ground Water | GEOCOMFORT | GVS006*9 |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9105372 | Ground Water | HYDRON MODULE | HVS006*9 |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9105373 | Ground Water | TETCO | TVS006*9 |  | 7900 | 24 | 7100 | 4.5 | 0.65833 | No
9111997 | Ground Water | BOSCH | SM024-1VT/CF*-*****B |  | 29400 | 24.85 | 24700 | 4.9 | 2.45 | No
9111998 | Ground Water | BOSCH | SM036-1VT/CF*-*****B |  | 44300 | 27.1 | 36700 | 5.4 | 3.6917 | No
9113111 | Ground Water | BOSCH | SM048-1VT/CF*-*****B* |  | 56900 | 24.3 | 49200 | 4.9 | 4.7417 | No
9113180 | Ground Water | BOSCH | SM060-1VT/CF*-*****B |  | 71600 | 24 | 62400 | 4.7 | 5.9667 | No
9113181 | Ground Water | BOSCH | SM070-1VT/CF*-*****B |  | 78900 | 22.1 | 72600 | 4.4 | 6.575 | No
9113182 | Ground Water | BOSCH | SM024-1VT/CF*-*****B |  | 29400 | 24.85 | 24700 | 4.9 | 2.45 | Yes
9113183 | Ground Water | BOSCH | SM036-1VT/CF*-*****B |  | 44300 | 27.1 | 36700 | 5.4 | 3.6917 | Yes
9113184 | Ground Water | BOSCH | SM048-1VT/CF*-*****B* |  | 56900 | 24.3 | 49200 | 4.9 | 4.7417 | Yes
9113185 | Ground Water | BOSCH | SM060-1VT/CF*-*****B |  | 71600 | 24 | 62400 | 4.7 | 5.9667 | Yes
9113186 | Ground Water | BOSCH | SM070-1VT/CF*-*****B |  | 78900 | 22.1 | 72600 | 4.4 | 6.575 | Yes
207178495 | Ground Water | GEOSTAR | 163J049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207178496 | Ground Water | GEOSTAR | 163J049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207178497 | Ground Water | GEOSTAR | 163J064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207178498 | Ground Water | GEOSTAR | 163J064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207178499 | Ground Water | GEOSTAR | 164J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207178500 | Ground Water | GEOSTAR | 163J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
207178519 | Ground Water | GEOSTAR | 164H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207178520 | Ground Water | GEOSTAR | 164H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207178521 | Ground Water | GEOSTAR | 164H064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207178522 | Ground Water | GEOSTAR | 164H064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207178523 | Ground Water | GEOSTAR | 164H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207178524 | Ground Water | GEOSTAR | 164H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207178525 | Ground Water | GEOSTAR | 161/162J064**1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207178536 | Ground Water | GEOSTAR | 163H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207178537 | Ground Water | GEOSTAR | 163H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
216759832 | Ground Water | GEOSTAR | G5SZ036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216759833 | Ground Water | GEOSTAR | G5SZ048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216759834 | Ground Water | GEOSTAR | G5SZ060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216759835 | Ground Water | GEOSTAR | G5SZ066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216767321 | Ground Water | TETCO | TVT024* |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
216767322 | Ground Water | TETCO | TVT030* |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
216767323 | Ground Water | TETCO | TVT036* |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
216767324 | Ground Water | TETCO | TVT042* |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
216767325 | Ground Water | TETCO | TVT048* |  | 53600 | 24.5 | 48500 | 4.9 | 4.4667 | Yes
216767326 | Ground Water | TETCO | TYT024* |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
216767327 | Ground Water | TETCO | TYT036* |  | 42300 | 27.9 | 35500 | 5.4 | 3.525 | Yes
216767328 | Ground Water | TETCO | TYT048* |  | 55200 | 24.9 | 46500 | 5 | 4.6 | Yes
216767329 | Ground Water | TETCO | TVT060* |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
216767330 | Ground Water | TETCO | TYT060* |  | 66900 | 23.8 | 60700 | 4.8 | 5.575 | Yes
207337518 | Ground Water | GEOSTAR | 103H048**1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
207337521 | Ground Water | GEOSTAR | 103H070**1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
207337522 | Ground Water | GEOSTAR | 103H070**1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
207338127 | Ground Water | GEOSTAR | 141/142C036**1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
207338129 | Ground Water | GEOSTAR | 141/142C060**1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | No
207338249 | Ground Water | TRANE | GETE0241-5 |  | 25100 | 22.1 | 22400 | 4.2 | 2.0917 | No
207338250 | Ground Water | TRANE | GETE0242-5 |  | 25100 | 22.1 | 22400 | 4.2 | 2.0917 | No
207338251 | Ground Water | TRANE | GETE0247-5 |  | 25100 | 22.1 | 22400 | 4.2 | 2.0917 | No
207348654 | Ground Water | WaterFurnace | URS036*0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348655 | Ground Water | WaterFurnace | URS036*0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348656 | Ground Water | WaterFurnace | URS036*0*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348657 | Ground Water | WaterFurnace | URS036*3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348658 | Ground Water | WaterFurnace | URS036*3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348659 | Ground Water | WaterFurnace | URS036*3*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348660 | Ground Water | WaterFurnace | URS036*4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348661 | Ground Water | WaterFurnace | URS036*4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348662 | Ground Water | WaterFurnace | URS036*4*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
207348663 | Ground Water | WaterFurnace | URS048*0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348664 | Ground Water | WaterFurnace | URS048*0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348665 | Ground Water | WaterFurnace | URS048*0*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348666 | Ground Water | WaterFurnace | URS048*3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348667 | Ground Water | WaterFurnace | URS048*3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348668 | Ground Water | WaterFurnace | URS048*3*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348669 | Ground Water | WaterFurnace | URS048*4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348670 | Ground Water | WaterFurnace | URS048*4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348671 | Ground Water | WaterFurnace | URS048*4*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207348672 | Ground Water | WaterFurnace | URS070*0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348673 | Ground Water | WaterFurnace | URS070*0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348674 | Ground Water | WaterFurnace | URS070*0*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348675 | Ground Water | WaterFurnace | URS070*3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348676 | Ground Water | WaterFurnace | URS070*3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348677 | Ground Water | WaterFurnace | URS070*3*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348678 | Ground Water | WaterFurnace | URS070*4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201907620 | Ground Water | WaterFurnace | URS048*0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907621 | Ground Water | WaterFurnace | URS048*0*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907622 | Ground Water | WaterFurnace | URS048*3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907623 | Ground Water | WaterFurnace | URS048*3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907624 | Ground Water | WaterFurnace | URS048*3*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907625 | Ground Water | WaterFurnace | URS048*4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907626 | Ground Water | WaterFurnace | URS048*4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907627 | Ground Water | WaterFurnace | URS048*4*5 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
201907628 | Ground Water | WaterFurnace | URD038*4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
201907629 | Ground Water | WaterFurnace | URD038*4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
201907630 | Ground Water | WaterFurnace | URD038*4*5 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
201907631 | Ground Water | WaterFurnace | URD049*4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
201907632 | Ground Water | WaterFurnace | URD049*4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
201907633 | Ground Water | WaterFurnace | URD049*4*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
201926691 | Ground Water | WaterFurnace | URS060*0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926694 | Ground Water | WaterFurnace | URS060*0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926696 | Ground Water | WaterFurnace | URS060*0*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926699 | Ground Water | WaterFurnace | URS060*3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926702 | Ground Water | WaterFurnace | URS060*3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926705 | Ground Water | WaterFurnace | URS060*3*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926708 | Ground Water | WaterFurnace | URS060*4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926711 | Ground Water | WaterFurnace | URS060*4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926714 | Ground Water | WaterFurnace | URS060*4*5 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
201926717 | Ground Water | WaterFurnace | URS070*0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926719 | Ground Water | WaterFurnace | URS070*0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926724 | Ground Water | WaterFurnace | URS070*0*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926727 | Ground Water | WaterFurnace | URS070*3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926730 | Ground Water | WaterFurnace | URS070*3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926733 | Ground Water | WaterFurnace | URS070*3*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926736 | Ground Water | WaterFurnace | URS070*4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
206194160 | Ground Water | Johnson Controls | JCH/V006A*W/K B |  | 7000 | 24 | 6300 | 4.2 | 0.58333 | No
206194161 | Ground Water | SKYMARK | JCH/V006A*W/K C |  | 7000 | 24 | 6300 | 4.2 | 0.58333 | No
206194171 | Ground Water | Johnson Controls | JSH/V/D030C*K B |  | 30800 | 26.7 | 28000 | 4.9 | 2.5667 | Yes
206194172 | Ground Water | SKYMARK | JSH/V/D030C*K C |  | 30800 | 26.7 | 28000 | 4.9 | 2.5667 | Yes
206194173 | Ground Water | Johnson Controls | JSH/V/D048C*K B |  | 53700 | 23.9 | 45700 | 4.4 | 4.475 | No
206194174 | Ground Water | SKYMARK | JSH/V/D048C*K C |  | 53700 | 23.9 | 45700 | 4.4 | 4.475 | No
206194175 | Ground Water | Johnson Controls | JSH/V/D060C*K B |  | 68900 | 24.9 | 58200 | 4.6 | 5.7417 | No
206194176 | Ground Water | SKYMARK | JSH/V/D060C*K C |  | 68900 | 24.9 | 58200 | 4.6 | 5.7417 | No
206194177 | Ground Water | Johnson Controls | JSH/V/D070C*K B |  | 78100 | 23 | 65200 | 4.1 | 6.5083 | No
206194178 | Ground Water | SKYMARK | JSH/V/D070C*K C |  | 78100 | 23 | 65200 | 4.1 | 6.5083 | No
202833355 | Ground Water | BOSCH | EC096-1VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833356 | Ground Water | BOSCH | EC096-3VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833357 | Ground Water | BOSCH | EC096-4VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833829 | Ground Water | CARRIER | 50H/VQP096**N3B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202833831 | Ground Water | CARRIER | 50H/VQP096**C3B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833833 | Ground Water | FHP | EC096-1VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833835 | Ground Water | CARRIER | 50H/VQP096**N5B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202833836 | Ground Water | CARRIER | 50H/VQP096**N6B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202833839 | Ground Water | CARRIER | 50H/VQP096**C5B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833840 | Ground Water | CARRIER | 50H/VQP096**C6B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833843 | Ground Water | FHP | EC096-3VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202833844 | Ground Water | FHP | EC096-4VT/HZC-*****B |  | 107800 | 22 | 96300 | 4.35 | 8.9833 | No
202835053 | Ground Water | BOSCH | SM036-1HZ*-*****C |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | Yes
202835056 | Ground Water | BOSCH | SM024-1VT*-*****C |  | 29400 | 24.85 | 24700 | 4.9 | 2.45 | Yes
202835057 | Ground Water | BOSCH | SM060-1VT*-*****C |  | 71600 | 24 | 62400 | 4.7 | 5.9667 | Yes
202836307 | Ground Water | BOSCH | SM036-1VT*-*****C |  | 44300 | 27.1 | 36700 | 5.4 | 3.6917 | Yes
202836309 | Ground Water | BOSCH | SM048-1VT*-*****C |  | 56900 | 24.3 | 49200 | 4.9 | 4.7417 | Yes
7411100 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7411231 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7411301 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
7411380 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7411778 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7411875 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
7411949 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7412057 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7412158 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
7412253 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7412381 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
7412626 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**0*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7412712 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**0*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7412777 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**2*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7412856 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**2*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7412926 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**3*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7413034 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**3*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7413487 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**4*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7414142 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
7414232 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7414335 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7414470 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
7414553 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7414651 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7414828 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
7414896 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7415098 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7415209 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
7415301 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7415373 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
7415455 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
216979875 | Ground Water | KEEPRITE | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979876 | Ground Water | TEMPSTAR | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979877 | Ground Water | COMFORTMAKER | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979878 | Ground Water | DAY & NIGHT | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979879 | Ground Water | HEIL | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979880 | Ground Water | ARCOAIRE | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979881 | Ground Water | KEEPRITE | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979882 | Ground Water | TEMPSTAR | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979883 | Ground Water | COMFORTMAKER | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979884 | Ground Water | DAY & NIGHT | HCR48V/H**N******1 |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
216979885 | Ground Water | HEIL | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
216979886 | Ground Water | ARCOAIRE | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979887 | Ground Water | KEEPRITE | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979888 | Ground Water | TEMPSTAR | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979889 | Ground Water | COMFORTMAKER | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979890 | Ground Water | DAY & NIGHT | HCR60V/H**C******1 |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
216979891 | Ground Water | HEIL | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979892 | Ground Water | ARCOAIRE | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979893 | Ground Water | KEEPRITE | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979894 | Ground Water | TEMPSTAR | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979895 | Ground Water | COMFORTMAKER | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
216979896 | Ground Water | DAY & NIGHT | HCR60V/H**N******1 |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
217014524 | Ground Water | CARRIER | GCA72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014525 | Ground Water | BRYANT | GCA72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014526 | Ground Water | CARRIER | GCA72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014527 | Ground Water | BRYANT | GCA72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014528 | Ground Water | CARRIER | GCA72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014529 | Ground Water | BRYANT | GCA72H**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014530 | Ground Water | CARRIER | GCA72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014531 | Ground Water | BRYANT | GCA72H**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014532 | Ground Water | HEIL | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014533 | Ground Water | ARCOAIRE | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014534 | Ground Water | KEEPRITE | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014535 | Ground Water | TEMPSTAR | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
202541572 | Ground Water | BOSCH-GEO | BP048-1VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
202541573 | Ground Water | BOSCH | BP048-1VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202541574 | Ground Water | CARRIER | GB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
202541575 | Ground Water | BRYANT | GB048V******1**1 |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | Yes
202543170 | Ground Water | CARRIER | GB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
202543171 | Ground Water | BRYANT | GB018V******1**2 |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202547425 | Ground Water | BOSCH | EC096-1VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202547426 | Ground Water | BOSCH | EC096-3VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202547427 | Ground Water | BOSCH | EC096-4VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
216625646 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D2**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625647 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D2**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
3628355 | Ground Water | WaterFurnace | USV/USH070**0*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
3628356 | Ground Water | WaterFurnace | USV/USH070**3*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
3628357 | Ground Water | WaterFurnace | USV/USH070**4*1 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
3628359 | Ground Water | WaterFurnace | USV/USH060**0*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
3628360 | Ground Water | WaterFurnace | USV/USH060**3*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
3628361 | Ground Water | WaterFurnace | USV/USH060**4*1 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
3628363 | Ground Water | WaterFurnace | USV/USH048**0*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3628364 | Ground Water | WaterFurnace | USV/USH048**3*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3628365 | Ground Water | WaterFurnace | USV/USH048**4*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3628367 | Ground Water | WaterFurnace | USV/USH042**0*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3628368 | Ground Water | WaterFurnace | USV/USH042**3*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3628369 | Ground Water | WaterFurnace | USV/USH042**4*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3628403 | Ground Water | WaterFurnace | USV/USH030**0*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3628404 | Ground Water | WaterFurnace | USV/USH030**2*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3628405 | Ground Water | WaterFurnace | USV/USH030**3*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3628406 | Ground Water | WaterFurnace | USV/USH030**4*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
215223348 | Ground Water | WaterFurnace | V3C(C/W/S)015**0**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
215223349 | Ground Water | WaterFurnace | V3C(C/W/S)015**2**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
215223354 | Ground Water | WaterFurnace | V5C(C/W/S)015**2**1 |  | 15500 | 22 | 14000 | 4.1 | 1.2917 | No
205311951 | Ground Water | GEOSTAR | ZBV/ZBH009**0*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
205311952 | Ground Water | GEOSTAR | ZBV/ZBH009**9*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
205311983 | Ground Water | GEOSTAR | ZBV/ZBH030**0*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311984 | Ground Water | GEOSTAR | ZBV/ZBH030**2*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311985 | Ground Water | GEOSTAR | ZBV/ZBH030**3*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311986 | Ground Water | GEOSTAR | ZBV/ZBH030**4*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311987 | Ground Water | GEOSTAR | ZBV/ZBH030**0*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311988 | Ground Water | GEOSTAR | ZBV/ZBH030**2*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311989 | Ground Water | GEOSTAR | ZBV/ZBH030**3*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311990 | Ground Water | GEOSTAR | ZBV/ZBH030**4*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
205311991 | Ground Water | GEOSTAR | ZBV/ZBH036**0*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
205311992 | Ground Water | GEOSTAR | ZBV/ZBH036**2*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
205311993 | Ground Water | GEOSTAR | ZBV/ZBH036**3*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
205311994 | Ground Water | GEOSTAR | ZBV/ZBH036**4*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
205311995 | Ground Water | GEOSTAR | ZBV/ZBH036**0*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205311996 | Ground Water | GEOSTAR | ZBV/ZBH036**2*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205311997 | Ground Water | GEOSTAR | ZBV/ZBH036**3*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205311998 | Ground Water | GEOSTAR | ZBV/ZBH036**4*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205311999 | Ground Water | GEOSTAR | ZBV/ZBH036**0*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205312000 | Ground Water | GEOSTAR | ZBV/ZBH036**2*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205312001 | Ground Water | GEOSTAR | ZBV/ZBH036**3*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
205312002 | Ground Water | GEOSTAR | ZBV/ZBH036**4*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
10271778 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ026H1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10271926 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ072H1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10271930 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ026H1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
10271959 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ022H1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
10271961 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ022H1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
10271981 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ030H1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
10271985 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ030H1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
10272006 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ048H1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
10272008 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ048H1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
10272012 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ060H1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
10272014 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ060H1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
10272021 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ070H1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
10272215 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS026H1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10272216 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS026H1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10272219 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS049H1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10272220 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS049H1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10272221 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS064H1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10272222 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS064H1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10272228 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS072H1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10298936 | Ground Water | WaterFurnace | UVV/UVH036**0*1 |  | 43000 | 28 | 37000 | 4.4 | 3.5833 | No
10298937 | Ground Water | WaterFurnace | UVV/UVH036**3*1 |  | 43000 | 28 | 37000 | 4.4 | 3.5833 | No
10298938 | Ground Water | WaterFurnace | UVV/UVH036**4*1 |  | 43000 | 28 | 37000 | 4.4 | 3.5833 | No
205973781 | Ground Water | COMFORT-AIRE | HZS048B | MWG48**-B | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
205973782 | Ground Water | CENTURY | HZS048B | MWG48**-B | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
205996637 | Ground Water | Johnson Controls | JCH/V024A*W/K B |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
205996638 | Ground Water | SKYMARK | JCH/V024A*W/K C |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
205996643 | Ground Water | Johnson Controls | JEV/H/D026B B |  | 28500 | 26.4 | 25800 | 5.3 | 2.375 | No
205996644 | Ground Water | Johnson Controls | JEV/H/D038B B |  | 42100 | 26.1 | 37900 | 5.2 | 3.5083 | No
205996645 | Ground Water | Johnson Controls | JEV/H/D049B B |  | 55000 | 25.3 | 46800 | 4.6 | 4.5833 | No
205996646 | Ground Water | Johnson Controls | JEV/H/D064B B |  | 71500 | 24.4 | 63200 | 4.8 | 5.9583 | No
205996647 | Ground Water | Johnson Controls | JEV/H/D072B B |  | 77700 | 22.5 | 71400 | 4.4 | 6.475 | No
214776168 | Ground Water | TRANE | GETK0121-5 |  | 13500 | 26.2 | 10500 | 4.21 | 1.125 | No
214776169 | Ground Water | TRANE | GETK0151-5 |  | 16500 | 21.8 | 16400 | 4.79 | 1.375 | No
214776170 | Ground Water | TRANE | GETK0181-5 |  | 19400 | 21.6 | 19000 | 4.47 | 1.6167 | No
214776171 | Ground Water | TRANE | GETK0241-5 |  | 26300 | 24 | 24700 | 4.56 | 2.1917 | No
214776172 | Ground Water | TRANE | GETK0361-5 |  | 41700 | 22.6 | 37200 | 4.26 | 3.475 | No
214776173 | Ground Water | TRANE | GETK0092 |  | 9500 | 23.6 | 8600 | 4.13 | 0.79167 | No
214776174 | Ground Water | TRANE | GETK0097 |  | 9500 | 23.6 | 8600 | 4.13 | 0.79167 | No
214776185 | Ground Water | TRANE | GETK0092-5 |  | 9700 | 27 | 8400 | 4.44 | 0.80833 | No
214776186 | Ground Water | TRANE | GETK0097-5 |  | 9700 | 27 | 8400 | 4.44 | 0.80833 | No
214776187 | Ground Water | TRANE | GETK0122-5 |  | 13500 | 26.2 | 10500 | 4.21 | 1.125 | No
214776188 | Ground Water | TRANE | GETK0127-5 |  | 13500 | 26.2 | 10500 | 4.21 | 1.125 | No
214776189 | Ground Water | TRANE | GETK0152-5 |  | 16500 | 21.8 | 16400 | 4.79 | 1.375 | No
214776190 | Ground Water | TRANE | GETK0157-5 |  | 16500 | 21.8 | 16400 | 4.79 | 1.375 | No
214776191 | Ground Water | TRANE | GETK0182-5 |  | 19400 | 21.6 | 19000 | 4.47 | 1.6167 | No
206438913 | Ground Water | CARRIER | 50PSH012**N0/BA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438914 | Ground Water | CARRIER | 50PSH012**N4/DA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206570649 | Ground Water | 7 SERIES | NVV/NVH036C1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
206570651 | Ground Water | 7 SERIES | NVV/NVH060C1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
206570652 | Ground Water | GEOSTAR | 141/142C036**1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
214839496 | Ground Water | CARRIER | 50WC*042(G-K;N-R)**3*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839497 | Ground Water | CARRIER | 50WC*042(L/M/S/T)**3*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839498 | Ground Water | CARRIER | 50WC*042(G-K;N-R)**5*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839499 | Ground Water | CARRIER | 50WC*042(L/M/S/T)**5*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839500 | Ground Water | CARRIER | 50WC*042(G-K;N-R)**6*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839501 | Ground Water | CARRIER | 50WC*042(L/M/S/T)**6*(A-H)** |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
215268669 | Ground Water | WaterFurnace | V5A(V/H)036*S0**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268670 | Ground Water | WaterFurnace | V5A(V/H)042*S0**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
215268671 | Ground Water | WaterFurnace | V5A(V/H)048*S0**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
215268672 | Ground Water | WaterFurnace | V5A(V/H)060*S0**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
215268673 | Ground Water | WaterFurnace | V5A(V/H)072*S0**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268674 | Ground Water | WaterFurnace | V5A(V/H)009*R2**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
215268675 | Ground Water | WaterFurnace | V5A(V/H)012*R2**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
215268676 | Ground Water | WaterFurnace | V5A(V/H)015*R2**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
217351073 | Ground Water | BOSCH | CP036-1CSC-*****A | BIVA-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | No
217351074 | Ground Water | BOSCH | CP036-1CSN-*****A | BIVA-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | No
217351075 | Ground Water | BOSCH | CP048-1CSC-*****A | BIVA-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | No
217351076 | Ground Water | BOSCH | CP048-1CSN-*****A | BIVA-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | No
217351077 | Ground Water | BOSCH | CP060-1CSC-*****A | BIVA-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | No
217351078 | Ground Water | BOSCH | CP060-1CSN-*****A | BIVA-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | No
217351079 | Ground Water | BOSCH | CP024-1CSC-*****A | BMAC2430BBTA | 27400 | 23.2 | 23800 | 5 | 2.2833 | No
217351080 | Ground Water | BOSCH | CP024-1CSN-*****A | BMAC2430BBTA | 27600 | 24.3 | 23800 | 5.1 | 2.3 | No
217351081 | Ground Water | BOSCH | CP036-1CSC-*****A | BMAC3036BBTA | 39600 | 21.5 | 37800 | 4.8 | 3.3 | No
217351082 | Ground Water | BOSCH | CP036-1CSN-*****A | BMAC3036BBTA | 40200 | 22.2 | 38800 | 5 | 3.35 | No
217351083 | Ground Water | BOSCH | CP048-1CSC-*****A | BMAC4248CBTA | 52000 | 21.6 | 45400 | 4.5 | 4.3333 | No
217351084 | Ground Water | BOSCH | CP048-1CSN-*****A | BMAC4248CBTA | 53400 | 22.5 | 46600 | 4.7 | 4.45 | No
217351086 | Ground Water | BOSCH | CP060-1CSN-*****A | BMAC4860CBTA | 63200 | 21.1 | 59400 | 4.5 | 5.2667 | No
217351087 | Ground Water | BOSCH-GEO | RP024-1CSC-*****A | BIVA-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | Yes
217351088 | Ground Water | BOSCH-GEO | RP024-1CSN-*****A | BIVA-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | Yes
217351089 | Ground Water | BOSCH-GEO | RP036-1CSC-*****A | BIVA-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | Yes
217351090 | Ground Water | BOSCH-GEO | RP036-1CSN-*****A | BIVA-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | Yes
217351091 | Ground Water | BOSCH-GEO | RP048-1CSC-*****A | BIVA-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | Yes
217351092 | Ground Water | BOSCH-GEO | RP048-1CSN-*****A | BIVA-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | Yes
217351093 | Ground Water | BOSCH-GEO | RP060-1CSC-*****A | BIVA-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | Yes
217351094 | Ground Water | BOSCH-GEO | RP060-1CSN-*****A | BIVA-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | Yes
217351095 | Ground Water | BOSCH-GEO | RP024-1CSC-*****A | BMAC2430BBTA | 27400 | 23.2 | 23800 | 5 | 2.2833 | Yes
217351096 | Ground Water | BOSCH-GEO | RP024-1CSN-*****A | BMAC2430BBTA | 27600 | 24.3 | 23800 | 5.1 | 2.3 | Yes
217351097 | Ground Water | BOSCH-GEO | RP036-1CSC-*****A | BMAC3036BBTA | 39600 | 21.5 | 37800 | 4.8 | 3.3 | Yes
217351098 | Ground Water | BOSCH-GEO | RP036-1CSN-*****A | BMAC3036BBTA | 40200 | 22.2 | 38800 | 5 | 3.35 | Yes
217351099 | Ground Water | BOSCH-GEO | RP048-1CSC-*****A | BMAC4248CBTA | 52000 | 21.6 | 45400 | 4.5 | 4.3333 | Yes
217351100 | Ground Water | BOSCH-GEO | RP048-1CSN-*****A | BMAC4248CBTA | 53400 | 22.5 | 46600 | 4.7 | 4.45 | Yes
217351102 | Ground Water | BOSCH-GEO | RP060-1CSN-*****A | BMAC4860CBTA | 63200 | 21.1 | 59400 | 4.5 | 5.2667 | Yes
217351103 | Ground Water | GEO-THERMAL SPLIT | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351104 | Ground Water | GEO-THERMAL SPLIT | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351105 | Ground Water | GEO-THERMAL SPLIT | GZ036SA*C******1 | F(T,G,E)5(A,B)***36*** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351106 | Ground Water | GEO-THERMAL SPLIT | GZ036SA*N******1 | F(T,G,E)5(A,B)***36*** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351107 | Ground Water | GEO-THERMAL SPLIT | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351108 | Ground Water | GEO-THERMAL SPLIT | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351109 | Ground Water | GEO-THERMAL SPLIT | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351111 | Ground Water | GEO-THERMAL SPLIT | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351112 | Ground Water | GEO-THERMAL SPLIT | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351114 | Ground Water | GEO-THERMAL SPLIT | GZ024SA*C******1 | CAAMP2***AMA | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351115 | Ground Water | GEO-THERMAL SPLIT | GZ024SA*N******1 | CAAMP2***AMA | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351116 | Ground Water | GEO-THERMAL SPLIT | GZ036SA*C******1 | CAAMP3***AMA | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351117 | Ground Water | GEO-THERMAL SPLIT | GZ036SA*N******1 | CAAMP3***AMA | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351118 | Ground Water | GEO-THERMAL SPLIT | GZ048SA*C******1 | CAAMP4***AMA | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351119 | Ground Water | GEO-THERMAL SPLIT | GZ048SA*N******1 | CAAMP4***AMA | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351120 | Ground Water | GEO-THERMAL SPLIT | GZ060SA*C******1 | CAAMP6***AMA | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351122 | Ground Water | GEO-THERMAL SPLIT | GZ072SA*C******1 | CAAMP6***AMA | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351123 | Ground Water | GEO-THERMAL SPLIT | GZ072SA*N******1 | CAAMP6***AMA | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351671 | Ground Water | BOSCH | RP024-1CSC-*****A | BIVA-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | Yes
217351672 | Ground Water | BOSCH | RP024-1CSN-*****A | BIVA-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | Yes
217351673 | Ground Water | BOSCH | RP036-1CSC-*****A | BIVA-36RCB-M20X | 40200 | 23.4 | 36400 | 4.7 | 3.35 | Yes
217351674 | Ground Water | BOSCH | RP036-1CSN-*****A | BIVA-36RCB-M20X | 41400 | 24.1 | 37000 | 4.8 | 3.45 | Yes
202921908 | Ground Water | BOSCH | EP036-1VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921909 | Ground Water | BOSCH | EP036-3VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921910 | Ground Water | BOSCH | EP036-4VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921911 | Ground Water | BOSCH-GEO | BP036-1VT*-*****B |  | 40200 | 25.9 | 34400 | 4.9 | 3.35 | No
202921912 | Ground Water | BOSCH | EP036-1HZ*-*****B |  | 40200 | 24.3 | 34400 | 4.7 | 3.35 | No
214063756 | Ground Water | GeoSmart Energy | GBV/GBH024**2*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214063757 | Ground Water | GeoSmart Energy | GBV/GBH024**2*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214063758 | Ground Water | GeoSmart Energy | GBV/GBH026**0*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214063759 | Ground Water | GeoSmart Energy | GBV/GBH026**0*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214063760 | Ground Water | GeoSmart Energy | GBV/GBH026**2*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214063761 | Ground Water | GeoSmart Energy | GBV/GBH026**2*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
214063762 | Ground Water | GeoSmart Energy | GBV/GBH030**0*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
214063763 | Ground Water | GeoSmart Energy | GBV/GBH030**0*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214063764 | Ground Water | GeoSmart Energy | GBV/GBH030**0*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214063765 | Ground Water | GeoSmart Energy | GBV/GBH030**2*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
214063766 | Ground Water | GeoSmart Energy | GBV/GBH030**2*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214063767 | Ground Water | GeoSmart Energy | GBV/GBH030**2*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
214063768 | Ground Water | GeoSmart Energy | GBV/GBH036**0*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
214063769 | Ground Water | GeoSmart Energy | GBV/GBH036**0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214063770 | Ground Water | GeoSmart Energy | GBV/GBH036**0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214063771 | Ground Water | GeoSmart Energy | GBV/GBH036**2*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
214063772 | Ground Water | GeoSmart Energy | GBV/GBH036**2*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214063773 | Ground Water | GeoSmart Energy | GBV/GBH036**2*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
214063774 | Ground Water | GeoSmart Energy | GBV/GBH038**0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214063775 | Ground Water | GeoSmart Energy | GBV/GBH038**0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214063776 | Ground Water | GeoSmart Energy | GBV/GBH038**2*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214063777 | Ground Water | GeoSmart Energy | GBV/GBH038**2*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
214063778 | Ground Water | GeoSmart Energy | GBV/GBH042**0*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214063779 | Ground Water | GeoSmart Energy | GBV/GBH042**0*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
214063780 | Ground Water | GeoSmart Energy | GBV/GBH049**0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214063781 | Ground Water | GeoSmart Energy | GBV/GBH049**0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
214063782 | Ground Water | GeoSmart Energy | GBV/GBH060**0*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
214063783 | Ground Water | GeoSmart Energy | GBV/GBH060**0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214063784 | Ground Water | GeoSmart Energy | GBV/GBH060**0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
214063785 | Ground Water | GeoSmart Energy | GBV/GBH064**0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214063786 | Ground Water | GeoSmart Energy | GBV/GBH064**0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
214063788 | Ground Water | GeoSmart Energy | GBV/GBH070**0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214063789 | Ground Water | GeoSmart Energy | GBV/GBH070**0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214063790 | Ground Water | GeoSmart Energy | GBV/GBH072**0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214063791 | Ground Water | GeoSmart Energy | GBV/GBH072**0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
8993504 | Ground Water | YORK BY JOHNSON CONTROLS | YCC/YCW/YCS/YCE15*0 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
8993505 | Ground Water | YORK BY JOHNSON CONTROLS | YCC/YCW/YCS/YCE15*2 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
9008839 | Ground Water | BOSCH | ES025-1CF/HZ/VT*-*****A |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
9008840 | Ground Water | BOSCH | ES025-2CF/HZ/VT*-*****A |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
9008841 | Ground Water | BOSCH | ES035-1CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9008842 | Ground Water | BOSCH | ES035-3CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9008843 | Ground Water | BOSCH | ES035-4CF/HZ/VT*-*****A |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
9009353 | Ground Water | FHP | ES025-1CF/HZ/VT*-*****A |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
205312007 | Ground Water | GEOSTAR | ZBV/ZBH042**3*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
205312008 | Ground Water | GEOSTAR | ZBV/ZBH042**4*1 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
205312009 | Ground Water | GEOSTAR | ZBV/ZBH042**0*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
205312010 | Ground Water | GEOSTAR | ZBV/ZBH042**3*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
205312011 | Ground Water | GEOSTAR | ZBV/ZBH042**4*4 |  | 47000 | 22 | 41400 | 4.5 | 3.9167 | No
205312027 | Ground Water | GEOSTAR | ZBV/ZBH060**0*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312028 | Ground Water | GEOSTAR | ZBV/ZBH060**3*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312029 | Ground Water | GEOSTAR | ZBV/ZBH060**4*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312030 | Ground Water | GEOSTAR | ZBV/ZBH060**0*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312031 | Ground Water | GEOSTAR | ZBV/ZBH060**3*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312032 | Ground Water | GEOSTAR | ZBV/ZBH060**4*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
205312037 | Ground Water | GEOSTAR | ZBV/ZBH070**0*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
205312038 | Ground Water | GEOSTAR | ZBV/ZBH070**3*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
205312039 | Ground Water | GEOSTAR | ZBV/ZBH070**4*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
216625704 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D0**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625705 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D0**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625706 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D0**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625707 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D2**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625708 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D3**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625709 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D3**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625710 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D3**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625711 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D4**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625712 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D4**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625713 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D4**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625714 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S0**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625715 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S0**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625716 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S0**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625717 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S2**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625718 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S3**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625719 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S3**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625720 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S3**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625721 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S4**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625722 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S4**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625723 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S4**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625724 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D0**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625725 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D0**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625726 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D3**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625727 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D3**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625728 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D4**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625729 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D4**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625730 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S0**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625731 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S0**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625732 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S3**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625733 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S3**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625734 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S4**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625735 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S4**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625736 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D0**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625737 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D0**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625738 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D3**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625739 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D3**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625740 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D4**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625741 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D4**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625742 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S0**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625743 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S0**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625744 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S3**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625745 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S3**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625746 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S4**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625747 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S4**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625748 | Ground Water | GeoSmart Energy | S5A(V/H)009*R0**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216625749 | Ground Water | GeoSmart Energy | S5A(V/H)009*R2**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216625750 | Ground Water | GeoSmart Energy | S5A(V/H)012*R0**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
216625751 | Ground Water | GeoSmart Energy | S5A(V/H)012*R2**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
216625752 | Ground Water | GeoSmart Energy | S5A(V/H)015*R0**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625753 | Ground Water | GeoSmart Energy | S5A(V/H)015*R0**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625754 | Ground Water | GeoSmart Energy | S5A(V/H)015*R2**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625755 | Ground Water | GeoSmart Energy | S5A(V/H)015*R2**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625756 | Ground Water | GeoSmart Energy | S5A(V/H)018*D0**1 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216625757 | Ground Water | GeoSmart Energy | S5A(V/H)018*D0**4 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216625758 | Ground Water | GeoSmart Energy | S5A(V/H)018*R0**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625759 | Ground Water | GeoSmart Energy | S5A(V/H)018*R0**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
7409789 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH009**0*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
7409859 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH009**2*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
7409937 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH012**0*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
7410008 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH012**2*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
7410095 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
7410164 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
7410223 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
7410291 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
7410355 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
7410435 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
7410522 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**0*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
7410657 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**0*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
7410717 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**2*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
7410825 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**2*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
7410908 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**2*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
7411002 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
217642983 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S4**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642984 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S4**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
207177429 | Ground Water | TRANE | GEVG006A |  | 8100 | 21.3 | 7500 | 4.1 | 0.675 | No
207177430 | Ground Water | TRANE | GEVG0067 |  | 8100 | 21.3 | 7500 | 4.1 | 0.675 | No
207177431 | Ground Water | TRANE | GEVG009A |  | 9600 | 23.8 | 9100 | 4.7 | 0.8 | No
207177432 | Ground Water | TRANE | GEVG0097 |  | 9600 | 23.8 | 9100 | 4.7 | 0.8 | No
207177433 | Ground Water | TRANE | GEVG012A |  | 13300 | 24.2 | 12400 | 4.6 | 1.1083 | No
207177434 | Ground Water | TRANE | GEVG0127 |  | 13300 | 24.2 | 12400 | 4.6 | 1.1083 | No
207177435 | Ground Water | TRANE | GEVG015A |  | 16600 | 23 | 15400 | 4.3 | 1.3833 | No
207177436 | Ground Water | TRANE | GEVG0157 |  | 16600 | 23 | 15400 | 4.3 | 1.3833 | No
207177437 | Ground Water | TRANE | GEVG018A |  | 19300 | 23.5 | 18400 | 4.4 | 1.6083 | No
207177438 | Ground Water | TRANE | GEVG0187 |  | 19300 | 23.5 | 18400 | 4.4 | 1.6083 | No
207177439 | Ground Water | TRANE | GEVG024A |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
207177440 | Ground Water | TRANE | GEVG024B |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
205973166 | Ground Water | Enertech | ERE036D |  | 39800 | 21.7 | 35400 | 4.4 | 3.3167 | No
205973167 | Ground Water | Enertech | ERE048D |  | 54800 | 21.1 | 48500 | 4.1 | 4.5667 | No
205973168 | Ground Water | Enertech | ERE060D |  | 69800 | 23.5 | 60100 | 4.5 | 5.8167 | No
205973169 | Ground Water | Enertech | ERE072D |  | 79000 | 23 | 72000 | 4.4 | 6.5833 | No
205973771 | Ground Water | COMFORT-AIRE | HEV/H024D |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
205973772 | Ground Water | CENTURY | HEV/H024D |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
205973775 | Ground Water | COMFORT-AIRE | HEV/H042D |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
205973776 | Ground Water | CENTURY | HEV/H042D |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
205973779 | Ground Water | COMFORT-AIRE | HEV/H060D |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
205973780 | Ground Water | CENTURY | HEV/H060D |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
214772143 | Ground Water | TRANE | DXHK048A |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772144 | Ground Water | TRANE | DXHK060A |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772145 | Ground Water | TRANE | DXHK070A |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772146 | Ground Water | TRANE | DXVK024B |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772147 | Ground Water | TRANE | DXVK0244 |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772148 | Ground Water | TRANE | DXVK036B |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772149 | Ground Water | TRANE | DXVK0364 |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772150 | Ground Water | TRANE | DXVK048B |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772151 | Ground Water | TRANE | DXVK0484 |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772152 | Ground Water | TRANE | DXVK060B |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772153 | Ground Water | TRANE | DXVK0604 |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772154 | Ground Water | TRANE | DXVK070B |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772155 | Ground Water | TRANE | DXVK0704 |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772156 | Ground Water | TRANE | DXHK024B |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772157 | Ground Water | TRANE | DXHK0244 |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772158 | Ground Water | TRANE | DXHK036B |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772159 | Ground Water | TRANE | DXHK0364 |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772160 | Ground Water | TRANE | DXHK048B |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772161 | Ground Water | TRANE | DXHK0484 |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772162 | Ground Water | TRANE | DXHK060B |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772163 | Ground Water | TRANE | DXHK0604 |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772164 | Ground Water | TRANE | DXHK070B |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772165 | Ground Water | TRANE | DXHK0704 |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772166 | Ground Water | TRANE | DXVK0247 |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772167 | Ground Water | TRANE | DXVK0367 |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772168 | Ground Water | TRANE | DXHK0247 |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772169 | Ground Water | TRANE | DXHK0367 |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214773311 | Ground Water | TRANE | GEVK072 |  | 84100 | 25.1 | 67800 | 4.19 | 7.0083 | No
214773312 | Ground Water | TRANE | GEVK090 |  | 101600 | 25.3 | 88600 | 4.42 | 8.4667 | No
214776122 | Ground Water | TRANE | GEVK0721 |  | 84100 | 25.1 | 67800 | 4.19 | 7.0083 | No
214776123 | Ground Water | TRANE | GEVK0724 |  | 84100 | 25.1 | 67800 | 4.19 | 7.0083 | No
214776124 | Ground Water | TRANE | GEVK0728 |  | 84100 | 25.1 | 67800 | 4.19 | 7.0083 | No
214776125 | Ground Water | TRANE | GEVK0904 |  | 101600 | 25.3 | 88600 | 4.42 | 8.4667 | No
214776126 | Ground Water | TRANE | GEVK0908 |  | 101600 | 25.3 | 88600 | 4.42 | 8.4667 | No
214776134 | Ground Water | TRANE | GEVK0722 |  | 84100 | 25.1 | 67800 | 4.19 | 7.0083 | No
200083647 | Ground Water | CENTURY | HZV/H/D048B |  | 55000 | 25.3 | 46800 | 4.6 | 4.5833 | Yes
200083648 | Ground Water | COMFORT-AIRE | HZV/H/D060B |  | 71500 | 24.4 | 63200 | 4.8 | 5.9583 | Yes
200083649 | Ground Water | CENTURY | HZV/H/D060B |  | 71500 | 24.4 | 63200 | 4.8 | 5.9583 | Yes
200083650 | Ground Water | COMFORT-AIRE | HZV/H/D070B |  | 77700 | 22.5 | 71400 | 4.4 | 6.475 | Yes
200083651 | Ground Water | CENTURY | HZV/H/D070B |  | 77700 | 22.5 | 71400 | 4.4 | 6.475 | Yes
200083684 | Ground Water | COMFORT-AIRE | HZS024B | WDG024**A-*B | 25600 | 22.4 | 24900 | 4.5 | 2.1333 | Yes
200083685 | Ground Water | CENTURY | HZS024B | WDG024**A-*B | 25600 | 22.4 | 24900 | 4.5 | 2.1333 | Yes
200083686 | Ground Water | COMFORT-AIRE | HZS024B | WDG024**B-*B | 27300 | 24 | 22800 | 4.4 | 2.275 | Yes
200083687 | Ground Water | CENTURY | HZS024B | WDG024**B-*B | 27300 | 24 | 22800 | 4.4 | 2.275 | Yes
200083688 | Ground Water | COMFORT-AIRE | HZS024B | MWG24*A-B | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
200083689 | Ground Water | CENTURY | HZS024B | MWG24*A-B | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
200083690 | Ground Water | COMFORT-AIRE | HZS024B | MWG24*C-B | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
200083691 | Ground Water | CENTURY | HZS024B | MWG24*C-B | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
200083692 | Ground Water | COMFORT-AIRE | HZS024B | MWG24*B-B | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
200083693 | Ground Water | CENTURY | HZS024B | MWG24*B-B | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
200083694 | Ground Water | COMFORT-AIRE | HZS036B | MWG36**-B | 40200 | 22.3 | 32800 | 4.4 | 3.35 | No
200083695 | Ground Water | CENTURY | HZS036B | MWG36**-B | 40200 | 22.3 | 32800 | 4.4 | 3.35 | Yes
200083696 | Ground Water | COMFORT-AIRE | HZS036B | WDG036***-*B | 40500 | 23.4 | 32700 | 4.5 | 3.375 | Yes
200083697 | Ground Water | CENTURY | HZS036B | WDG036***-*B | 40500 | 23.4 | 32700 | 4.5 | 3.375 | Yes
200083700 | Ground Water | COMFORT-AIRE | HZS048B | WDG048***-*B | 52800 | 23 | 45900 | 4.2 | 4.4 | Yes
214823484 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)036BD1**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | Yes
214823485 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)042BD1**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | Yes
215415734 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)024A*B |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415735 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)024A*C |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415736 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)024A*VB |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415737 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)024A*VC |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415740 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)030A*VB |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415741 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)030A*VC |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415744 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)036A*VB |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415745 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)036A*VC |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415748 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)042A*VB |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415749 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)042A*VC |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415750 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)048A*B |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415751 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)048A*C |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415752 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)048A*VB |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415753 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)048A*VC |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
7519551 | Ground Water | TETCO | TVS024*A |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519552 | Ground Water | GEOCOMFORT | GVS024*2 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519553 | Ground Water | HYDRON MODULE | HVS024*2 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519554 | Ground Water | TETCO | TVS024*2 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519555 | Ground Water | GEOCOMFORT | GVS024*3 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519556 | Ground Water | HYDRON MODULE | HVS024*3 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519557 | Ground Water | TETCO | TVS024*3 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519558 | Ground Water | GEOCOMFORT | GVS024*4 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519559 | Ground Water | HYDRON MODULE | HVS024*4 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519560 | Ground Water | TETCO | TVS024*4 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519561 | Ground Water | GEOCOMFORT | GVS030*A |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519562 | Ground Water | HYDRON MODULE | HVS030*A |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519563 | Ground Water | TETCO | TVS030*A |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519564 | Ground Water | GEOCOMFORT | GVS030*2 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519565 | Ground Water | HYDRON MODULE | HVS030*2 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
7519566 | Ground Water | TETCO | TVS030*2 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | No
203113888 | Ground Water | GEOSTAR | 103J036**1 | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
203113890 | Ground Water | GEOSTAR | 103J042**1 | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
203113892 | Ground Water | GEOSTAR | 103J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
203113894 | Ground Water | GEOSTAR | 104J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
203143108 | Ground Water | GEOCOMFORT | GVS041 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | Yes
203143111 | Ground Water | GEOCOMFORT | GVS041*2 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143114 | Ground Water | GEOCOMFORT | GVS041*3 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143119 | Ground Water | GEOCOMFORT | GVS041*4 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143124 | Ground Water | HYDRON MODULE | HVS041 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | Yes
203143129 | Ground Water | HYDRON MODULE | HVS041*2 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143133 | Ground Water | HYDRON MODULE | HVS041*3 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143138 | Ground Water | HYDRON MODULE | HVS041*4 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143143 | Ground Water | TETCO | TVS041 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | Yes
203143148 | Ground Water | TETCO | TVS041*2 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143153 | Ground Water | TETCO | TVS041*3 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143157 | Ground Water | TETCO | TVS041*4 |  | 41400 | 22.3 | 38900 | 4.1 | 3.45 | No
203143746 | Ground Water | GEOCOMFORT | GVS041*****1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | Yes
203143749 | Ground Water | GEOCOMFORT | GVS041*2***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203143752 | Ground Water | GEOCOMFORT | GVS041*3***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203143764 | Ground Water | HYDRON MODULE | HVS041*****1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | Yes
203143767 | Ground Water | HYDRON MODULE | HVS041*2***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203143770 | Ground Water | HYDRON MODULE | HVS041*3***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203143781 | Ground Water | TETCO | TVS041*****1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | Yes
203143785 | Ground Water | TETCO | TVS041*2***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203143790 | Ground Water | TETCO | TVS041*3***1 |  | 43000 | 23.6 | 39200 | 4.4 | 3.5833 | No
203238019 | Ground Water | BOSCH-GEO | BP042-1HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203238020 | Ground Water | GEO-THERMAL SPLIT | GZ036***C***1**2 | FE/V****005*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203238919 | Ground Water | BOSCH-GEO | SM024-1VT/CFN-*****A |  | 29000 | 23.7 | 23500 | 4.6 | 2.4167 | Yes
203238923 | Ground Water | BOSCH-GEO | SM024-1HZC-*****A |  | 29000 | 25.75 | 23500 | 5 | 2.4167 | No
203238926 | Ground Water | BOSCH-GEO | SM024-1HZN-*****A |  | 29000 | 24.1 | 23500 | 5 | 2.4167 | No
203253412 | Ground Water | BOSCH | BP042-1HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | Yes
203253413 | Ground Water | BOSCH | SM024-1HZC-*****A |  | 29000 | 25.75 | 23500 | 5 | 2.4167 | Yes
203253414 | Ground Water | BOSCH | SM024-1HZC-*****C |  | 29000 | 25.75 | 23500 | 5 | 2.4167 | Yes
203253415 | Ground Water | BOSCH | SM024-1HZN-*****A |  | 29000 | 24.1 | 23500 | 5 | 2.4167 | Yes
203253416 | Ground Water | BOSCH | SM024-1HZN-*****C |  | 29000 | 24.1 | 23500 | 5 | 2.4167 | Yes
203254061 | Ground Water | BOSCH-GEO | SM070-1VT*-*****C |  | 78900 | 22.1 | 72600 | 4.4 | 6.575 | Yes
203254465 | Ground Water | BOSCH | SM070-1VT*******C |  | 78900 | 22.1 | 72600 | 4.4 | 6.575 | Yes
203254574 | Ground Water | CARRIER | GZ036***C***1**2 | FE/V****005 | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
203254575 | Ground Water | BRYANT | GZ036***C***1**2 | FE/V****005 | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254576 | Ground Water | HEIL | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
203254577 | Ground Water | ARCOAIRE | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254578 | Ground Water | KEEPRITE | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254579 | Ground Water | TEMPSTAR | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254580 | Ground Water | COMFORTMAKER | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254581 | Ground Water | DAY & NIGHT | HS036***C***1**2 | FVM4X4800BL | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
203254606 | Ground Water | CARRIER | GB042H******1**1 |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
205752888 | Ground Water | ClimateMaster | TCH/V006A*W/K |  | 7000 | 24 | 6300 | 4.2 | 0.58333 | No
205754885 | Ground Water | Johnson Controls | JCH/V015A*W/K B |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
205754886 | Ground Water | SKYMARK | JCH/V015A*W/K C |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
205754887 | Ground Water | Johnson Controls | JCH/V018A B |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
205754888 | Ground Water | SKYMARK | JCH/V018A C |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
205754889 | Ground Water | Johnson Controls | JCH/V018A*W/K B |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
205754890 | Ground Water | SKYMARK | JCH/V018A*W/K C |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
205754895 | Ground Water | Johnson Controls | JCH/V030A*W/K B |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
205754896 | Ground Water | SKYMARK | JCH/V030A*W/K C |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
214595658 | Ground Water | AAON, Inc. | RN-009-2-0-FCAY-S0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595659 | Ground Water | AAON, Inc. | RN-009-3-0-FCAY-S0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595660 | Ground Water | AAON, Inc. | RN-009-4-0-FCAY-S0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595661 | Ground Water | AAON, Inc. | RN-009-2-0-GCAY-V0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595662 | Ground Water | AAON, Inc. | RN-009-3-0-GCAY-V0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595663 | Ground Water | AAON, Inc. | RN-009-4-0-GCAY-V0-10-000-A |  | 109000 | 24.5 | 89900 | 4.9 | 9.0833 | No
214595670 | Ground Water | AAON, Inc. | RN-011-2-0-FCAY-S0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
214595671 | Ground Water | AAON, Inc. | RN-011-3-0-FCAY-S0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
214595672 | Ground Water | AAON, Inc. | RN-011-4-0-FCAY-S0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
214595673 | Ground Water | AAON, Inc. | RN-011-2-0-GCAY-V0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
214595674 | Ground Water | AAON, Inc. | RN-011-3-0-GCAY-V0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
214595675 | Ground Water | AAON, Inc. | RN-011-4-0-GCAY-V0-10-000-A |  | 125000 | 21.1 | 112500 | 4.5 | 10.4167 | No
217122387 | Ground Water | ClimateMaster | SWM060A |  | 58700 | 23.4 | 57900 | 4.1 | 4.8917 | Yes
217193306 | Ground Water | WaterFurnace | V7A(V/H)024*V0**1* |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
217193307 | Ground Water | WaterFurnace | V7A(V/H)036*V0**1* |  | 43000 | 28 | 37000 | 4.5 | 3.5833 | No
217193308 | Ground Water | WaterFurnace | V7A(V/H)048*V0**1* |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
217193309 | Ground Water | WaterFurnace | V7A(V/H)060*V0**1* |  | 65000 | 23 | 58000 | 4.2 | 5.4167 | No
217193552 | Ground Water | WaterFurnace | V7A(V/H)024*V3**1* |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
217193553 | Ground Water | WaterFurnace | V7A(V/H)024*V4**1* |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
217193554 | Ground Water | WaterFurnace | V7A(V/H)036*V3**1* |  | 43000 | 28 | 37000 | 4.5 | 3.5833 | No
217193555 | Ground Water | WaterFurnace | V7A(V/H)036*V4**1* |  | 43000 | 28 | 37000 | 4.5 | 3.5833 | No
217193556 | Ground Water | WaterFurnace | V7A(V/H)048*V3**1* |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
217193557 | Ground Water | WaterFurnace | V7A(V/H)048*V4**1* |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
217193558 | Ground Water | WaterFurnace | V7A(V/H)060*V3**1* |  | 65000 | 23 | 58000 | 4.2 | 5.4167 | No
217193559 | Ground Water | WaterFurnace | V7A(V/H)060*V4**1* |  | 65000 | 23 | 58000 | 4.2 | 5.4167 | No
217212043 | Ground Water | FHP | CP024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212044 | Ground Water | FHP | CP024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
217212045 | Ground Water | FHP | CP024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212046 | Ground Water | FHP | CP024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
217212048 | Ground Water | FHP | CP024-2HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212049 | Ground Water | FHP | CP024-2HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
217212050 | Ground Water | FHP | CP024-2VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212051 | Ground Water | FHP | CP024-2VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
217212052 | Ground Water | FHP | CP024-3HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212054 | Ground Water | FHP | CP024-3HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | No
217212055 | Ground Water | FHP | CP024-3VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | No
217212056 | Ground Water | FHP | CP024-3VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | No
201864513 | Ground Water | GEOCOMFORT | GZT024*A |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201864514 | Ground Water | HYDRON MODULE | HZT024*A |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201864515 | Ground Water | TETCO | TZT024*A |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201864519 | Ground Water | GEOCOMFORT | GZT024*3 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201864521 | Ground Water | HYDRON MODULE | HZT024*3 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
201864523 | Ground Water | TETCO | TZT024*3 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | No
206342110 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH080**5 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
206342111 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH095**3 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
206342112 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH095**4 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
206342113 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH095**5 |  | 95000 | 23 | 78000 | 4.3 | 7.9167 | No
206342114 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH120**3 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
206342115 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH120**4 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
206342116 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH120**5 |  | 129000 | 21.9 | 115000 | 4.1 | 10.75 | No
206342117 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*3 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
206342118 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*4 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
206342119 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*5 |  | 84000 | 24.2 | 71000 | 4.4 | 7 | No
206342120 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*3 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
206342121 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*4 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
206342122 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*5 |  | 101000 | 25.7 | 83000 | 4.6 | 8.4167 | No
206342123 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*3 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
206342124 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*5 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
206342125 | Ground Water | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*4 |  | 135000 | 24.3 | 107500 | 4.4 | 11.25 | No
206345837 | Ground Water | HYDROTECH | WSS6006*7* |  | 8600 | 26 | 7200 | 4.5 | 0.71667 | No
206345838 | Ground Water | HYDROTECH | WSS6009*7* |  | 11200 | 26 | 8200 | 4.5 | 0.93333 | No
206345839 | Ground Water | HYDROTECH | WSS6012*7* |  | 13800 | 26 | 10400 | 4.5 | 1.15 | No
206345840 | Ground Water | HYDROTECH | WSS6015*7* |  | 18100 | 23.1 | 15500 | 4.3 | 1.5083 | No
202330486 | Ground Water | AAON, Inc. | SB-004-1-0-BCBC-V0-10-000-A |  | 48100 | 21.7 | 50300 | 4.2 | 4.0083 | No
202330488 | Ground Water | AAON, Inc. | SB-004-2-0-BCBC-V0-10-000-A |  | 48100 | 21.7 | 50300 | 4.2 | 4.0083 | No
202330490 | Ground Water | AAON, Inc. | SB-004-3-0-BCBC-V0-10-000-A |  | 48100 | 21.7 | 50300 | 4.2 | 4.0083 | No
202330492 | Ground Water | AAON, Inc. | SB-004-4-0-BCBC-V0-10-000-A |  | 48100 | 21.7 | 50300 | 4.2 | 4.0083 | No
202330514 | Ground Water | AAON, Inc. | M2-003-1-H-BCBC-V0-10-000-A |  | 46200 | 25.5 | 38000 | 4.3 | 3.85 | No
206900573 | Ground Water | YORK BY JOHNSON CONTROLS | YDLV084**5 |  | 98000 | 24 | 84000 | 4.4 | 8.1667 | No
206900574 | Ground Water | YORK BY JOHNSON CONTROLS | YDLH084**3 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900575 | Ground Water | YORK BY JOHNSON CONTROLS | YDLH084**4 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900576 | Ground Water | YORK BY JOHNSON CONTROLS | YDLH084**5 |  | 96000 | 22 | 82500 | 4.3 | 8 | No
206900577 | Ground Water | YORK BY JOHNSON CONTROLS | YDLV096**3 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900578 | Ground Water | YORK BY JOHNSON CONTROLS | YDLV096**4 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
206900579 | Ground Water | YORK BY JOHNSON CONTROLS | YDLV096**5 |  | 106000 | 22 | 96000 | 4.4 | 8.8333 | No
5273062 | Ground Water | WaterFurnace | NBV/NBH009**0*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
5273082 | Ground Water | WaterFurnace | NBV/NBH009**2*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
5273138 | Ground Water | WaterFurnace | NBV/NBH012**0*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
5274236 | Ground Water | WaterFurnace | NBV/NBH012**2*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
5295936 | Ground Water | WaterFurnace | NBV/NBH015**0*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
5295937 | Ground Water | WaterFurnace | NBV/NBH015**2*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
5295944 | Ground Water | WaterFurnace | NBV/NBH015**2*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
5295945 | Ground Water | WaterFurnace | NBV/NBH015**2*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
5295947 | Ground Water | WaterFurnace | NBV/NBH015**0*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
5295948 | Ground Water | WaterFurnace | NBV/NBH015**0*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
5295960 | Ground Water | WaterFurnace | NBV/NBH018**0*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
5295962 | Ground Water | WaterFurnace | NBV/NBH018**2*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
5295964 | Ground Water | WaterFurnace | NBV/NBH018**2*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
207822807 | Ground Water | HYDROTECH | HRCX30*-6 |  | 30000 | 23.5 | 25000 | 4.1 | 2.5 | Yes
207822813 | Ground Water | HYDROTECH | HRCX36*-6 |  | 35500 | 21.6 | 31500 | 4.1 | 2.9583 | Yes
208106952 | Ground Water | 5 SERIES GEO-READY | NGV/NGH038*1*(1,2) |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
208106953 | Ground Water | 5 SERIES GEO-READY | NGV/NGH049*1*(1,2) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
208106954 | Ground Water | 5 SERIES GEO-READY | NGV/NGH064*1*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
214771937 | Ground Water | TRANE | EXVK036A |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214771938 | Ground Water | TRANE | EXVK042A |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214771939 | Ground Water | TRANE | EXVK048A |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214771940 | Ground Water | TRANE | EXVK060A |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
201907610 | Ground Water | WaterFurnace | URS036*0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907611 | Ground Water | WaterFurnace | URS036*0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907612 | Ground Water | WaterFurnace | URS036*0*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907613 | Ground Water | WaterFurnace | URS036*3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907614 | Ground Water | WaterFurnace | URS036*3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907615 | Ground Water | WaterFurnace | URS036*3*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907616 | Ground Water | WaterFurnace | URS036*4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907617 | Ground Water | WaterFurnace | URS036*4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907618 | Ground Water | WaterFurnace | URS036*4*5 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
201907619 | Ground Water | WaterFurnace | URS048*0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
206722530 | Ground Water | ClimateMaster | TRH/V006A*W/K |  | 7000 | 24 | 6300 | 4.2 | 0.58333 | No
206726680 | Ground Water | WaterFurnace | UVV/UVH024**0*1 |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
214841657 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
214841658 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
214841660 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
214841662 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
214841664 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
214595583 | Ground Water | AAON, Inc. | SB-004-3-0-GCBC-V0-10-000-A |  | 48100 | 21.3 | 48300 | 4.1 | 4.0083 | No
214595585 | Ground Water | AAON, Inc. | SB-004-4-0-GCBC-V0-10-000-A |  | 48100 | 21.3 | 48300 | 4.1 | 4.0083 | No
214595607 | Ground Water | AAON, Inc. | M2-003-2-H-GCBC-V0-10-000-A |  | 46200 | 25 | 36500 | 4.2 | 3.85 | No
214595611 | Ground Water | AAON, Inc. | M2-003-3-H-GCBC-V0-10-000-A |  | 46200 | 25 | 36500 | 4.2 | 3.85 | No
214595615 | Ground Water | AAON, Inc. | M2-003-4-H-GCBC-V0-10-000-A |  | 46200 | 25 | 36500 | 4.2 | 3.85 | No
214595618 | Ground Water | AAON, Inc. | M2-004-1-H-FCAC-S0-10-000-A |  | 54200 | 23 | 44000 | 4.1 | 4.5167 | No
214595619 | Ground Water | AAON, Inc. | M2-004-1-H-FCBC-S0-10-000-A |  | 56200 | 23.4 | 44400 | 4.3 | 4.6833 | No
214595620 | Ground Water | AAON, Inc. | M2-004-2-H-GCAC-V0-10-000-A |  | 55200 | 24.2 | 44400 | 4.2 | 4.6 | No
214595621 | Ground Water | AAON, Inc. | M2-004-2-H-GCBC-V0-10-000-A |  | 57500 | 25.6 | 44800 | 4.3 | 4.7917 | No
214595622 | Ground Water | AAON, Inc. | M2-004-2-H-FCAC-S0-10-000-A |  | 54200 | 23 | 44000 | 4.1 | 4.5167 | No
214595623 | Ground Water | AAON, Inc. | M2-004-2-H-FCBC-S0-10-000-A |  | 56200 | 23.4 | 44400 | 4.3 | 4.6833 | No
214595624 | Ground Water | AAON, Inc. | M2-004-3-H-GCAC-V0-10-000-A |  | 55200 | 24.2 | 44400 | 4.2 | 4.6 | No
214595625 | Ground Water | AAON, Inc. | M2-004-3-H-GCBC-V0-10-000-A |  | 57500 | 25.6 | 44800 | 4.3 | 4.7917 | No
214595626 | Ground Water | AAON, Inc. | M2-004-3-H-FCAC-S0-10-000-A |  | 54200 | 23 | 44000 | 4.1 | 4.5167 | No
214595627 | Ground Water | AAON, Inc. | M2-004-3-H-FCBC-S0-10-000-A |  | 56200 | 23.4 | 44400 | 4.3 | 4.6833 | No
214595628 | Ground Water | AAON, Inc. | M2-004-4-H-GCAC-V0-10-000-A |  | 55200 | 24.2 | 44400 | 4.2 | 4.6 | No
214595629 | Ground Water | AAON, Inc. | M2-004-4-H-GCBC-V0-10-000-A |  | 57500 | 25.6 | 44800 | 4.3 | 4.7917 | No
214595630 | Ground Water | AAON, Inc. | M2-004-4-H-FCAC-S0-10-000-A |  | 54200 | 23 | 44000 | 4.1 | 4.5167 | No
214595631 | Ground Water | AAON, Inc. | M2-004-4-H-FCBC-S0-10-000-A |  | 56200 | 23.4 | 44400 | 4.3 | 4.6833 | No
215268318 | Ground Water | WaterFurnace | V3A(V/H)024*S0**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268320 | Ground Water | WaterFurnace | V3A(V/H)036*S0**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268321 | Ground Water | WaterFurnace | V3A(V/H)042*S0**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268323 | Ground Water | WaterFurnace | V3A(V/H)060*S0**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268325 | Ground Water | WaterFurnace | V3A(V/H)006*R2**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
215268328 | Ground Water | WaterFurnace | V3A(V/H)015*R0**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
215268329 | Ground Water | WaterFurnace | V3A(V/H)015*R2**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
215268330 | Ground Water | WaterFurnace | V3A(V/H)015*R2**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217212078 | Ground Water | FHP | CP048-4VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | No
217212079 | Ground Water | FHP | CP060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
217212080 | Ground Water | FHP | CP060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
217212082 | Ground Water | FHP | CP060-3VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
217212083 | Ground Water | FHP | CP060-3VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
217212084 | Ground Water | FHP | CP060-4VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | No
217212085 | Ground Water | FHP | CP060-4VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | No
217212086 | Ground Water | FHP | CP070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212088 | Ground Water | FHP | CP070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212089 | Ground Water | FHP | CP070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212090 | Ground Water | FHP | CP070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212091 | Ground Water | FHP | CP070-3HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212093 | Ground Water | FHP | CP070-3HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212094 | Ground Water | FHP | CP070-3VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212095 | Ground Water | FHP | CP070-3VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212097 | Ground Water | FHP | CP070-4HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212098 | Ground Water | FHP | CP070-4HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212099 | Ground Water | FHP | CP070-4VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | No
217212101 | Ground Water | FHP | CP070-4VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | No
217212102 | Ground Water | BOSCH | RP024-1HZC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
217212103 | Ground Water | BOSCH | RP024-1HZN-*****A |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
217212105 | Ground Water | BOSCH | RP024-1VTC-*****A |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
217212106 | Ground Water | BOSCH | RP024-1VTN-*****A |  | 26500 | 24 | 22500 | 4.8 | 2.2083 | Yes
217212107 | Ground Water | BOSCH | RP036-1VT/HZC-*****A |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
217212108 | Ground Water | BOSCH | RP036-1VT/HZN-*****A |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
217212109 | Ground Water | BOSCH | RP048-1VT/HZC-*****A |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
217212111 | Ground Water | BOSCH | RP048-1VT/HZN-*****A |  | 53000 | 22.5 | 47500 | 5 | 4.4167 | Yes
217212112 | Ground Water | BOSCH | RP060-1VT/HZC-*****A |  | 67500 | 23.5 | 62000 | 5 | 5.625 | Yes
217212113 | Ground Water | BOSCH | RP060-1VT/HZN-*****A |  | 67000 | 23 | 61500 | 5 | 5.5833 | Yes
217212114 | Ground Water | BOSCH | RP070-1HZC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217212115 | Ground Water | BOSCH | RP070-1HZN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217212116 | Ground Water | BOSCH | RP070-1VTC-*****A |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217212117 | Ground Water | BOSCH | RP070-1VTN-*****A |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217351071 | Ground Water | BOSCH | CP024-1CSC-*****A | BIVA-24RCB-M20X | 27400 | 24.3 | 23200 | 4.8 | 2.2833 | No
217351072 | Ground Water | BOSCH | CP024-1CSN-*****A | BIVA-24RCB-M20X | 27200 | 25.2 | 23200 | 4.9 | 2.2667 | No
204031803 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT049**1*J | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
204031812 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT049**1*J | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
5440703 | Ground Water | GEOCOMFORT | GXT060D3 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440704 | Ground Water | HYDRON MODULE | HXT060D3 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440705 | Ground Water | TETCO | TXT060D3 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440708 | Ground Water | GEOCOMFORT | GXT072D3 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5440709 | Ground Water | HYDRON MODULE | HXT072D3 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5440710 | Ground Water | TETCO | TXT072D3 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5599272 | Ground Water | BOSCH-GEO | SM036-1CF/HZ/VT |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
5599275 | Ground Water | BOSCH-GEO | SM060-1CF/HZ/VT |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | Yes
5599276 | Ground Water | BOSCH-GEO | SM070-1CF/HZ/VT |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | Yes
202443461 | Ground Water | GeoSmart Energy | GSZ036*1*J | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
202443462 | Ground Water | GeoSmart Energy | GSZ042*1*J | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
202443463 | Ground Water | GeoSmart Energy | GTZ038*1*J | SAH038* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
202443470 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
202443471 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS042**1*J | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
202443472 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT038**1*J | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
202443473 | Ground Water | YORK BY JOHNSON CONTROLS | YAST038**1*J | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
202449772 | Ground Water | WaterFurnace | UBV/UBH030**0*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449773 | Ground Water | WaterFurnace | UBV/UBH030**2*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449774 | Ground Water | WaterFurnace | UBV/UBH030**3*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449775 | Ground Water | WaterFurnace | UBV/UBH030**4*1 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449776 | Ground Water | WaterFurnace | UBV/UBH030**0*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449777 | Ground Water | WaterFurnace | UBV/UBH030**2*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449778 | Ground Water | WaterFurnace | UBV/UBH030**3*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449779 | Ground Water | WaterFurnace | UBV/UBH030**4*4 |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
202449780 | Ground Water | WaterFurnace | UBV/UBH036**0*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
202449781 | Ground Water | WaterFurnace | UBV/UBH036**2*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
202449782 | Ground Water | WaterFurnace | UBV/UBH036**3*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
202449783 | Ground Water | WaterFurnace | UBV/UBH036**4*0 |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
202449784 | Ground Water | WaterFurnace | UBV/UBH036**0*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449785 | Ground Water | WaterFurnace | UBV/UBH036**2*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449786 | Ground Water | WaterFurnace | UBV/UBH036**3*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449787 | Ground Water | WaterFurnace | UBV/UBH036**4*1 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449788 | Ground Water | WaterFurnace | UBV/UBH036**0*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449789 | Ground Water | WaterFurnace | UBV/UBH036**2*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449790 | Ground Water | WaterFurnace | UBV/UBH036**3*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
202449791 | Ground Water | WaterFurnace | UBV/UBH036**4*4 |  | 40000 | 23 | 35600 | 4.4 | 3.3333 | No
207200579 | Ground Water | GeoSmart Energy | GTS026*1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207200580 | Ground Water | GeoSmart Energy | GTS049*1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207200581 | Ground Water | GeoSmart Energy | GTS049*1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207200582 | Ground Water | GeoSmart Energy | GTS064*1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
207200583 | Ground Water | GeoSmart Energy | GTS064*1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
8738037 | Ground Water | GEOCOMFORT | GVT060*3 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738038 | Ground Water | HYDRON MODULE | HVT060*3 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738039 | Ground Water | TETCO | TVT060*3 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738040 | Ground Water | GEOCOMFORT | GVT060*A |  | 64200 | 21.1 | 57500 | 4.4 | 5.35 | No
8738041 | Ground Water | HYDRON MODULE | HVT060*A |  | 64200 | 21.1 | 57500 | 4.4 | 5.35 | No
8738042 | Ground Water | TETCO | TVT060*A |  | 64200 | 21.1 | 57500 | 4.4 | 5.35 | No
8738051 | Ground Water | GEOCOMFORT | GVS042 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | Yes
8738052 | Ground Water | HYDRON MODULE | HVS042 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | Yes
8738053 | Ground Water | TETCO | TVS042 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | Yes
8738054 | Ground Water | GEOCOMFORT | GVS042*2 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738055 | Ground Water | HYDRON MODULE | HVS042*2 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738056 | Ground Water | TETCO | TVS042*2 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738057 | Ground Water | GEOCOMFORT | GVS042*3 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738058 | Ground Water | HYDRON MODULE | HVS042*3 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738059 | Ground Water | TETCO | TVS042*3 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738060 | Ground Water | GEOCOMFORT | GVS042*4 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738061 | Ground Water | HYDRON MODULE | HVS042*4 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738062 | Ground Water | TETCO | TVS042*4 |  | 46700 | 24.4 | 39200 | 4.7 | 3.8917 | No
8738067 | Ground Water | GEOCOMFORT | GVS048 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | Yes
8738068 | Ground Water | HYDRON MODULE | HVS048 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | Yes
8738069 | Ground Water | TETCO | TVS048 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | Yes
8738070 | Ground Water | GEOCOMFORT | GVS048*2 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738071 | Ground Water | HYDRON MODULE | HVS048*2 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738072 | Ground Water | TETCO | TVS048*2 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738073 | Ground Water | GEOCOMFORT | GVS048*3 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738074 | Ground Water | HYDRON MODULE | HVS048*3 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738075 | Ground Water | TETCO | TVS048*3 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738076 | Ground Water | GEOCOMFORT | GVS048*4 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738077 | Ground Water | HYDRON MODULE | HVS048*4 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
8738078 | Ground Water | TETCO | TVS048*4 |  | 53400 | 22.6 | 48100 | 4.4 | 4.45 | No
204272856 | Ground Water | GeoSmart Energy | GT064**1*(1,4)*J |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
204272857 | Ground Water | GeoSmart Energy | GTS064*1*J | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
204272858 | Ground Water | GeoSmart Energy | GTS064*1*J | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
204272859 | Ground Water | GeoSmart Energy | GTZ064*1*J | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204272860 | Ground Water | GeoSmart Energy | GTZ064*1*J | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204272890 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT064**1*(1,4)*J |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
204272892 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT064**1*J | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204272893 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT064**1*J | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
204276830 | Ground Water | GEOSTAR | 104J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
204276831 | Ground Water | GEOSTAR | 103J038**1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
204278291 | Ground Water | WaterFurnace | SDV038J1*(1,2) |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
204283848 | Ground Water | BOSCH-GEO | SM048-1CS*-*****A | SM048-1AH*******A | 52800 | 21.15 | 46600 | 4.4 | 4.4 | Yes
204283849 | Ground Water | BOSCH | SM048-1CS*-*****A | SM048-1AH*******A | 52800 | 21.15 | 46600 | 4.4 | 4.4 | Yes
204346746 | Ground Water | GeoCool | GCHPV/H/D024T**A*** |  | 29000 | 27.4 | 25700 | 5.4 | 2.4167 | No
204346873 | Ground Water | GeoCool | GCHPV/H/D036T**A*** |  | 43000 | 27.2 | 38000 | 5.3 | 3.5833 | No
204346874 | Ground Water | GeoCool | GCHPV/H/D048T**A*** |  | 56000 | 26 | 50000 | 4.9 | 4.6667 | No
204370721 | Ground Water | GeoCool | GCHPV/H/D060T**A*** |  | 72500 | 24 | 64500 | 4.9 | 6.0417 | No
205767582 | Ground Water | ClimateMaster | TES/P038B | TAH038C | 40500 | 23.4 | 32700 | 4.5 | 3.375 | Yes
205767583 | Ground Water | ClimateMaster | TES/P049B | TAH049C | 52800 | 23 | 45900 | 4.2 | 4.4 | Yes
205767586 | Ground Water | ClimateMaster | TES/P026B | TAH026C***A* | 25600 | 22.4 | 24900 | 4.5 | 2.1333 | Yes
205767587 | Ground Water | ClimateMaster | TES/P026B | TAH026C***B* | 27300 | 24 | 22800 | 4.4 | 2.275 | Yes
205767588 | Ground Water | ClimateMaster | TES/P026B | TAC026B***A* | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
205767589 | Ground Water | ClimateMaster | TES/P026B | TAC026B***B* | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
205767590 | Ground Water | ClimateMaster | TRE036D |  | 39800 | 21.7 | 35400 | 4.4 | 3.3167 | No
205767591 | Ground Water | ClimateMaster | TRE048D |  | 54800 | 21.1 | 48500 | 4.1 | 4.5667 | No
205767592 | Ground Water | ClimateMaster | TRE060D |  | 69800 | 23.5 | 60100 | 4.5 | 5.8167 | No
205767593 | Ground Water | ClimateMaster | TRE072D |  | 79000 | 23 | 72000 | 4.4 | 6.5833 | No
205767605 | Ground Water | ClimateMaster | VEV/H/D1860 |  | 48000 | 35.5 | 60000 | 4.3 | 4 | Yes
205767606 | Ground Water | ClimateMaster | VEV/H/D0930 |  | 24000 | 42 | 30000 | 4.8 | 2 | Yes
205767607 | Ground Water | ClimateMaster | TZV/H036D |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
205767608 | Ground Water | ClimateMaster | TZV/H024D |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
205767610 | Ground Water | ClimateMaster | TZV/H042D |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
205767612 | Ground Water | ClimateMaster | TZV/H060D |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
205767615 | Ground Water | ClimateMaster | QEV/H/D0930 |  | 24000 | 42 | 30000 | 4.8 | 2 | Yes
205767616 | Ground Water | ClimateMaster | TYV/H060B |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | No
214771941 | Ground Water | TRANE | EXVK070A |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214771943 | Ground Water | TRANE | GEHK009A |  | 9400 | 25.6 | 8600 | 4.94 | 0.78333 | No
214771944 | Ground Water | TRANE | GEHK012A |  | 11900 | 22.3 | 11500 | 4.45 | 0.99167 | No
214771945 | Ground Water | TRANE | GEHK015A |  | 16800 | 24.1 | 16700 | 4.69 | 1.4 | No
214771946 | Ground Water | TRANE | GEHK018A |  | 19600 | 23.4 | 19500 | 4.46 | 1.6333 | No
214771947 | Ground Water | TRANE | GEHK024A |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214771948 | Ground Water | TRANE | GEHK030A |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214771949 | Ground Water | TRANE | GEHK036A |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214771950 | Ground Water | TRANE | GEHK042A |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214771951 | Ground Water | TRANE | GEHK048A |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214771952 | Ground Water | TRANE | GEHK060A |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214771953 | Ground Water | TRANE | EXHK009A |  | 9600 | 29.7 | 8500 | 5.16 | 0.8 | No
214771954 | Ground Water | TRANE | EXHK012A |  | 12500 | 26.1 | 11500 | 4.98 | 1.0417 | No
214771955 | Ground Water | TRANE | EXHK015A |  | 17100 | 24.6 | 15600 | 4.6 | 1.425 | No
214771956 | Ground Water | TRANE | EXHK018A |  | 21100 | 29.6 | 18600 | 4.77 | 1.7583 | No
214771957 | Ground Water | TRANE | EXHK024A |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214771958 | Ground Water | TRANE | EXHK030A |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
214771959 | Ground Water | TRANE | EXHK036A |  | 39500 | 28.4 | 35500 | 4.91 | 3.2917 | No
214771960 | Ground Water | TRANE | EXHK042A |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214771961 | Ground Water | TRANE | EXHK048A |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214771962 | Ground Water | TRANE | EXHK060A |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214771963 | Ground Water | TRANE | EXHK070A |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214772055 | Ground Water | TRANE | GEVK0097 |  | 9400 | 25.6 | 8600 | 4.94 | 0.78333 | No
214772056 | Ground Water | TRANE | GEVK0127 |  | 11900 | 22.3 | 11500 | 4.45 | 0.99167 | No
214772057 | Ground Water | TRANE | GEVK0157 |  | 16800 | 24.1 | 16700 | 4.69 | 1.4 | No
214772058 | Ground Water | TRANE | GEVK0187 |  | 19600 | 23.4 | 19500 | 4.46 | 1.6333 | No
214772059 | Ground Water | TRANE | GEVK024B |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772060 | Ground Water | TRANE | GEVK0244 |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772061 | Ground Water | TRANE | GEVK0247 |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214772062 | Ground Water | TRANE | GEVK030B |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772063 | Ground Water | TRANE | GEVK0304 |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772064 | Ground Water | TRANE | GEVK0307 |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214772065 | Ground Water | TRANE | GEVK036B |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
215415870 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415871 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415872 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415873 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415874 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415875 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415876 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415877 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415878 | Ground Water | CENTURY | MZ(L/R/B/P/T/K)024A |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | Yes
215415879 | Ground Water | COMFORT-AIRE | MZ(L/R/B/P/T/K)024A |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | Yes
215415880 | Ground Water | CENTURY | MZ(L/R/B/P/T/K)030A |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | Yes
215415881 | Ground Water | COMFORT-AIRE | MZ(L/R/B/P/T/K)030A |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | Yes
215415884 | Ground Water | CENTURY | MZ(L/R/B/P/T/K)042A |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | Yes
215415885 | Ground Water | COMFORT-AIRE | MZ(L/R/B/P/T/K)042A |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | Yes
215415886 | Ground Water | CENTURY | MZ(L/R/B/P/T/K)048A |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | Yes
215415887 | Ground Water | COMFORT-AIRE | MZ(L/R/B/P/T/K)048A |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | Yes
215415888 | Ground Water | CENTURY | MZ(L/R/B/P/T/K)060A |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | Yes
215415889 | Ground Water | COMFORT-AIRE | MZ(L/R/B/P/T/K)060A |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | Yes
215415909 | Ground Water | CENTURY | ME(L/R/B/P/D/N/T/K)024A |  | 28600 | 26.1 | 23700 | 5 | 2.3833 | Yes
215415910 | Ground Water | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)024A |  | 28600 | 26.1 | 23700 | 5 | 2.3833 | Yes
215415911 | Ground Water | CENTURY | ME(L/R/B/P/D/N/T/K)036A |  | 42000 | 23.9 | 36000 | 4.8 | 3.5 | Yes
215415912 | Ground Water | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)036A |  | 42000 | 23.9 | 36000 | 4.8 | 3.5 | Yes
215415913 | Ground Water | CENTURY | ME(L/R/B/P/D/N/T/K)048A |  | 55000 | 26 | 49100 | 4.6 | 4.5833 | Yes
215415914 | Ground Water | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)048A |  | 55000 | 26 | 49100 | 4.6 | 4.5833 | Yes
215415915 | Ground Water | CENTURY | ME(L/R/B/P/D/N/T/K)060A |  | 66800 | 24.7 | 55700 | 4.7 | 5.5667 | Yes
215415916 | Ground Water | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)060A |  | 66800 | 24.7 | 55700 | 4.7 | 5.5667 | Yes
215415917 | Ground Water | CENTURY | ME(L/R/B/P/D/N/T/K)072A |  | 78000 | 22.4 | 67400 | 4.4 | 6.5 | Yes
215415918 | Ground Water | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)072A |  | 78000 | 22.4 | 67400 | 4.4 | 6.5 | Yes
215415919 | Ground Water | Johnson Controls | BE(L/R/B/P/D/N/T/K)024A |  | 28600 | 26.1 | 23700 | 5 | 2.3833 | No
215415920 | Ground Water | SKYMARK | BE(L/R/B/P/D/N/T/K)024A |  | 28600 | 26.1 | 23700 | 5 | 2.3833 | No
215415921 | Ground Water | Johnson Controls | BE(L/R/B/P/D/N/T/K)036A |  | 42000 | 23.9 | 36000 | 4.8 | 3.5 | No
215415922 | Ground Water | SKYMARK | BE(L/R/B/P/D/N/T/K)036A |  | 42000 | 23.9 | 36000 | 4.8 | 3.5 | No
215415923 | Ground Water | Johnson Controls | BE(L/R/B/P/D/N/T/K)048A |  | 55000 | 26 | 49100 | 4.6 | 4.5833 | No
215415924 | Ground Water | SKYMARK | BE(L/R/B/P/D/N/T/K)048A |  | 55000 | 26 | 49100 | 4.6 | 4.5833 | No
215415925 | Ground Water | Johnson Controls | BE(L/R/B/P/D/N/T/K)060A |  | 66800 | 24.7 | 55700 | 4.7 | 5.5667 | No
215415926 | Ground Water | SKYMARK | BE(L/R/B/P/D/N/T/K)060A |  | 66800 | 24.7 | 55700 | 4.7 | 5.5667 | No
215415927 | Ground Water | Johnson Controls | BE(L/R/B/P/D/N/T/K)072A |  | 78000 | 22.4 | 67400 | 4.4 | 6.5 | No
215415928 | Ground Water | SKYMARK | BE(L/R/B/P/D/N/T/K)072A |  | 78000 | 22.4 | 67400 | 4.4 | 6.5 | No
215426638 | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215426639 | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215426640 | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
215429151 | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)072A*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
215429152 | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)096A |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
215429153 | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)096A*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
216625840 | Ground Water | GeoSmart Energy | S5A(V/H)048*D0**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625841 | Ground Water | GeoSmart Energy | S5A(V/H)048*D2**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625842 | Ground Water | GeoSmart Energy | S5A(V/H)048*D3**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625843 | Ground Water | GeoSmart Energy | S5A(V/H)048*D3**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625844 | Ground Water | GeoSmart Energy | S5A(V/H)048*D3**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625845 | Ground Water | GeoSmart Energy | S5A(V/H)048*D4**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625846 | Ground Water | GeoSmart Energy | S5A(V/H)048*D4**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625847 | Ground Water | GeoSmart Energy | S5A(V/H)048*D4**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625848 | Ground Water | GeoSmart Energy | S5A(V/H)048*S0**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625849 | Ground Water | GeoSmart Energy | S5A(V/H)048*S0**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625850 | Ground Water | GeoSmart Energy | S5A(V/H)048*S0**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625851 | Ground Water | GeoSmart Energy | S5A(V/H)048*S2**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625852 | Ground Water | GeoSmart Energy | S5A(V/H)048*S3**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625853 | Ground Water | GeoSmart Energy | S5A(V/H)048*S3**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625854 | Ground Water | GeoSmart Energy | S5A(V/H)048*S3**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625855 | Ground Water | GeoSmart Energy | S5A(V/H)048*S4**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625856 | Ground Water | GeoSmart Energy | S5A(V/H)048*S4**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625857 | Ground Water | GeoSmart Energy | S5A(V/H)048*S4**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625858 | Ground Water | GeoSmart Energy | S5A(V/H)060*D0**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625859 | Ground Water | GeoSmart Energy | S5A(V/H)060*D0**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625860 | Ground Water | GeoSmart Energy | S5A(V/H)060*D3**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625861 | Ground Water | GeoSmart Energy | S5A(V/H)060*D3**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625862 | Ground Water | GeoSmart Energy | S5A(V/H)060*D4**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625863 | Ground Water | GeoSmart Energy | S5A(V/H)060*D4**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625864 | Ground Water | GeoSmart Energy | S5A(V/H)060*S0**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625865 | Ground Water | GeoSmart Energy | S5A(V/H)060*S0**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625866 | Ground Water | GeoSmart Energy | S5A(V/H)060*S3**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625867 | Ground Water | GeoSmart Energy | S5A(V/H)060*S3**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625868 | Ground Water | GeoSmart Energy | S5A(V/H)060*S4**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625869 | Ground Water | GeoSmart Energy | S5A(V/H)060*S4**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625870 | Ground Water | GeoSmart Energy | S5A(V/H)072*D0**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625871 | Ground Water | GeoSmart Energy | S5A(V/H)072*D0**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
8740368 | Ground Water | GEOCOMFORT | GVS048*****1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | Yes
8740369 | Ground Water | HYDRON MODULE | HVS048*****1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | Yes
8740370 | Ground Water | TETCO | TVS048*****1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | Yes
8740371 | Ground Water | GEOCOMFORT | GVS048*2***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8740372 | Ground Water | HYDRON MODULE | HVS048*2***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8740373 | Ground Water | TETCO | TVS048*2***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8740374 | Ground Water | GEOCOMFORT | GVS048*3***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8740375 | Ground Water | HYDRON MODULE | HVS048*3***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8740376 | Ground Water | TETCO | TVS048*3***1 |  | 54900 | 26.4 | 47500 | 4.8 | 4.575 | No
8791878 | Ground Water | GEOSTAR | 101/102H060**1*(1,4)***** |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
8791879 | Ground Water | GeoSmart Energy | GS060**1*(1,4)********H |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
8791880 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS060**1*(1,4)****H |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
8791883 | Ground Water | GEOSTAR | 101/102H060**1*0***** |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
8791884 | Ground Water | GeoSmart Energy | GS060**1*0********H |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
8791885 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS060**1*0****H |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
8963989 | Ground Water | HEIL | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | No
8963990 | Ground Water | ARCOAIRE | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8963991 | Ground Water | COMFORTMAKER | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8963992 | Ground Water | DAY & NIGHT | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8963993 | Ground Water | TEMPSTAR | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8963994 | Ground Water | KEEPRITE | HS024* | FVM4X3600BL | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
10318050 | Ground Water | GEOSTAR | 103H048**1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
10318051 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS060**1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
10318052 | Ground Water | GeoSmart Energy | GSZ060*1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
10318054 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS060**1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
10318055 | Ground Water | GeoSmart Energy | GSZ060*1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
10318056 | Ground Water | GEOSTAR | 103H060**1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | Yes
10318060 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS070**1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
10318061 | Ground Water | GEOSTAR | 103H070**1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
10318062 | Ground Water | GeoSmart Energy | GSZ070*1 | SRAA060* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
10346272 | Ground Water | GEOCOMFORT | GZS006 |  | 7600 | 23.2 | 6400 | 4.3 | 0.63333 | Yes
10346273 | Ground Water | HYDRON MODULE | HZS006 |  | 7600 | 23.2 | 6400 | 4.3 | 0.63333 | Yes
10346274 | Ground Water | TETCO | TZS006 |  | 7600 | 23.2 | 6400 | 4.3 | 0.63333 | Yes
10346276 | Ground Water | GEOCOMFORT | GZS009 |  | 10500 | 22.9 | 9500 | 4.2 | 0.875 | Yes
10346277 | Ground Water | HYDRON MODULE | HZS009 |  | 10500 | 22.9 | 9500 | 4.2 | 0.875 | Yes
10346278 | Ground Water | TETCO | TZS009 |  | 10500 | 22.9 | 9500 | 4.2 | 0.875 | Yes
10346377 | Ground Water | GEOCOMFORT | GZS006*A |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10346378 | Ground Water | HYDRON MODULE | HZS006*A |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10346379 | Ground Water | TETCO | TZS006*A |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10346380 | Ground Water | GEOCOMFORT | GZS006*9 |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10346381 | Ground Water | HYDRON MODULE | HZS006*9 |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
10346382 | Ground Water | TETCO | TZS006*9 |  | 7200 | 22 | 6100 | 4.1 | 0.6 | No
205901397 | Ground Water | DUAL AIR | CFX049 |  | 43569 | 21.1 | 37280 | 4.1 | 3.6307 | Yes
205901398 | Ground Water | MIAMI HEAT PUMP | HPX049 |  | 43569 | 21.1 | 37280 | 4.1 | 3.6307 | Yes
205901399 | Ground Water | Johnson Controls | JCH/V015A B |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
205901400 | Ground Water | SKYMARK | JCH/V015A C |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
205958295 | Ground Water | BOSCH-GEO | SM036-1CS*-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | No
205958297 | Ground Water | BOSCH | SM036-1CS*-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | Yes
205961527 | Ground Water | Johnson Controls | JRE036D |  | 39800 | 21.7 | 35400 | 4.4 | 3.3167 | No
205961528 | Ground Water | Johnson Controls | JRE048D |  | 54800 | 21.1 | 48500 | 4.1 | 4.5667 | No
205961529 | Ground Water | Johnson Controls | JRE060D |  | 69800 | 23.5 | 60100 | 4.5 | 5.8167 | No
205961530 | Ground Water | Johnson Controls | JRE072D |  | 79000 | 23 | 72000 | 4.4 | 6.5833 | No
6501951 | Ground Water | GEOSTAR | GBV/GBH042**0*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501952 | Ground Water | GEOSTAR | GBV/GBH042**0*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501953 | Ground Water | GEOSTAR | GBV/GBH042**3*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
6501954 | Ground Water | GEOSTAR | GBV/GBH042**3*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501955 | Ground Water | GEOSTAR | GBV/GBH042**3*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501956 | Ground Water | GEOSTAR | GBV/GBH042**4*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
6501957 | Ground Water | GEOSTAR | GBV/GBH042**4*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501958 | Ground Water | GEOSTAR | GBV/GBH042**4*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
6501959 | Ground Water | GEOSTAR | GBV/GBH042**5*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
6501960 | Ground Water | GEOSTAR | GBV/GBH048**0*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
6501961 | Ground Water | GEOSTAR | GBV/GBH048**0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501962 | Ground Water | GEOSTAR | GBV/GBH048**0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501963 | Ground Water | GEOSTAR | GBV/GBH048**3*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
6501964 | Ground Water | GEOSTAR | GBV/GBH048**3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501965 | Ground Water | GEOSTAR | GBV/GBH048**3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501966 | Ground Water | GEOSTAR | GBV/GBH048**4*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
6501967 | Ground Water | GEOSTAR | GBV/GBH048**4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501968 | Ground Water | GEOSTAR | GBV/GBH048**4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
6501969 | Ground Water | GEOSTAR | GBV/GBH048**5*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
6501970 | Ground Water | GEOSTAR | GBV/GBH049**0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501971 | Ground Water | GEOSTAR | GBV/GBH049**0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501972 | Ground Water | GEOSTAR | GBV/GBH049**3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501973 | Ground Water | GEOSTAR | GBV/GBH049**3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501974 | Ground Water | GEOSTAR | GBV/GBH049**4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501975 | Ground Water | GEOSTAR | GBV/GBH049**4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
6501976 | Ground Water | GEOSTAR | GBV/GBH060**0*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
6501977 | Ground Water | GEOSTAR | GBV/GBH060**0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501978 | Ground Water | GEOSTAR | GBV/GBH060**0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501979 | Ground Water | GEOSTAR | GBV/GBH060**3*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
6501980 | Ground Water | GEOSTAR | GBV/GBH060**3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501981 | Ground Water | GEOSTAR | GBV/GBH060**3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501982 | Ground Water | GEOSTAR | GBV/GBH060**4*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
6501983 | Ground Water | GEOSTAR | GBV/GBH060**4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501984 | Ground Water | GEOSTAR | GBV/GBH060**4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
6501985 | Ground Water | GEOSTAR | GBV/GBH060**5*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
6501986 | Ground Water | GEOSTAR | GBV/GBH064**0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501987 | Ground Water | GEOSTAR | GBV/GBH064**0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501988 | Ground Water | GEOSTAR | GBV/GBH064**3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501989 | Ground Water | GEOSTAR | GBV/GBH064**3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501990 | Ground Water | GEOSTAR | GBV/GBH064**4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501991 | Ground Water | GEOSTAR | GBV/GBH064**4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
6501993 | Ground Water | GEOSTAR | GBV/GBH070**0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6501994 | Ground Water | GEOSTAR | GBV/GBH070**0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6501996 | Ground Water | GEOSTAR | GBV/GBH070**3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6501997 | Ground Water | GEOSTAR | GBV/GBH070**3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6501999 | Ground Water | GEOSTAR | GBV/GBH070**4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6502000 | Ground Water | GEOSTAR | GBV/GBH070**4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
6502002 | Ground Water | GEOSTAR | GBV/GBH072**0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
200083572 | Ground Water | COMFORT-AIRE | HBH/V015 |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
200083573 | Ground Water | CENTURY | HBH/V015 |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
200083574 | Ground Water | COMFORT-AIRE | HBH/V018 |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
200083575 | Ground Water | CENTURY | HBH/V018 |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
200083642 | Ground Water | COMFORT-AIRE | HZV/H/D036B |  | 42100 | 26.1 | 37900 | 5.2 | 3.5083 | Yes
200083643 | Ground Water | CENTURY | HZV/H/D036B |  | 42100 | 26.1 | 37900 | 5.2 | 3.5083 | Yes
200083644 | Ground Water | COMFORT-AIRE | HZV/H/D024B |  | 28500 | 26.4 | 25800 | 5.3 | 2.375 | Yes
200083645 | Ground Water | CENTURY | HZV/H/D024B |  | 28500 | 26.4 | 25800 | 5.3 | 2.375 | Yes
200083646 | Ground Water | COMFORT-AIRE | HZV/H/D048B |  | 55000 | 25.3 | 46800 | 4.6 | 4.5833 | Yes
216759817 | Ground Water | WaterFurnace | W5SS036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216759818 | Ground Water | WaterFurnace | W5SS048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216759819 | Ground Water | WaterFurnace | W5SS060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216759820 | Ground Water | WaterFurnace | W5SS066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216759821 | Ground Water | GEOSTAR | G5SS024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216759822 | Ground Water | GEOSTAR | G5SS036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216759823 | Ground Water | GEOSTAR | G5SS048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216759824 | Ground Water | GEOSTAR | G5SS060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216759825 | Ground Water | GEOSTAR | G5SS066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216759826 | Ground Water | WaterFurnace | W5SZ024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216759827 | Ground Water | WaterFurnace | W5SZ036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216759828 | Ground Water | WaterFurnace | W5SZ048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216759829 | Ground Water | WaterFurnace | W5SZ060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216759830 | Ground Water | WaterFurnace | W5SZ066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216759831 | Ground Water | GEOSTAR | G5SZ024BD1 | A5D(C/U)024B* | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
217967024 | Ground Water | TRANE | VSHK050A |  | 55900 | 25.5 | 54500 | 5.2 | 4.6583 | No
217967025 | Ground Water | TRANE | VSVK050A |  | 52200 | 25.9 | 51500 | 5.1 | 4.35 | No
217967026 | Ground Water | TRANE | VSHK060A |  | 63800 | 21.6 | 67400 | 4.8 | 5.3167 | No
217967027 | Ground Water | TRANE | VSVK060A |  | 62300 | 22.7 | 63700 | 5 | 5.1917 | No
217967028 | Ground Water | TRANE | VSHK024B |  | 26900 | 32.5 | 25700 | 5.6 | 2.2417 | No
217967029 | Ground Water | TRANE | VSVK024B |  | 28300 | 38.8 | 24900 | 5.6 | 2.3583 | No
217967030 | Ground Water | TRANE | VSHK033B |  | 35500 | 25.2 | 35600 | 5.1 | 2.9583 | No
217967031 | Ground Water | TRANE | VSVK033B |  | 37500 | 28.8 | 32900 | 5.3 | 3.125 | No
217967032 | Ground Water | TRANE | VSHK042B |  | 45000 | 30.2 | 41200 | 5.5 | 3.75 | No
217967033 | Ground Water | TRANE | VSVK042B |  | 46600 | 32.1 | 43400 | 5.4 | 3.8833 | No
217967034 | Ground Water | TRANE | VSHK050B |  | 55900 | 25.5 | 54500 | 5.2 | 4.6583 | No
217967035 | Ground Water | TRANE | VSVK050B |  | 52200 | 25.9 | 51500 | 5.1 | 4.35 | No
217967036 | Ground Water | TRANE | VSHK060B |  | 63800 | 21.6 | 67400 | 4.8 | 5.3167 | No
217967037 | Ground Water | TRANE | VSVK060B |  | 62300 | 22.7 | 63700 | 5 | 5.1917 | No
217967038 | Ground Water | TRANE | VSHK0244 |  | 26900 | 32.5 | 25700 | 5.6 | 2.2417 | No
217967039 | Ground Water | TRANE | VSVK0244 |  | 28300 | 38.8 | 24900 | 5.6 | 2.3583 | No
217967040 | Ground Water | TRANE | VSHK0334 |  | 35500 | 25.2 | 35600 | 5.1 | 2.9583 | No
217967041 | Ground Water | TRANE | VSVK0334 |  | 37500 | 28.8 | 32900 | 5.3 | 3.125 | No
217967042 | Ground Water | TRANE | VSHK0424 |  | 45000 | 30.2 | 41200 | 5.5 | 3.75 | No
217967043 | Ground Water | TRANE | VSVK0424 |  | 46600 | 32.1 | 43400 | 5.4 | 3.8833 | No
217967044 | Ground Water | TRANE | VSHK0504 |  | 55900 | 25.5 | 54500 | 5.2 | 4.6583 | No
217967045 | Ground Water | TRANE | VSVK0504 |  | 52200 | 25.9 | 51500 | 5.1 | 4.35 | No
217967046 | Ground Water | TRANE | VSHK0604 |  | 63800 | 21.6 | 67400 | 4.8 | 5.3167 | No
217967047 | Ground Water | TRANE | VSVK0604 |  | 62300 | 22.7 | 63700 | 5 | 5.1917 | No
214839122 | Ground Water | FHP | CL042-1HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839123 | Ground Water | FHP | CL042-1VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839124 | Ground Water | FHP | CL042-3HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839125 | Ground Water | FHP | CL042-3VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839126 | Ground Water | FHP | CL042-4HZC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
214839127 | Ground Water | FHP | CL042-4VTC****T/A*A |  | 44500 | 21.5 | 36800 | 4.6 | 3.7083 | No
216625760 | Ground Water | GeoSmart Energy | S5A(V/H)018*R2**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625761 | Ground Water | GeoSmart Energy | S5A(V/H)018*R2**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625762 | Ground Water | GeoSmart Energy | S5A(V/H)024*D0**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625763 | Ground Water | GeoSmart Energy | S5A(V/H)024*D0**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
203265288 | Ground Water | BOSCH-GEO | SM048-1VT/CFC-*****A |  | 55300 | 23.8 | 46300 | 4.45 | 4.6083 | Yes
203265289 | Ground Water | BOSCH-GEO | SM048-1VT/CFN-*****A |  | 55300 | 23.35 | 46300 | 4.3 | 4.6083 | Yes
203265290 | Ground Water | BOSCH-GEO | SM048-1HZC-*****A |  | 55300 | 24.4 | 46300 | 4.8 | 4.6083 | Yes
203265291 | Ground Water | BOSCH-GEO | SM048-1HZN-*****A |  | 55300 | 23.8 | 46300 | 4.8 | 4.6083 | Yes
203265529 | Ground Water | BOSCH | SM048-1HZC-*****A |  | 55300 | 24.4 | 46300 | 4.8 | 4.6083 | Yes
203265533 | Ground Water | BOSCH | SM048-1HZC-*****C |  | 55300 | 24.4 | 46300 | 4.8 | 4.6083 | Yes
203265538 | Ground Water | BOSCH | SM048-1HZN-*****A |  | 55300 | 23.8 | 46300 | 4.8 | 4.6083 | Yes
203265540 | Ground Water | BOSCH | SM048-1HZN-*****C |  | 55300 | 23.8 | 46300 | 4.8 | 4.6083 | Yes
203265973 | Ground Water | CARRIER | GC048V/C**C***1**1 |  | 55300 | 23.8 | 46300 | 4.45 | 4.6083 | Yes
203265976 | Ground Water | BRYANT | GC048V/C**C***1*X1 |  | 55300 | 23.8 | 46300 | 4.45 | 4.6083 | Yes
203265980 | Ground Water | CARRIER | GC048V/C**N***1**1 |  | 55300 | 23.35 | 46300 | 4.3 | 4.6083 | Yes
203265983 | Ground Water | BRYANT | GC048V/C**N***1*X1 |  | 55300 | 23.35 | 46300 | 4.3 | 4.6083 | Yes
203265987 | Ground Water | CARRIER | GC048H**C***1**1 |  | 55300 | 24.4 | 46300 | 4.8 | 4.6083 | Yes
203265989 | Ground Water | BRYANT | GC048H**C***1*X1 |  | 55300 | 24.4 | 46300 | 4.8 | 4.6083 | Yes
203265990 | Ground Water | CARRIER | GC048H**N***1**1 |  | 55300 | 23.8 | 46300 | 4.8 | 4.6083 | Yes
203265991 | Ground Water | BRYANT | GC048H**N***1*X1 |  | 55300 | 23.8 | 46300 | 4.8 | 4.6083 | Yes
203268807 | Ground Water | BOSCH | SM060-1HZ*******C |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | Yes
203303750 | Ground Water | BOSCH-GEO | CE035-1VT/HZ/CF*-*****B |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
203303751 | Ground Water | BOSCH-GEO | BP048-1HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203303773 | Ground Water | BOSCH | CE035-1VT/HZ/CF*-*****B |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303774 | Ground Water | BOSCH | BP048-1HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303777 | Ground Water | CARRIER | GB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203303778 | Ground Water | BRYANT | GB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303779 | Ground Water | HEIL | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203303780 | Ground Water | ARCOAIRE | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303781 | Ground Water | KEEPRITE | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303782 | Ground Water | TEMPSTAR | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303783 | Ground Water | COMFORTMAKER | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
208771547 | Ground Water | HYDROTECH | WSV6012B* |  | 13500 | 26 | 11000 | 4.1 | 1.125 | Yes
208771548 | Ground Water | HYDROTECH | WSV6024B* |  | 24000 | 23 | 22000 | 4.1 | 2 | Yes
208771549 | Ground Water | HYDROTECH | WSV6030B* |  | 35500 | 22.5 | 30000 | 4.1 | 2.9583 | Yes
208816675 | Ground Water | HYDROTECH | WSHXE06A6* |  | 7800 | 23.5 | 6400 | 4.3 | 0.65 | No
208816703 | Ground Water | HYDROTECH | WSHXE06A7* |  | 7800 | 23.5 | 6400 | 4.3 | 0.65 | No
208856966 | Ground Water | HYDROTECH | WSV6060B* |  | 68000 | 23.8 | 53500 | 4.3 | 5.6667 | Yes
208856967 | Ground Water | HYDROTECH | WSV6072B* |  | 77500 | 22.6 | 66000 | 4.1 | 6.4583 | Yes
208856972 | Ground Water | AE Air | WSV6012B* |  | 13500 | 26 | 11000 | 4.1 | 1.125 | Yes
208856973 | Ground Water | AE Air | WSV6024B* |  | 24000 | 23 | 22000 | 4.1 | 2 | Yes
208856974 | Ground Water | AE Air | WSV6030B* |  | 35500 | 22.5 | 30000 | 4.1 | 2.9583 | Yes
208856975 | Ground Water | AE Air | WSV6060B* |  | 68000 | 23.8 | 53500 | 4.3 | 5.6667 | Yes
208856976 | Ground Water | AE Air | WSV6072B* |  | 77500 | 22.6 | 66000 | 4.1 | 6.4583 | Yes
209156925 | Ground Water | AE Air | HRCC09*-2 |  | 11500 | 23.9 | 8800 | 4.1 | 0.95833 | No
217351696 | Ground Water | FHP | CP048-1CSC-*****A | BIVA-48RCB-M20X | 53000 | 23.1 | 47000 | 4.8 | 4.4167 | No
217351697 | Ground Water | FHP | CP048-1CSN-*****A | BIVA-48RCB-M20X | 53000 | 23.9 | 45200 | 4.9 | 4.4167 | No
217351698 | Ground Water | FHP | CP060-1CSC-*****A | BIVA-60RCB-M20X | 64200 | 21.8 | 62200 | 4.6 | 5.35 | No
217351699 | Ground Water | FHP | CP060-1CSN-*****A | BIVA-60RCB-M20X | 64000 | 22.2 | 62400 | 4.8 | 5.3333 | No
217351700 | Ground Water | FHP | CP024-1CSC-*****A | BMAC2430BBTA | 27400 | 23.2 | 23800 | 5 | 2.2833 | No
217351701 | Ground Water | FHP | CP024-1CSN-*****A | BMAC2430BBTA | 27600 | 24.3 | 23800 | 5.1 | 2.3 | No
217351702 | Ground Water | FHP | CP036-1CSC-*****A | BMAC3036BBTA | 39600 | 21.5 | 37800 | 4.8 | 3.3 | No
217351703 | Ground Water | FHP | CP036-1CSN-*****A | BMAC3036BBTA | 40200 | 22.2 | 38800 | 5 | 3.35 | No
217351704 | Ground Water | FHP | CP048-1CSC-*****A | BMAC4248CBTA | 52000 | 21.6 | 45400 | 4.5 | 4.3333 | No
217351705 | Ground Water | FHP | CP048-1CSN-*****A | BMAC4248CBTA | 53400 | 22.5 | 46600 | 4.7 | 4.45 | No
217351707 | Ground Water | FHP | CP060-1CSN-*****A | BMAC4860CBTA | 63200 | 21.1 | 59400 | 4.5 | 5.2667 | No
217351708 | Ground Water | FHP | WT025-1***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
217351709 | Ground Water | FHP | WT025-2***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
217351720 | Ground Water | FHP | WT025-3***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
217351721 | Ground Water | FHP | WT025-4***-*****C |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | No
217351730 | Ground Water | CARRIER | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
7487654 | Ground Water | TETCO | TYT036 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | Yes
7487655 | Ground Water | TETCO | TYT036*2 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487656 | Ground Water | GEOCOMFORT | GYT036*2 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487657 | Ground Water | HYDRON MODULE | HYT036*2 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487658 | Ground Water | HYDRON MODULE | HYT036*3 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487659 | Ground Water | GEOCOMFORT | GYT036*3 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487660 | Ground Water | TETCO | TYT036*3 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | No
7487661 | Ground Water | GEOCOMFORT | GYT048 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | Yes
7487662 | Ground Water | HYDRON MODULE | HYT048 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | Yes
7487663 | Ground Water | TETCO | TYT048 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | Yes
7487664 | Ground Water | TETCO | TYT048*2 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7487665 | Ground Water | HYDRON MODULE | HYT048*2 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7487666 | Ground Water | GEOCOMFORT | GYT048*2 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7487667 | Ground Water | GEOCOMFORT | GYT048*3 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7487668 | Ground Water | HYDRON MODULE | HYT048*3 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7487669 | Ground Water | TETCO | TYT048*3 |  | 57100 | 26.2 | 49500 | 5.2 | 4.7583 | No
7499543 | Ground Water | FHP | LM024-1CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7499546 | Ground Water | FHP | LM024-2CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7499547 | Ground Water | FHP | LM024-3CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7499548 | Ground Water | FHP | LM024-4CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7499550 | Ground Water | FHP | LM036-1VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7499552 | Ground Water | FHP | LM036-2VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7499553 | Ground Water | FHP | LM036-3VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7499554 | Ground Water | FHP | LM036-4VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7499556 | Ground Water | FHP | LM048-1VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7499559 | Ground Water | FHP | LM048-3VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7499560 | Ground Water | FHP | LM048-4VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7499562 | Ground Water | FHP | LM060-1VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7499565 | Ground Water | FHP | LM060-3VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7499566 | Ground Water | FHP | LM060-4VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7499569 | Ground Water | FHP | LM070-1VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7499571 | Ground Water | FHP | LM070-3VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7499572 | Ground Water | FHP | LM070-4VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7499702 | Ground Water | BOSCH | SM036-1CF/HZ/VT |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | Yes
7499719 | Ground Water | BOSCH | SM070-1CF/HZ/VT |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7519546 | Ground Water | GEOCOMFORT | GVS018*A |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | No
7519547 | Ground Water | HYDRON MODULE | HVS018*A |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | No
7519548 | Ground Water | TETCO | TVS018*A |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | No
7519549 | Ground Water | GEOCOMFORT | GVS024*A |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
7519550 | Ground Water | HYDRON MODULE | HVS024*A |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | No
215743520 | Ground Water | TRANE | GECK0062 |  | 9300 | 21.7 | 8100 | 4.5 | 0.775 | No
215743521 | Ground Water | TRANE | GECK0067 |  | 9300 | 21.7 | 8100 | 4.5 | 0.775 | No
215743522 | Ground Water | TRANE | GECK0092 |  | 9500 | 23 | 8400 | 4.5 | 0.79167 | No
215743523 | Ground Water | TRANE | GECK0097 |  | 9500 | 23 | 8400 | 4.5 | 0.79167 | No
215743524 | Ground Water | TRANE | GECK0122 |  | 13300 | 23.2 | 11600 | 4.3 | 1.1083 | No
215743525 | Ground Water | TRANE | GECK0127 |  | 13300 | 23.2 | 11600 | 4.3 | 1.1083 | No
217754991 | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217754992 | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217754993 | Ground Water | ClimateMaster | SB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217755000 | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217755001 | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217755002 | Ground Water | Enertech | FB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217755007 | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217755008 | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217755009 | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217755010 | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217755011 | Ground Water | Johnson Controls | BB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217755012 | Ground Water | SKYMARK | BB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217755019 | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217755020 | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)072B*(6/F) |  | 78000 | 21.6 | 75000 | 4.7 | 6.5 | No
217755021 | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217755022 | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)096B |  | 110500 | 22.3 | 99500 | 4.4 | 9.2083 | No
217755023 | Ground Water | CENTURY | MB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217755024 | Ground Water | COMFORT-AIRE | MB(L/R/B/P/F/C/G/H)096B*(6/F) |  | 110800 | 23 | 100000 | 4.4 | 9.2333 | No
217893588 | Ground Water | Engineered Comfort | 44VHB/VCB-19 |  | 21000 | 21.1 | 18500 | 4.1 | 1.75 | Yes
217897411 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
217897412 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
217897413 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
217897414 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
217897417 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
217897418 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215224810 | Ground Water | HEIL | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224811 | Ground Water | ARCOAIRE | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224812 | Ground Water | KEEPRITE | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224813 | Ground Water | TEMPSTAR | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224814 | Ground Water | COMFORTMAKER | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224815 | Ground Water | DAY & NIGHT | HBR18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224816 | Ground Water | HEIL | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224817 | Ground Water | ARCOAIRE | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224818 | Ground Water | KEEPRITE | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224819 | Ground Water | TEMPSTAR | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224820 | Ground Water | COMFORTMAKER | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224821 | Ground Water | DAY & NIGHT | HBR18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
7422072 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422083 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422093 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7422134 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422147 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422187 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422202 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422225 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422234 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
7422268 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7422280 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7422290 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7422299 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7422309 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7422322 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
7423168 | Ground Water | WaterFurnace | NBV/NBH026**4*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7423169 | Ground Water | GEOSTAR | GBV/GBH026**4*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7423171 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**4*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
7487652 | Ground Water | GEOCOMFORT | GYT036 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | Yes
7487653 | Ground Water | HYDRON MODULE | HYT036 |  | 44300 | 27 | 37500 | 5.5 | 3.6917 | Yes
215224599 | Ground Water | CARRIER | 50WD*007***3*(A-H)** |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224600 | Ground Water | CARRIER | 50WD*007***3*(J-R)** |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224601 | Ground Water | CARRIER | 50WD*007***4*(A-H)** |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224602 | Ground Water | CARRIER | 50WD*007***4*(J-R)** |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224603 | Ground Water | CARRIER | 50WD*009***3*(A-H)** |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224604 | Ground Water | CARRIER | 50WD*009***3*(J-R)** |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224605 | Ground Water | CARRIER | 50WD*009***4*(A-H)** |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224606 | Ground Water | CARRIER | 50WD*009***4*(J-R)** |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224607 | Ground Water | CARRIER | 50WD*012***3*(A-H)** |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224608 | Ground Water | CARRIER | 50WD*012***3*(J-R)** |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224609 | Ground Water | CARRIER | 50WD*012***4*(A-H)** |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224610 | Ground Water | CARRIER | 50WD*012***4*(J-R)** |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224611 | Ground Water | CARRIER | 50WD*015***3*(A-H)** |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224612 | Ground Water | CARRIER | 50WD*015***3*(J-R)** |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
215224613 | Ground Water | CARRIER | 50WD*015***4*(A-H)** |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224614 | Ground Water | CARRIER | 50WD*015***4*(J-R)** |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
215224615 | Ground Water | CARRIER | 50WD*018***3*(A-H)** |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224616 | Ground Water | CARRIER | 50WD*018***3*(J-R)** |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
215224617 | Ground Water | CARRIER | 50WD*018***4*(A-H)** |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224618 | Ground Water | CARRIER | 50WD*018***4*(J-R)** |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
216979853 | Ground Water | COMFORTMAKER | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979854 | Ground Water | DAY & NIGHT | HCR24H**C******1 |  | 27000 | 24 | 23000 | 4.8 | 2.25 | Yes
216979855 | Ground Water | HEIL | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979856 | Ground Water | ARCOAIRE | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979857 | Ground Water | KEEPRITE | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979858 | Ground Water | TEMPSTAR | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979859 | Ground Water | COMFORTMAKER | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979860 | Ground Water | DAY & NIGHT | HCR24H**N******1 |  | 27000 | 24 | 22500 | 4.8 | 2.25 | Yes
216979861 | Ground Water | HEIL | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979862 | Ground Water | ARCOAIRE | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979863 | Ground Water | KEEPRITE | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979864 | Ground Water | TEMPSTAR | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979865 | Ground Water | COMFORTMAKER | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979866 | Ground Water | DAY & NIGHT | HCR36V/H**C******1 |  | 40500 | 24 | 37000 | 5 | 3.375 | Yes
216979867 | Ground Water | HEIL | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979868 | Ground Water | ARCOAIRE | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979869 | Ground Water | KEEPRITE | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979870 | Ground Water | TEMPSTAR | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979871 | Ground Water | COMFORTMAKER | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979872 | Ground Water | DAY & NIGHT | HCR36V/H**N******1 |  | 40000 | 23.5 | 36500 | 5 | 3.3333 | Yes
216979873 | Ground Water | HEIL | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216979874 | Ground Water | ARCOAIRE | HCR48V/H**C******1 |  | 53500 | 23 | 48000 | 5 | 4.4583 | Yes
216625516 | Ground Water | GEOSTAR | G5A(V/H)048*S3**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625517 | Ground Water | GEOSTAR | G5A(V/H)048*S4**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625518 | Ground Water | GEOSTAR | G5A(V/H)048*D4**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625519 | Ground Water | GEOSTAR | G5A(V/H)048*D2**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625520 | Ground Water | GEOSTAR | G5A(V/H)048*D4**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625521 | Ground Water | GEOSTAR | G5A(V/H)048*D4**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625522 | Ground Water | GEOSTAR | G5A(V/H)060*S3**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625523 | Ground Water | GEOSTAR | G5A(V/H)060*S4**1 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625524 | Ground Water | GEOSTAR | G5A(V/H)060*S0**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625525 | Ground Water | GEOSTAR | G5A(V/H)060*S3**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625526 | Ground Water | GEOSTAR | G5A(V/H)060*S4**4 |  | 68000 | 25 | 59200 | 4.7 | 5.6667 | No
216625527 | Ground Water | GEOSTAR | G5A(V/H)060*D4**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625528 | Ground Water | GEOSTAR | G5A(V/H)060*D4**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216625529 | Ground Water | GEOSTAR | G5A(V/H)072*S3**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625530 | Ground Water | GEOSTAR | G5A(V/H)072*S4**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625531 | Ground Water | GEOSTAR | G5A(V/H)072*S0**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625532 | Ground Water | GEOSTAR | G5A(V/H)072*S3**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625533 | Ground Water | GEOSTAR | G5A(V/H)072*S4**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625534 | Ground Water | GEOSTAR | G5A(V/H)072*D4**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625535 | Ground Water | GEOSTAR | G5A(V/H)072*D4**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625542 | Ground Water | GEOSTAR | G5A(V/H)042*S4**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625543 | Ground Water | GEOSTAR | G5A(V/H)042*S2**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625614 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)009*R0**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216625615 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)009*R2**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216625616 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)012*R0**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
216625617 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)012*R2**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
216625618 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R0**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625619 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R0**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625620 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R2**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625621 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R2**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625622 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*D0**1 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216625623 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*D0**4 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
216625624 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R0**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625625 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R0**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625626 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R2**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625627 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R2**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625628 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D0**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625629 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D0**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625630 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D2**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625631 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D2**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625632 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D3**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625633 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D3**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625634 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D4**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625635 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D4**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625636 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S0**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625637 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S0**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625638 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S2**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625639 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S2**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625640 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S3**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625641 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S3**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625642 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S4**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625643 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S4**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625644 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D0**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625645 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D0**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
214067603 | Ground Water | GeoSmart Energy | GBV/GBH070**4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214067604 | Ground Water | GeoSmart Energy | GBV/GBH070**4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
214067606 | Ground Water | GeoSmart Energy | GBV/GBH072**3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214067607 | Ground Water | GeoSmart Energy | GBV/GBH072**3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214067608 | Ground Water | GeoSmart Energy | GBV/GBH072**4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214067609 | Ground Water | GeoSmart Energy | GBV/GBH072**4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214067865 | Ground Water | GeoSmart Energy | GBV/GBH048**3*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
214067866 | Ground Water | GeoSmart Energy | GBV/GBH048**3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214067867 | Ground Water | GeoSmart Energy | GBV/GBH048**3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214067868 | Ground Water | GeoSmart Energy | GBV/GBH009**0*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
214067869 | Ground Water | GeoSmart Energy | GBV/GBH042**0*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
214067870 | Ground Water | GeoSmart Energy | GBV/GBH048**0*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
214067871 | Ground Water | GeoSmart Energy | GBV/GBH048**0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214067872 | Ground Water | GeoSmart Energy | GBV/GBH048**0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
214595542 | Ground Water | AAON, Inc. | RQ-003-2-0-GCAY-V0-10-000-A |  | 42600 | 22.6 | 35600 | 4.2 | 3.55 | No
214595543 | Ground Water | AAON, Inc. | RQ-003-3-0-GCAY-V0-10-000-A |  | 42600 | 22.6 | 35600 | 4.2 | 3.55 | No
214595544 | Ground Water | AAON, Inc. | RQ-003-4-0-GCAY-V0-10-000-A |  | 42600 | 22.6 | 35600 | 4.2 | 3.55 | No
214595548 | Ground Water | AAON, Inc. | RQ-004-1-0-FCAY-S0-10-000-A |  | 53000 | 21.4 | 42900 | 4.5 | 4.4167 | No
214595549 | Ground Water | AAON, Inc. | RQ-004-2-0-GCAY-V0-10-000-A |  | 54000 | 23 | 43600 | 4.5 | 4.5 | No
214595550 | Ground Water | AAON, Inc. | RQ-004-3-0-GCAY-V0-10-000-A |  | 54000 | 23 | 43600 | 4.5 | 4.5 | No
214595551 | Ground Water | AAON, Inc. | RQ-004-4-0-GCAY-V0-10-000-A |  | 54000 | 23 | 43600 | 4.5 | 4.5 | No
214595552 | Ground Water | AAON, Inc. | RQ-004-2-0-FCAY-S0-10-000-A |  | 53000 | 21.4 | 42900 | 4.5 | 4.4167 | No
214595553 | Ground Water | AAON, Inc. | RQ-004-3-0-FCAY-S0-10-000-A |  | 53000 | 21.4 | 42900 | 4.5 | 4.4167 | No
214595554 | Ground Water | AAON, Inc. | RQ-004-4-0-FCAY-S0-10-000-A |  | 53000 | 21.4 | 42900 | 4.5 | 4.4167 | No
214595555 | Ground Water | AAON, Inc. | RQ-005-1-0-FCAY-S0-10-000-A |  | 61500 | 21.9 | 50900 | 4.5 | 5.125 | No
214595556 | Ground Water | AAON, Inc. | RQ-005-2-0-GCAY-V0-10-000-A |  | 66900 | 21.6 | 54200 | 4.3 | 5.575 | No
214595557 | Ground Water | AAON, Inc. | RQ-005-3-0-GCAY-V0-10-000-A |  | 66900 | 21.6 | 54200 | 4.3 | 5.575 | No
214595558 | Ground Water | AAON, Inc. | RQ-005-4-0-GCAY-V0-10-000-A |  | 66900 | 21.6 | 54200 | 4.3 | 5.575 | No
214595559 | Ground Water | AAON, Inc. | RQ-005-2-0-FCAY-S0-10-000-A |  | 61500 | 21.9 | 50900 | 4.5 | 5.125 | No
214595560 | Ground Water | AAON, Inc. | RQ-005-3-0-FCAY-S0-10-000-A |  | 61500 | 21.9 | 50900 | 4.5 | 5.125 | No
214595561 | Ground Water | AAON, Inc. | RQ-005-4-0-FCAY-S0-10-000-A |  | 61500 | 21.9 | 50900 | 4.5 | 5.125 | No
214595562 | Ground Water | AAON, Inc. | RN-006-2-0-FCAY-S0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
214595563 | Ground Water | AAON, Inc. | RN-006-3-0-FCAY-S0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
214595564 | Ground Water | AAON, Inc. | RN-006-4-0-FCAY-S0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
214595565 | Ground Water | AAON, Inc. | RN-006-2-0-GCAY-V0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
214595566 | Ground Water | AAON, Inc. | RN-006-3-0-GCAY-V0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
214595567 | Ground Water | AAON, Inc. | RN-006-4-0-GCAY-V0-10-000-A |  | 63300 | 21.8 | 50100 | 4.1 | 5.275 | No
217897450 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
217897451 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
217897452 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
217897453 | Ground Water | CENTURY | MR(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
217897454 | Ground Water | COMFORT-AIRE | MR(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
217897455 | Ground Water | CENTURY | MJN024A | MKN024A | 24700 | 23.6 | 22800 | 4.6 | 2.0583 | Yes
217897456 | Ground Water | COMFORT-AIRE | MJN024A | MKN024A | 24700 | 23.6 | 22800 | 4.6 | 2.0583 | Yes
217897457 | Ground Water | CENTURY | MJN036A | MKN036A | 41000 | 23.6 | 33200 | 4.4 | 3.4167 | Yes
217897458 | Ground Water | COMFORT-AIRE | MJN036A | MKN036A | 41000 | 23.6 | 33200 | 4.4 | 3.4167 | Yes
217897463 | Ground Water | CENTURY | MJN024A | MAN024A | 24700 | 25.2 | 22500 | 4.8 | 2.0583 | Yes
217897464 | Ground Water | COMFORT-AIRE | MJN024A | MAN024A | 24700 | 25.2 | 22500 | 4.8 | 2.0583 | Yes
217897465 | Ground Water | CENTURY | MJN036A | MAN036A | 41800 | 25 | 33700 | 4.7 | 3.4833 | Yes
217897466 | Ground Water | COMFORT-AIRE | MJN036A | MAN036A | 41800 | 25 | 33700 | 4.7 | 3.4833 | Yes
217897467 | Ground Water | CENTURY | MJN048A | MAN048A | 51900 | 22.2 | 46000 | 4.4 | 4.325 | Yes
217897468 | Ground Water | COMFORT-AIRE | MJN048A | MAN048A | 51900 | 22.2 | 46000 | 4.4 | 4.325 | Yes
217897469 | Ground Water | CENTURY | MJN060A | MAN060A | 65000 | 22.9 | 55100 | 4.3 | 5.4167 | Yes
217897470 | Ground Water | COMFORT-AIRE | MJN060A | MAN060A | 65000 | 22.9 | 55100 | 4.3 | 5.4167 | Yes
217897473 | Ground Water | CENTURY | MWM060A |  | 58700 | 23.4 | 57900 | 4.1 | 4.8917 | Yes
217897474 | Ground Water | COMFORT-AIRE | MWM060A |  | 58700 | 23.4 | 57900 | 4.1 | 4.8917 | Yes
10384616 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ070H1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | Yes
10384620 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ072H1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
10384621 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS072H1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10435611 | Ground Water | GEOSTAR | 103H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
10435612 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10435613 | Ground Water | GeoSmart Energy | GTZ072*1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | Yes
10435614 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS070**1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | No
10435615 | Ground Water | GEOSTAR | 103H070**1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | Yes
10435616 | Ground Water | GeoSmart Energy | GSZ070*1 | SAH066* | 66400 | 21.7 | 62100 | 4.1 | 5.5333 | Yes
10435617 | Ground Water | GEOSTAR | 104H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10435618 | Ground Water | YORK BY JOHNSON CONTROLS | YAST072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10435619 | Ground Water | GeoSmart Energy | GTS072*1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10581121 | Ground Water | GEOSTAR | 107H064**1*1 |  | 67500 | 23.1 | 58200 | 4.5 | 5.625 | No
202147010 | Ground Water | TETCO | TZS036*2 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147011 | Ground Water | TETCO | TZS036*3 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147012 | Ground Water | TETCO | TZS036*4 |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147013 | Ground Water | TETCO | TZS036*A |  | 39500 | 24.1 | 34800 | 4.4 | 3.2917 | No
202147014 | Ground Water | TETCO | TZS036*****1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | Yes
202147015 | Ground Water | TETCO | TZS036*2***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147016 | Ground Water | TETCO | TZS036*3***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147017 | Ground Water | TETCO | TZS036*A***1 |  | 39500 | 24.7 | 33600 | 4.6 | 3.2917 | No
202147018 | Ground Water | GEOCOMFORT | GZS042 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | Yes
202147019 | Ground Water | GEOCOMFORT | GZS042*2 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147020 | Ground Water | GEOCOMFORT | GZS042*3 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147021 | Ground Water | GEOCOMFORT | GZS042*4 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147022 | Ground Water | GEOCOMFORT | GZS042*****1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | Yes
202147023 | Ground Water | GEOCOMFORT | GZS042*2***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147024 | Ground Water | HYDRON MODULE | HZS042 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | Yes
202147025 | Ground Water | HYDRON MODULE | HZS042*2 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147026 | Ground Water | HYDRON MODULE | HZS042*3 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147027 | Ground Water | HYDRON MODULE | HZS042*4 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147028 | Ground Water | HYDRON MODULE | HZS042*****1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | Yes
202147029 | Ground Water | HYDRON MODULE | HZS042*2***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147030 | Ground Water | TETCO | TZS042 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | Yes
202147031 | Ground Water | TETCO | TZS042*2 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147032 | Ground Water | TETCO | TZS042*3 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147033 | Ground Water | TETCO | TZS042*4 |  | 44200 | 23.7 | 38900 | 4.5 | 3.6833 | No
202147034 | Ground Water | TETCO | TZS042*****1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | Yes
202147035 | Ground Water | TETCO | TZS042*2***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
202147036 | Ground Water | GEOCOMFORT | GZS048 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | Yes
202147037 | Ground Water | GEOCOMFORT | GZS048*2 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
202147038 | Ground Water | GEOCOMFORT | GZS048*3 |  | 52100 | 22.4 | 46800 | 4.2 | 4.3417 | No
206438869 | Ground Water | CARRIER | 50PSH/V007***4/DA* |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438870 | Ground Water | CARRIER | 50PSH/V007***3/CA* |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438871 | Ground Water | CARRIER | 50PSH/V009***3/CA* |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438872 | Ground Water | CARRIER | 50PSH/V009***4/DA* |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438873 | Ground Water | CARRIER | 50PSH/V012***3/CA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438874 | Ground Water | CARRIER | 50PSH/V015***3/CA* |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438875 | Ground Water | CARRIER | 50PSH/V015***4/DA* |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438876 | Ground Water | CARRIER | 50PSH/V030***4/DA* |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438877 | Ground Water | CARRIER | 50PSH/V030***6/FA* |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438878 | Ground Water | CARRIER | 50PSH/V030***5/EA* |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438879 | Ground Water | CARRIER | 50PSH/V030***3/CA* |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438880 | Ground Water | CARRIER | 50PSH/V060***6/FA* |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438881 | Ground Water | CARRIER | 50PSH/V060***5/EA* |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438882 | Ground Water | CARRIER | 50PSH/V060***3/CA* |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438883 | Ground Water | CARRIER | 50PSH/V070***3/CA* |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438884 | Ground Water | CARRIER | 50PSH/V070***5/EA* |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438885 | Ground Water | CARRIER | 50PSH/V070***6/FA* |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438903 | Ground Water | CARRIER | 50PSV012**C3/CA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438904 | Ground Water | CARRIER | 50PSH012**C3/CA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438905 | Ground Water | CARRIER | 50PSV012**N3/CA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438906 | Ground Water | CARRIER | 50PSH012**N3/CA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438907 | Ground Water | CARRIER | 50PSV012**C0/BA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438908 | Ground Water | CARRIER | 50PSV012**C4/DA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438909 | Ground Water | CARRIER | 50PSH012**C0/BA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438910 | Ground Water | CARRIER | 50PSH012**C4/DA* |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438911 | Ground Water | CARRIER | 50PSV012**N0/BA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438912 | Ground Water | CARRIER | 50PSV012**N4/DA* |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
216621339 | Ground Water | GEOSTAR | G5A(V/H)036*D0**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621340 | Ground Water | GEOSTAR | G5A(V/H)036*D3**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621341 | Ground Water | GEOSTAR | G5A(V/H)036*D0**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621342 | Ground Water | GEOSTAR | G5A(V/H)036*D3**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216621343 | Ground Water | GEOSTAR | G5A(V/H)042*D0**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621344 | Ground Water | GEOSTAR | G5A(V/H)042*D3**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621345 | Ground Water | GEOSTAR | G5A(V/H)042*D0**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621346 | Ground Water | GEOSTAR | G5A(V/H)042*D3**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621347 | Ground Water | GEOSTAR | G5A(V/H)042*D0**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621348 | Ground Water | GEOSTAR | G5A(V/H)042*D3**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216621349 | Ground Water | GEOSTAR | G5A(V/H)048*D0**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621350 | Ground Water | GEOSTAR | G5A(V/H)048*D3**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621351 | Ground Water | GEOSTAR | G5A(V/H)048*D0**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621352 | Ground Water | GEOSTAR | G5A(V/H)048*D3**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621353 | Ground Water | GEOSTAR | G5A(V/H)048*D0**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621354 | Ground Water | GEOSTAR | G5A(V/H)048*D3**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216621355 | Ground Water | GEOSTAR | G5A(V/H)060*D0**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216621356 | Ground Water | GEOSTAR | G5A(V/H)060*D3**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216621357 | Ground Water | GEOSTAR | G5A(V/H)060*D0**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216621358 | Ground Water | GEOSTAR | G5A(V/H)060*D3**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
216621359 | Ground Water | GEOSTAR | G5A(V/H)072*D0**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216621360 | Ground Water | GEOSTAR | G5A(V/H)072*D3**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216621361 | Ground Water | GEOSTAR | G5A(V/H)072*D0**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216621362 | Ground Water | GEOSTAR | G5A(V/H)072*D3**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
216625455 | Ground Water | GEOSTAR | G5A(V/H)009*R2**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
216625456 | Ground Water | GEOSTAR | G5A(V/H)012*R2**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
216625457 | Ground Water | GEOSTAR | G5A(V/H)015*R2**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625458 | Ground Water | GEOSTAR | G5A(V/H)015*R0**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
216625459 | Ground Water | GEOSTAR | G5A(V/H)015*R2**4 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
215268334 | Ground Water | WaterFurnace | V3A(V/H)024*S0**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268335 | Ground Water | WaterFurnace | V3A(V/H)024*S2**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268336 | Ground Water | WaterFurnace | V3A(V/H)024*S2**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268337 | Ground Water | WaterFurnace | V3A(V/H)024*S3**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268338 | Ground Water | WaterFurnace | V3A(V/H)024*S3**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268339 | Ground Water | WaterFurnace | V3A(V/H)024*S4**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268340 | Ground Water | WaterFurnace | V3A(V/H)024*S4**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
215268348 | Ground Water | WaterFurnace | V3A(V/H)036*S0**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268349 | Ground Water | WaterFurnace | V3A(V/H)036*S2**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268350 | Ground Water | WaterFurnace | V3A(V/H)036*S2**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268351 | Ground Water | WaterFurnace | V3A(V/H)036*S3**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268352 | Ground Water | WaterFurnace | V3A(V/H)036*S3**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268353 | Ground Water | WaterFurnace | V3A(V/H)036*S4**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268354 | Ground Water | WaterFurnace | V3A(V/H)036*S4**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
215268355 | Ground Water | WaterFurnace | V3A(V/H)042*S0**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268356 | Ground Water | WaterFurnace | V3A(V/H)042*S3**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268357 | Ground Water | WaterFurnace | V3A(V/H)042*S3**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268358 | Ground Water | WaterFurnace | V3A(V/H)042*S4**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268359 | Ground Water | WaterFurnace | V3A(V/H)042*S4**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
215268365 | Ground Water | WaterFurnace | V3A(V/H)060*S0**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268366 | Ground Water | WaterFurnace | V3A(V/H)060*S3**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268367 | Ground Water | WaterFurnace | V3A(V/H)060*S3**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268368 | Ground Water | WaterFurnace | V3A(V/H)060*S4**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268369 | Ground Water | WaterFurnace | V3A(V/H)060*S4**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
215268663 | Ground Water | WaterFurnace | V5A(V/H)009*R0**6 |  | 12000 | 23.1 | 10000 | 4.1 | 1 | No
215268664 | Ground Water | WaterFurnace | V5A(V/H)012*R0**6 |  | 14000 | 26 | 12400 | 4.3 | 1.1667 | No
215268665 | Ground Water | WaterFurnace | V5A(V/H)015*R0**1 |  | 17000 | 28 | 16000 | 4.9 | 1.4167 | No
215268666 | Ground Water | WaterFurnace | V5A(V/H)018*R0**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
215268667 | Ground Water | WaterFurnace | V5A(V/H)024*S0**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
215268668 | Ground Water | WaterFurnace | V5A(V/H)030*S0**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
217642898 | Ground Water | GeoSmart Energy | S3A(V/H)024*S2**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642899 | Ground Water | GeoSmart Energy | S3A(V/H)024*S2**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642900 | Ground Water | GeoSmart Energy | S3A(V/H)024*S3**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642901 | Ground Water | GeoSmart Energy | S3A(V/H)024*S3**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642902 | Ground Water | GeoSmart Energy | S3A(V/H)024*S4**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642903 | Ground Water | GeoSmart Energy | S3A(V/H)024*S4**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642911 | Ground Water | GeoSmart Energy | S3A(V/H)036*S0**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642912 | Ground Water | GeoSmart Energy | S3A(V/H)036*S2**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642913 | Ground Water | GeoSmart Energy | S3A(V/H)036*S2**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642914 | Ground Water | GeoSmart Energy | S3A(V/H)036*S3**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642915 | Ground Water | GeoSmart Energy | S3A(V/H)036*S3**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642916 | Ground Water | GeoSmart Energy | S3A(V/H)036*S4**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642917 | Ground Water | GeoSmart Energy | S3A(V/H)036*S4**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642918 | Ground Water | GeoSmart Energy | S3A(V/H)042*S0**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642919 | Ground Water | GeoSmart Energy | S3A(V/H)042*S3**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642920 | Ground Water | GeoSmart Energy | S3A(V/H)042*S3**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642921 | Ground Water | GeoSmart Energy | S3A(V/H)042*S4**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642922 | Ground Water | GeoSmart Energy | S3A(V/H)042*S4**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
204835632 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ038J1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
204835633 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS038J1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
205129920 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ036J1 | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
205129921 | Ground Water | GEOSTAR | 103J036**1 | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
205145424 | Ground Water | GEOCOMFORT | GVT030*****1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
205145425 | Ground Water | GEOCOMFORT | GVT030*2***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145426 | Ground Water | GEOCOMFORT | GVT030*3***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145427 | Ground Water | HYDRON MODULE | HVT030*****1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
205145428 | Ground Water | HYDRON MODULE | HVT030*2***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145429 | Ground Water | HYDRON MODULE | HVT030*3***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145430 | Ground Water | TETCO | TVT030*****1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
205145431 | Ground Water | TETCO | TVT030*2***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145432 | Ground Water | TETCO | TVT030*3***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145433 | Ground Water | GEOCOMFORT | GVT042*****1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
205145434 | Ground Water | GEOCOMFORT | GVT042*2***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205145435 | Ground Water | GEOCOMFORT | GVT042*3***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205145436 | Ground Water | HYDRON MODULE | HVT042*****1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
205145437 | Ground Water | HYDRON MODULE | HVT042*2***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205145438 | Ground Water | HYDRON MODULE | HVT042*3***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205145439 | Ground Water | TETCO | TVT042*2***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205145527 | Ground Water | GEOCOMFORT | GVT030*A***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145528 | Ground Water | HYDRON MODULE | HVT030*A***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145529 | Ground Water | TETCO | TVT030*A***1 |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | No
205145530 | Ground Water | TETCO | TVT042*****1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
205145531 | Ground Water | TETCO | TVT042*3***1 |  | 49200 | 24 | 40100 | 4.6 | 4.1 | No
205148067 | Ground Water | HYDROTECH | WSV6060A |  | 65000 | 23 | 53500 | 4.1 | 5.4167 | No
214063737 | Ground Water | GeoSmart Energy | GBV/GBH009**2*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
214063738 | Ground Water | GeoSmart Energy | GBV/GBH012**0*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
214063739 | Ground Water | GeoSmart Energy | GBV/GBH012**2*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
214063740 | Ground Water | GeoSmart Energy | GBV/GBH015**0*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
214063741 | Ground Water | GeoSmart Energy | GBV/GBH015**0*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
214063742 | Ground Water | GeoSmart Energy | GBV/GBH015**0*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
214063743 | Ground Water | GeoSmart Energy | GBV/GBH015**2*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
214063744 | Ground Water | GeoSmart Energy | GBV/GBH015**2*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
214063745 | Ground Water | GeoSmart Energy | GBV/GBH015**2*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
214063746 | Ground Water | GeoSmart Energy | GBV/GBH018**0*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
214063747 | Ground Water | GeoSmart Energy | GBV/GBH018**0*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
214063748 | Ground Water | GeoSmart Energy | GBV/GBH018**0*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
214063749 | Ground Water | GeoSmart Energy | GBV/GBH018**2*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
214063750 | Ground Water | GeoSmart Energy | GBV/GBH018**2*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
214063751 | Ground Water | GeoSmart Energy | GBV/GBH018**2*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
214063752 | Ground Water | GeoSmart Energy | GBV/GBH024**0*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
214063753 | Ground Water | GeoSmart Energy | GBV/GBH024**0*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214063754 | Ground Water | GeoSmart Energy | GBV/GBH024**0*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
214063755 | Ground Water | GeoSmart Energy | GBV/GBH024**2*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
8964157 | Ground Water | BRYANT | GC036C/H/V******1*X1 + UI |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | Yes
8964158 | Ground Water | CARRIER | GC036C/H/V******1**1 + UI |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | Yes
8964161 | Ground Water | BRYANT | GC060C/H/V******1*X1 + UI |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | Yes
8964162 | Ground Water | CARRIER | GC060C/H/V******1**1 + UI |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | Yes
8964163 | Ground Water | BRYANT | GC072C/H/V******1*X1 + UI |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | Yes
8964164 | Ground Water | CARRIER | GC072C/H/V******1**1 + UI |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | Yes
207349053 | Ground Water | WaterFurnace | NCC/NCW/NCS/NCE15*0 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
207349059 | Ground Water | WaterFurnace | NCC/NCW/NCS/NCE15*2 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
207349379 | Ground Water | WaterFurnace | NBV/NBH026**0*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349380 | Ground Water | WaterFurnace | NBV/NBH026**3*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349381 | Ground Water | WaterFurnace | NBV/NBH026**2*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349382 | Ground Water | WaterFurnace | NBV/NBH026**4*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349383 | Ground Water | WaterFurnace | NBV/NBH026**0*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349384 | Ground Water | WaterFurnace | NBV/NBH026**3*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349385 | Ground Water | WaterFurnace | NBV/NBH026**4*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349386 | Ground Water | WaterFurnace | NBV/NBH026**2*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207349387 | Ground Water | WaterFurnace | NBV/NBH038**0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349388 | Ground Water | WaterFurnace | NBV/NBH038**3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349389 | Ground Water | WaterFurnace | NBV/NBH038**2*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349390 | Ground Water | WaterFurnace | NBV/NBH038**4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349391 | Ground Water | WaterFurnace | NBV/NBH038**0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349392 | Ground Water | WaterFurnace | NBV/NBH038**3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349393 | Ground Water | WaterFurnace | NBV/NBH038**4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349394 | Ground Water | WaterFurnace | NBV/NBH038**2*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207349395 | Ground Water | WaterFurnace | NBV/NBH049**0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349396 | Ground Water | WaterFurnace | NBV/NBH049**3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349397 | Ground Water | WaterFurnace | NBV/NBH049**4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349398 | Ground Water | WaterFurnace | NBV/NBH049**0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349399 | Ground Water | WaterFurnace | NBV/NBH049**3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349400 | Ground Water | WaterFurnace | NBV/NBH049**4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207349401 | Ground Water | WaterFurnace | NBV/NBH064**0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349402 | Ground Water | WaterFurnace | NBV/NBH064**3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349403 | Ground Water | WaterFurnace | NBV/NBH064**4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
7167551 | Ground Water | CARRIER | 50PTD/H/V060***6/FA |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7167552 | Ground Water | CARRIER | 50PTD/H/V070***3/CA |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7167553 | Ground Water | CARRIER | 50PTD/H/V070***5/EA |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7167554 | Ground Water | CARRIER | 50PTD/H/V070***6/FA |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7170602 | Ground Water | GEOCOMFORT | GVS018 |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | Yes
7170603 | Ground Water | HYDRON MODULE | HVS018 |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | Yes
7170604 | Ground Water | TETCO | TVS018 |  | 23200 | 27.5 | 20100 | 5 | 1.9333 | Yes
7170606 | Ground Water | GEOCOMFORT | GVS024 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | Yes
7170607 | Ground Water | HYDRON MODULE | HVS024 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | Yes
7170608 | Ground Water | TETCO | TVS024 |  | 28100 | 26 | 24200 | 4.9 | 2.3417 | Yes
7170609 | Ground Water | GEOCOMFORT | GVS030 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | Yes
7170610 | Ground Water | HYDRON MODULE | HVS030 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | Yes
7170611 | Ground Water | TETCO | TVS030 |  | 31000 | 23.4 | 28700 | 4.7 | 2.5833 | Yes
7170612 | Ground Water | GEOCOMFORT | GVS036 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | Yes
7170613 | Ground Water | HYDRON MODULE | HVS036 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | Yes
7170614 | Ground Water | TETCO | TVS036 |  | 40500 | 23.5 | 37600 | 4.6 | 3.375 | Yes
7785665 | Ground Water | DAIKIN | WVHW3021*J (W/ECM MOTOR) |  | 24100 | 23.2 | 19900 | 4.2 | 2.0083 | No
7795914 | Ground Water | GEOCOMFORT | GVT024 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
7795915 | Ground Water | HYDRON MODULE | HVT024 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
7795916 | Ground Water | TETCO | TVT024 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
7795918 | Ground Water | GEOCOMFORT | GVT024*2 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795919 | Ground Water | HYDRON MODULE | HVT024*2 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795920 | Ground Water | TETCO | TVT024*2 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795921 | Ground Water | GEOCOMFORT | GVT024*3 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795922 | Ground Water | HYDRON MODULE | HVT024*3 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795923 | Ground Water | TETCO | TVT024*3 |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795924 | Ground Water | GEOCOMFORT | GVT024*A |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795925 | Ground Water | HYDRON MODULE | HVT024*A |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
203303784 | Ground Water | DAY & NIGHT | HB048H******1**1 |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | Yes
203303785 | Ground Water | CARRIER | GP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
203303786 | Ground Water | BRYANT | GP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303787 | Ground Water | HEIL | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | No
203303788 | Ground Water | ARCOAIRE | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303789 | Ground Water | KEEPRITE | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303790 | Ground Water | TEMPSTAR | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303791 | Ground Water | COMFORTMAKER | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203303792 | Ground Water | DAY & NIGHT | HP036V/H/C******1**1 |  | 42000 | 21.25 | 36000 | 4.2 | 3.5 | Yes
203337768 | Ground Water | BOSCH-GEO | CE025-1VT/HZ/CF*-*****B |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
203337769 | Ground Water | BOSCH | CE025-1VT/HZ/CF*-*****B |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337770 | Ground Water | CARRIER | GP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
203337771 | Ground Water | BRYANT | GP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337772 | Ground Water | HEIL | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | No
203337773 | Ground Water | ARCOAIRE | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337774 | Ground Water | KEEPRITE | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337775 | Ground Water | TEMPSTAR | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337776 | Ground Water | COMFORTMAKER | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203337777 | Ground Water | DAY & NIGHT | HP024V/H/C******1**1 |  | 29000 | 23.2 | 23400 | 4.5 | 2.4167 | Yes
203343532 | Ground Water | BOSCH-GEO | SM024-1CS*******A | SM024-1AV/AH*-*****A | 28500 | 22.2 | 22200 | 4.5 | 2.375 | Yes
203343535 | Ground Water | BOSCH | SM024-1CS*******A | SM024-1AV/AH*-*****A | 28500 | 22.2 | 22200 | 4.5 | 2.375 | Yes
4504310 | Ground Water | BOSCH-GEO | BP012-1HZ/VT |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
4509712 | Ground Water | BOSCH-GEO | BP024-1HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
4510474 | Ground Water | BOSCH-GEO | BP030-1HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
4547265 | Ground Water | DUAL AIR | CFX024 |  | 22804 | 21.1 | 18640 | 4.1 | 1.9003 | Yes
4547266 | Ground Water | DUAL AIR | CFX031 |  | 32445 | 21.1 | 24698 | 4.1 | 2.7037 | Yes
4547267 | Ground Water | DUAL AIR | CFX036 |  | 32908 | 21.1 | 29358 | 4.1 | 2.7423 | Yes
4547268 | Ground Water | DUAL AIR | CFX041 |  | 37543 | 21.1 | 34484 | 4.1 | 3.1286 | Yes
4547869 | Ground Water | MIAMI HEAT PUMP | HPX024 |  | 22804 | 21.1 | 18640 | 4.1 | 1.9003 | Yes
4547870 | Ground Water | MIAMI HEAT PUMP | HPX031 |  | 32445 | 21.1 | 24698 | 4.1 | 2.7037 | Yes
4547871 | Ground Water | MIAMI HEAT PUMP | HPX036 |  | 32908 | 21.1 | 29358 | 4.1 | 2.7423 | Yes
4547872 | Ground Water | MIAMI HEAT PUMP | HPX041 |  | 37543 | 21.1 | 34484 | 4.1 | 3.1286 | Yes
4651271 | Ground Water | WaterFurnace | USH023**0*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651272 | Ground Water | WaterFurnace | USH023**2*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651273 | Ground Water | WaterFurnace | USH023**3*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
206422420 | Ground Water | COMFORT-AIRE | HBH/V018*W/K |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
206422421 | Ground Water | CENTURY | HBH/V024*W/K |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
206422422 | Ground Water | COMFORT-AIRE | HBH/V024*W/K |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
206422423 | Ground Water | CENTURY | HBH/V030*W/K |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
206422424 | Ground Water | COMFORT-AIRE | HBH/V030*W/K |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
216625460 | Ground Water | GEOSTAR | G5A(V/H)018*R2**1 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625461 | Ground Water | GEOSTAR | G5A(V/H)018*R0**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625462 | Ground Water | GEOSTAR | G5A(V/H)018*R2**4 |  | 20600 | 25 | 18500 | 4.6 | 1.7167 | No
216625463 | Ground Water | GEOSTAR | G5A(V/H)024*S2**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625464 | Ground Water | GEOSTAR | G5A(V/H)024*S3**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625465 | Ground Water | GEOSTAR | G5A(V/H)024*S4**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625466 | Ground Water | GEOSTAR | G5A(V/H)024*S0**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625467 | Ground Water | GEOSTAR | G5A(V/H)024*S2**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625468 | Ground Water | GEOSTAR | G5A(V/H)024*S3**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625469 | Ground Water | GEOSTAR | G5A(V/H)024*S4**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625470 | Ground Water | GEOSTAR | G5A(V/H)030*S2**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625471 | Ground Water | GEOSTAR | G5A(V/H)030*S3**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625472 | Ground Water | GEOSTAR | G5A(V/H)030*S4**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625473 | Ground Water | GEOSTAR | G5A(V/H)030*S0**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625474 | Ground Water | GEOSTAR | G5A(V/H)030*S2**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625475 | Ground Water | GEOSTAR | G5A(V/H)030*S3**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625476 | Ground Water | GEOSTAR | G5A(V/H)030*S4**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625477 | Ground Water | GEOSTAR | G5A(V/H)030*D2**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625478 | Ground Water | GEOSTAR | G5A(V/H)030*D4**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625479 | Ground Water | GEOSTAR | G5A(V/H)030*D2**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625480 | Ground Water | GEOSTAR | G5A(V/H)030*D4**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625481 | Ground Water | GEOSTAR | G5A(V/H)036*S2**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625482 | Ground Water | GEOSTAR | G5A(V/H)036*S3**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625483 | Ground Water | GEOSTAR | G5A(V/H)036*S4**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625484 | Ground Water | GEOSTAR | G5A(V/H)036*S0**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625485 | Ground Water | GEOSTAR | G5A(V/H)036*S2**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625486 | Ground Water | GEOSTAR | G5A(V/H)036*S3**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625487 | Ground Water | GEOSTAR | G5A(V/H)036*S4**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625488 | Ground Water | GEOSTAR | G5A(V/H)036*S0**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625489 | Ground Water | GEOSTAR | G5A(V/H)036*S2**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625490 | Ground Water | GEOSTAR | G5A(V/H)036*S3**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625491 | Ground Water | GEOSTAR | G5A(V/H)036*S4**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625492 | Ground Water | GEOSTAR | G5A(V/H)036*D2**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625493 | Ground Water | GEOSTAR | G5A(V/H)036*D4**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625494 | Ground Water | GEOSTAR | G5A(V/H)036*D2**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625495 | Ground Water | GEOSTAR | G5A(V/H)036*D4**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625496 | Ground Water | GEOSTAR | G5A(V/H)036*D2**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625497 | Ground Water | GEOSTAR | G5A(V/H)036*D4**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625498 | Ground Water | GEOSTAR | G5A(V/H)042*S3**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625499 | Ground Water | GEOSTAR | G5A(V/H)042*S0**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625500 | Ground Water | GEOSTAR | G5A(V/H)042*S3**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625501 | Ground Water | GEOSTAR | G5A(V/H)042*S4**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625502 | Ground Water | GEOSTAR | G5A(V/H)042*S0**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625503 | Ground Water | GEOSTAR | G5A(V/H)042*S3**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625504 | Ground Water | GEOSTAR | G5A(V/H)042*S4**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625505 | Ground Water | GEOSTAR | G5A(V/H)042*D4**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625506 | Ground Water | GEOSTAR | G5A(V/H)042*D2**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
203372397 | Ground Water | HEIL | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
203372398 | Ground Water | ARCOAIRE | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
203372399 | Ground Water | KEEPRITE | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
203372400 | Ground Water | TEMPSTAR | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
203372401 | Ground Water | COMFORTMAKER | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
203372402 | Ground Water | DAY & NIGHT | HB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
203372403 | Ground Water | HEIL | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
203372404 | Ground Water | ARCOAIRE | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
203372405 | Ground Water | KEEPRITE | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
203372406 | Ground Water | TEMPSTAR | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
203372407 | Ground Water | COMFORTMAKER | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
203372408 | Ground Water | DAY & NIGHT | HB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
203372993 | Ground Water | BOSCH | SM060-1HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | Yes
203372994 | Ground Water | BOSCH | SM070-1HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | Yes
203372995 | Ground Water | BOSCH | SM070-1HZ*-*****C |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | Yes
203380957 | Ground Water | BOSCH | EP018-1VT*******B |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203380958 | Ground Water | BOSCH | EP018-2VT*******B |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203380959 | Ground Water | BOSCH | EP018-1HZ*******B |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203380960 | Ground Water | BOSCH | EP018-2HZ*******B |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203380963 | Ground Water | BOSCH | EP042-1VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203380964 | Ground Water | BOSCH | EP042-3VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203380965 | Ground Water | BOSCH | EP042-4VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203380966 | Ground Water | BOSCH | EP042-1HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203380967 | Ground Water | BOSCH | EP042-3HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203380968 | Ground Water | BOSCH | EP042-4HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203380969 | Ground Water | BOSCH | EP048-1VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203380970 | Ground Water | BOSCH | EP048-3VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203380971 | Ground Water | BOSCH | EP048-4VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203380972 | Ground Water | BOSCH | EP048-1HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203380973 | Ground Water | BOSCH | EP048-3HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203380974 | Ground Water | BOSCH | EP048-4HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383876 | Ground Water | CARRIER | 50PSV018***3/CA |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203383877 | Ground Water | CARRIER | 50PSV018***4/DA |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203383878 | Ground Water | CARRIER | 50PSH018***3/CA |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203383879 | Ground Water | CARRIER | 50PSH018***4/DA |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203383880 | Ground Water | CARRIER | 50PSV042***3/CA |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383881 | Ground Water | CARRIER | 50PSV042***5/EA |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383882 | Ground Water | CARRIER | 50PSV042***6/FA |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383883 | Ground Water | CARRIER | 50PSH042***3/CA |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383884 | Ground Water | CARRIER | 50PSH042***5/EA |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383885 | Ground Water | CARRIER | 50PSH042***6/FA |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
211594244 | Ground Water | TRANE | EXHG0157 |  | 17000 | 25.8 | 15300 | 4.6 | 1.4167 | No
211594245 | Ground Water | TRANE | EXHG0187 |  | 21100 | 28.7 | 18800 | 4.9 | 1.7583 | No
211594246 | Ground Water | TRANE | EXHG024B |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
211594247 | Ground Water | TRANE | EXHG0244 |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
211594248 | Ground Water | TRANE | EXHG0247 |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
211594249 | Ground Water | TRANE | EXHG030B |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
211594250 | Ground Water | TRANE | EXHG0304 |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
211594251 | Ground Water | TRANE | EXHG0307 |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
211594252 | Ground Water | TRANE | EXHG036B |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
5295998 | Ground Water | WaterFurnace | NBV/NBH030**3*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5295999 | Ground Water | WaterFurnace | NBV/NBH030**4*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5296000 | Ground Water | WaterFurnace | NBV/NBH030**4*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5296001 | Ground Water | WaterFurnace | NBV/NBH030**3*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5296002 | Ground Water | WaterFurnace | NBV/NBH030**0*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5296003 | Ground Water | WaterFurnace | NBV/NBH030**2*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
5296004 | Ground Water | WaterFurnace | NBV/NBH036**0*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
5296005 | Ground Water | WaterFurnace | NBV/NBH036**3*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
5296006 | Ground Water | WaterFurnace | NBV/NBH036**4*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
5296007 | Ground Water | WaterFurnace | NBV/NBH036**2*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
5296008 | Ground Water | WaterFurnace | NBV/NBH036**0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296009 | Ground Water | WaterFurnace | NBV/NBH036**3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296010 | Ground Water | WaterFurnace | NBV/NBH036**4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296011 | Ground Water | WaterFurnace | NBV/NBH036**2*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296012 | Ground Water | WaterFurnace | NBV/NBH036**2*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296013 | Ground Water | WaterFurnace | NBV/NBH036**0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296014 | Ground Water | WaterFurnace | NBV/NBH036**3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296015 | Ground Water | WaterFurnace | NBV/NBH036**4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
5296220 | Ground Water | WaterFurnace | NBV/NBH042**0*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
5296221 | Ground Water | WaterFurnace | NBV/NBH042**3*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
5296222 | Ground Water | WaterFurnace | NBV/NBH042**4*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
5296223 | Ground Water | WaterFurnace | NBV/NBH042**5*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
5296225 | Ground Water | WaterFurnace | NBV/NBH042**0*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5296226 | Ground Water | WaterFurnace | NBV/NBH042**3*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5296227 | Ground Water | WaterFurnace | NBV/NBH042**4*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5296228 | Ground Water | WaterFurnace | NBV/NBH042**4*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5296229 | Ground Water | WaterFurnace | NBV/NBH042**3*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5296230 | Ground Water | WaterFurnace | NBV/NBH042**0*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
5315753 | Ground Water | WaterFurnace | NBV/NBH048**0*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
5315754 | Ground Water | WaterFurnace | NBV/NBH048**3*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
5315755 | Ground Water | WaterFurnace | NBV/NBH048**4*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
5315756 | Ground Water | WaterFurnace | NBV/NBH048**5*0 |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
5315758 | Ground Water | WaterFurnace | NBV/NBH048**0*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315759 | Ground Water | WaterFurnace | NBV/NBH048**3*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315760 | Ground Water | WaterFurnace | NBV/NBH048**4*1 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
7022707 | Ground Water | GeoSmart Energy | ZS060**3*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
7022708 | Ground Water | GEOSTAR | ZS060**3*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
205767508 | Ground Water | ClimateMaster | TRH/V015A |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
205767509 | Ground Water | ClimateMaster | TRH/V018A |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
205767513 | Ground Water | ClimateMaster | TSH/V/D024C |  | 26500 | 24.9 | 24100 | 5 | 2.2083 | Yes
205767514 | Ground Water | ClimateMaster | TSH/V/D024C*K |  | 26900 | 26.9 | 23800 | 5.2 | 2.2417 | Yes
205767515 | Ground Water | ClimateMaster | TSH/V/D030C |  | 31000 | 24.9 | 28400 | 4.7 | 2.5833 | Yes
205767516 | Ground Water | ClimateMaster | TSH/V/D030C*K |  | 30800 | 26.7 | 28000 | 4.9 | 2.5667 | Yes
205767517 | Ground Water | ClimateMaster | TSH/V/D036C |  | 35400 | 23.2 | 33200 | 4.7 | 2.95 | Yes
205767518 | Ground Water | ClimateMaster | TSH/V/D036C*K |  | 35400 | 24.9 | 32600 | 4.9 | 2.95 | Yes
205767519 | Ground Water | ClimateMaster | TSH/V/D042C |  | 43700 | 25.4 | 36200 | 4.7 | 3.6417 | Yes
205767520 | Ground Water | ClimateMaster | TSH/V/D042C*K |  | 44400 | 29.5 | 35200 | 5.2 | 3.7 | Yes
205767521 | Ground Water | ClimateMaster | TSH/V/D048C*K |  | 53700 | 23.9 | 45700 | 4.4 | 4.475 | Yes
205767522 | Ground Water | ClimateMaster | TSH/V/D060C |  | 68500 | 23.1 | 58200 | 4.2 | 5.7083 | Yes
205767523 | Ground Water | ClimateMaster | TSH/V/D060C*K |  | 68900 | 24.9 | 58200 | 4.6 | 5.7417 | Yes
205767525 | Ground Water | ClimateMaster | TSH/V/D070C*K |  | 78100 | 23 | 65200 | 4.1 | 6.5083 | Yes
205767526 | Ground Water | ClimateMaster | TSH/V009A |  | 11100 | 25.2 | 9400 | 4.3 | 0.925 | No
205767541 | Ground Water | ClimateMaster | TCH/V018A*W/K |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
205767542 | Ground Water | ClimateMaster | TCH/V024A*W/K |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
205767543 | Ground Water | ClimateMaster | TCH/V030A*W/K |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
205767548 | Ground Water | ClimateMaster | TRH/V018A*W/K |  | 21500 | 23.6 | 17800 | 4.5 | 1.7917 | No
205767549 | Ground Water | ClimateMaster | TRH/V024A*W/K |  | 27000 | 21.5 | 23500 | 4.3 | 2.25 | No
205767550 | Ground Water | ClimateMaster | TRH/V030A*W/K |  | 32000 | 21.6 | 30500 | 4.3 | 2.6667 | No
205767554 | Ground Water | ClimateMaster | TZV/H024C |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
205767556 | Ground Water | ClimateMaster | TZV/H036C |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
205767557 | Ground Water | ClimateMaster | TZV/H042C |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
217903468 | Ground Water | WaterFurnace | V5R036*D0**1* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903469 | Ground Water | WaterFurnace | V5R036*D0**4* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903470 | Ground Water | WaterFurnace | V5R036*D0**5* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903471 | Ground Water | WaterFurnace | V5R036*D3**1* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903472 | Ground Water | WaterFurnace | V5R036*D3**4* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903473 | Ground Water | WaterFurnace | V5R036*D3**5* |  | 40100 | 27.3 | 34600 | 5.1 | 3.3417 | No
217903474 | Ground Water | WaterFurnace | V5R048*D0**1* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903475 | Ground Water | WaterFurnace | V5R048*D0**4* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903476 | Ground Water | WaterFurnace | V5R048*D0**5* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903477 | Ground Water | WaterFurnace | V5R048*D3**1* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903478 | Ground Water | WaterFurnace | V5R048*D3**4* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903479 | Ground Water | WaterFurnace | V5R048*D3**5* |  | 51000 | 23.9 | 47300 | 4.9 | 4.25 | No
217903480 | Ground Water | WaterFurnace | V5R060*D0**1* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903481 | Ground Water | WaterFurnace | V5R060*D0**4* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903482 | Ground Water | WaterFurnace | V5R060*D0**5* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903483 | Ground Water | WaterFurnace | V5R060*D3**1* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903484 | Ground Water | WaterFurnace | V5R060*D3**4* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903485 | Ground Water | WaterFurnace | V5R060*D3**5* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903486 | Ground Water | WaterFurnace | V5R072*D0**1* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903487 | Ground Water | WaterFurnace | V5R072*D0**4* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903488 | Ground Water | WaterFurnace | V5R072*D0**5* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903489 | Ground Water | WaterFurnace | V5R072*D3**1* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903490 | Ground Water | WaterFurnace | V5R072*D3**4* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903491 | Ground Water | WaterFurnace | V5R072*D3**5* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903492 | Ground Water | WaterFurnace | V5R096*T3**5* |  | 96600 | 24.9 | 85800 | 4.5 | 8.05 | No
217903493 | Ground Water | WaterFurnace | V5R120*T3**5* |  | 128500 | 23.3 | 113700 | 4.5 | 10.7083 | No
9100310 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**0*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100311 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**0*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100313 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**2*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100314 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**2*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100316 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**3*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100317 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**3*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100319 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**4*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100320 | Ground Water | YORK BY JOHNSON CONTROLS | YGSH023**4*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
9100325 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**0*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
9100326 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**0*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
9100327 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**2*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
9100328 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**2*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
9100330 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH018**0*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
9100332 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH018**2*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
9100335 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**0*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100337 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**2*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100338 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**2*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100340 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**3*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100341 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**3*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100343 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**4*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
9100345 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**0*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100346 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**0*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100348 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**2*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100349 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**2*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100351 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**3*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100352 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**3*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100354 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**4*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
9100355 | Ground Water | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**4*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
216625764 | Ground Water | GeoSmart Energy | S5A(V/H)024*D2**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625765 | Ground Water | GeoSmart Energy | S5A(V/H)024*D2**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625766 | Ground Water | GeoSmart Energy | S5A(V/H)024*D3**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625767 | Ground Water | GeoSmart Energy | S5A(V/H)024*D3**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625768 | Ground Water | GeoSmart Energy | S5A(V/H)024*D4**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625769 | Ground Water | GeoSmart Energy | S5A(V/H)024*D4**4 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
216625770 | Ground Water | GeoSmart Energy | S5A(V/H)024*S0**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625771 | Ground Water | GeoSmart Energy | S5A(V/H)024*S0**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625772 | Ground Water | GeoSmart Energy | S5A(V/H)024*S2**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625773 | Ground Water | GeoSmart Energy | S5A(V/H)024*S2**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625774 | Ground Water | GeoSmart Energy | S5A(V/H)024*S3**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625775 | Ground Water | GeoSmart Energy | S5A(V/H)024*S3**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625776 | Ground Water | GeoSmart Energy | S5A(V/H)024*S4**1 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625777 | Ground Water | GeoSmart Energy | S5A(V/H)024*S4**4 |  | 28000 | 28 | 24000 | 4.7 | 2.3333 | No
216625778 | Ground Water | GeoSmart Energy | S5A(V/H)030*D0**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625779 | Ground Water | GeoSmart Energy | S5A(V/H)030*D0**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625780 | Ground Water | GeoSmart Energy | S5A(V/H)030*D2**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625781 | Ground Water | GeoSmart Energy | S5A(V/H)030*D2**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625782 | Ground Water | GeoSmart Energy | S5A(V/H)030*D3**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625783 | Ground Water | GeoSmart Energy | S5A(V/H)030*D3**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625784 | Ground Water | GeoSmart Energy | S5A(V/H)030*D4**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625785 | Ground Water | GeoSmart Energy | S5A(V/H)030*D4**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625786 | Ground Water | GeoSmart Energy | S5A(V/H)030*S0**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625787 | Ground Water | GeoSmart Energy | S5A(V/H)030*S0**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625788 | Ground Water | GeoSmart Energy | S5A(V/H)030*S2**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625789 | Ground Water | GeoSmart Energy | S5A(V/H)030*S2**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625790 | Ground Water | GeoSmart Energy | S5A(V/H)030*S3**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625791 | Ground Water | GeoSmart Energy | S5A(V/H)030*S3**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625792 | Ground Water | GeoSmart Energy | S5A(V/H)030*S4**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625793 | Ground Water | GeoSmart Energy | S5A(V/H)030*S4**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625794 | Ground Water | GeoSmart Energy | S5A(V/H)036*D0**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625795 | Ground Water | GeoSmart Energy | S5A(V/H)036*D0**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625796 | Ground Water | GeoSmart Energy | S5A(V/H)036*D0**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625797 | Ground Water | GeoSmart Energy | S5A(V/H)036*D2**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625798 | Ground Water | GeoSmart Energy | S5A(V/H)036*D2**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625799 | Ground Water | GeoSmart Energy | S5A(V/H)036*D2**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625800 | Ground Water | GeoSmart Energy | S5A(V/H)036*D3**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625801 | Ground Water | GeoSmart Energy | S5A(V/H)036*D3**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625802 | Ground Water | GeoSmart Energy | S5A(V/H)036*D3**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625803 | Ground Water | GeoSmart Energy | S5A(V/H)036*D4**1 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625804 | Ground Water | GeoSmart Energy | S5A(V/H)036*D4**2 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625805 | Ground Water | GeoSmart Energy | S5A(V/H)036*D4**4 |  | 41800 | 28.4 | 36000 | 5.3 | 3.4833 | No
216625806 | Ground Water | GeoSmart Energy | S5A(V/H)036*S0**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625807 | Ground Water | GeoSmart Energy | S5A(V/H)036*S0**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625808 | Ground Water | GeoSmart Energy | S5A(V/H)036*S0**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625809 | Ground Water | GeoSmart Energy | S5A(V/H)036*S2**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625810 | Ground Water | GeoSmart Energy | S5A(V/H)036*S2**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625811 | Ground Water | GeoSmart Energy | S5A(V/H)036*S2**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625812 | Ground Water | GeoSmart Energy | S5A(V/H)036*S3**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625813 | Ground Water | GeoSmart Energy | S5A(V/H)036*S3**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625814 | Ground Water | GeoSmart Energy | S5A(V/H)036*S3**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625815 | Ground Water | GeoSmart Energy | S5A(V/H)036*S4**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
202350481 | Ground Water | AAON, Inc. | M2-011-2-H-ACBC-C0-10-000-A |  | 135000 | 21.5 | 125100 | 4.1 | 11.25 | No
202350484 | Ground Water | AAON, Inc. | M2-011-3-H-ACBC-C0-10-000-A |  | 135000 | 21.5 | 125100 | 4.1 | 11.25 | No
202350487 | Ground Water | AAON, Inc. | M2-011-4-H-ACBC-C0-10-000-A |  | 135000 | 21.5 | 125100 | 4.1 | 11.25 | No
202350489 | Ground Water | AAON, Inc. | M2-014-2-H-ACAC-C0-10-000-A |  | 131700 | 21.4 | 126600 | 4.1 | 10.975 | No
202350490 | Ground Water | AAON, Inc. | M2-014-2-H-BCAC-V0-10-000-A |  | 132100 | 21.3 | 126200 | 4.1 | 11.0083 | No
202350491 | Ground Water | AAON, Inc. | M2-014-3-H-ACAC-C0-10-000-A |  | 131700 | 21.4 | 126600 | 4.1 | 10.975 | No
202350492 | Ground Water | AAON, Inc. | M2-014-3-H-BCAC-V0-10-000-A |  | 132100 | 21.3 | 126200 | 4.1 | 11.0083 | No
202350493 | Ground Water | AAON, Inc. | M2-014-4-H-ACAC-C0-10-000-A |  | 131700 | 21.4 | 126600 | 4.1 | 10.975 | No
202350494 | Ground Water | AAON, Inc. | M2-014-4-H-BCAC-V0-10-000-A |  | 132100 | 21.3 | 126200 | 4.1 | 11.0083 | No
202350495 | Ground Water | AAON, Inc. | M2-011-2-H-BCBC-V0-10-000-A |  | 135000 | 21.4 | 124700 | 4.1 | 11.25 | No
202350496 | Ground Water | AAON, Inc. | M2-011-3-H-BCBC-V0-10-000-A |  | 135000 | 21.4 | 124700 | 4.1 | 11.25 | No
202350497 | Ground Water | AAON, Inc. | M2-011-4-H-BCBC-V0-10-000-A |  | 135000 | 21.4 | 124700 | 4.1 | 11.25 | No
207335399 | Ground Water | GeoSmart Energy | GT049**1*(1,2,4)*K |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335400 | Ground Water | GeoSmart Energy | GT064**1*(1,4)*K |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335401 | Ground Water | GeoSmart Energy | GT072**1*(1,4)*J |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207335402 | Ground Water | GeoSmart Energy | GS012**1*0*J |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | Yes
207335403 | Ground Water | GeoSmart Energy | GS018**1*(1,4)*J |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | Yes
207335404 | Ground Water | GeoSmart Energy | GS018**1*0*J |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | Yes
207335406 | Ground Water | GeoSmart Energy | GS022**1*(1,4)*J |  | 21900 | 27.5 | 19500 | 5 | 1.825 | Yes
207335407 | Ground Water | GeoSmart Energy | GS030**1*(0,3)*J |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | Yes
207335408 | Ground Water | GeoSmart Energy | GS030**1*(1,4)*J |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | Yes
207335409 | Ground Water | GeoSmart Energy | GS036**1*(0,3)*K |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | Yes
207335410 | Ground Water | GeoSmart Energy | GS036**1*(1,2,4)*K |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | Yes
207335411 | Ground Water | GeoSmart Energy | GS042**1*(0,3)*K |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | Yes
207335412 | Ground Water | GeoSmart Energy | GS048**1*(0,3)*K |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | Yes
207335413 | Ground Water | GeoSmart Energy | GS048**1*(1,2,4)*K |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | Yes
207335414 | Ground Water | GeoSmart Energy | GS060**1*(1,4)*K |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | Yes
207335415 | Ground Water | GeoSmart Energy | GS060**1*0*K |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | Yes
207335416 | Ground Water | GeoSmart Energy | GS070**1*(1,4)*J |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | Yes
207335514 | Ground Water | GeoSmart Energy | GS042**1*(1,2,4)*K |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | Yes
207335570 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS012**1*0****J |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | Yes
207335571 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS018**1*(1,4)****J |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | Yes
207335572 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS022**1*(1,4)****J |  | 21900 | 27.5 | 19500 | 5 | 1.825 | Yes
207335573 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****J |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | Yes
207335574 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS036**1*(1,2,4)*K |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | Yes
207335575 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*K |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | Yes
207335576 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS048**1*(1,2,4)*K |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | Yes
207335577 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS060**1*(1,4)****K |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | Yes
207335578 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS070**1*(1,4)****J |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | Yes
207335579 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT026**1*(1,4)****J |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335580 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,4)*K |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207335581 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,4)*K |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335582 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT064**1*(1,4)*K |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335583 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT072**1*(1,4)****J |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207335584 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT026**1*(1,4)****H |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335585 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*J |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207335586 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*J |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335587 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT064**1*(1,4)*J |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335588 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT072**1*(1,4)****H |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207335589 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT026**1*(1,4)****J |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335590 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*K |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207335591 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*K |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335592 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT064**1*(1,4)*K |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207335593 | Ground Water | YORK BY JOHNSON CONTROLS | YZFT072**1*(1,4)****J |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
202211051 | Ground Water | WaterFurnace | URD049*3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211052 | Ground Water | WaterFurnace | URD049*3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211053 | Ground Water | WaterFurnace | URD049*3*5 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
202211054 | Ground Water | WaterFurnace | URD064*0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211055 | Ground Water | WaterFurnace | URD064*0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211056 | Ground Water | WaterFurnace | URD064*0*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211057 | Ground Water | WaterFurnace | URD064*3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211058 | Ground Water | WaterFurnace | URD064*3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211059 | Ground Water | WaterFurnace | URD064*3*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
202211060 | Ground Water | WaterFurnace | URD072*0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211061 | Ground Water | WaterFurnace | URD072*0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211062 | Ground Water | WaterFurnace | URD072*0*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211063 | Ground Water | WaterFurnace | URD072*3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211064 | Ground Water | WaterFurnace | URD072*3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211065 | Ground Water | WaterFurnace | URD072*3*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
202211066 | Ground Water | WaterFurnace | URT096*3*5 |  | 100600 | 25.9 | 89400 | 4.7 | 8.3833 | No
202262237 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ036J1 | SAH036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
202262238 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ042J1 | SAH042* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
202272873 | Ground Water | BOSCH-GEO | BP018-1VT*******C |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
202319683 | Ground Water | BOSCH-GEO | SM048-1CSC-*****A | SM048-1AV*-*****A | 52800 | 21.25 | 46600 | 4.6 | 4.4 | No
206726691 | Ground Water | WaterFurnace | UVV/UVH024**3*1 |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
206726692 | Ground Water | WaterFurnace | UVV/UVH024**4*1 |  | 27300 | 37.4 | 23400 | 5 | 2.275 | No
206726812 | Ground Water | GEOCOMFORT | GBS018 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | Yes
206726813 | Ground Water | GEOCOMFORT | GBS018 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | Yes
206726814 | Ground Water | HYDRON MODULE | HBS018 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | Yes
206726815 | Ground Water | HYDRON MODULE | HBS018 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | Yes
206726816 | Ground Water | TETCO | TBS018 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | Yes
206726817 | Ground Water | TETCO | TBS018 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | Yes
206726818 | Ground Water | GEOCOMFORT | GBS018*2 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
206726819 | Ground Water | GEOCOMFORT | GBS018*2 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | No
206726820 | Ground Water | HYDRON MODULE | HBS018*2 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
206726821 | Ground Water | HYDRON MODULE | HBS018*2 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | No
206726822 | Ground Water | TETCO | TBS018*2 | EED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
206726823 | Ground Water | TETCO | TBS018*2 | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | No
206726824 | Ground Water | GEOCOMFORT | GBT036 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | Yes
206726825 | Ground Water | GEOCOMFORT | GBT036 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | Yes
206726826 | Ground Water | HYDRON MODULE | HBT036 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | Yes
206726827 | Ground Water | HYDRON MODULE | HBT036 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | Yes
206726828 | Ground Water | TETCO | TBT036 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | Yes
206726829 | Ground Water | TETCO | TBT036 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | Yes
206726830 | Ground Water | GEOCOMFORT | GBT036*2 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
206726831 | Ground Water | GEOCOMFORT | GBT036*2 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | No
206726832 | Ground Water | HYDRON MODULE | HBT036*2 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
206726833 | Ground Water | HYDRON MODULE | HBT036*2 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | No
206726834 | Ground Water | TETCO | TBT036*2 | EED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
206726835 | Ground Water | TETCO | TBT036*2 | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | No
206726836 | Ground Water | GEOCOMFORT | GBT048 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | Yes
206726837 | Ground Water | GEOCOMFORT | GBT048 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | Yes
206726838 | Ground Water | HYDRON MODULE | HBT048 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | Yes
206726839 | Ground Water | HYDRON MODULE | HBT048 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | Yes
206726840 | Ground Water | TETCO | TBT048 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | Yes
206726841 | Ground Water | TETCO | TBT048 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | Yes
206726842 | Ground Water | GEOCOMFORT | GBT048*2 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
206726843 | Ground Water | GEOCOMFORT | GBT048*2 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | No
206726844 | Ground Water | HYDRON MODULE | HBT048*2 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
206726845 | Ground Water | HYDRON MODULE | HBT048*2 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | No
206726846 | Ground Water | TETCO | TBT048*2 | EED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
206726847 | Ground Water | TETCO | TBT048*2 | EAD048 | 53400 | 23.4 | 50800 | 4.6 | 4.45 | No
206726848 | Ground Water | GEOCOMFORT | GBT060 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | Yes
4651274 | Ground Water | WaterFurnace | USH023**4*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651339 | Ground Water | WaterFurnace | USV/USH024**0*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651340 | Ground Water | WaterFurnace | USV/USH024**2*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651341 | Ground Water | WaterFurnace | USV/USH024**3*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651342 | Ground Water | WaterFurnace | USV/USH024**4*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651403 | Ground Water | WaterFurnace | USV/USH030**0*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651404 | Ground Water | WaterFurnace | USV/USH030**2*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651405 | Ground Water | WaterFurnace | USV/USH030**3*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651407 | Ground Water | WaterFurnace | USV/USH030**4*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651417 | Ground Water | WaterFurnace | USV/USH036**0*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651418 | Ground Water | WaterFurnace | USV/USH036**2*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651419 | Ground Water | WaterFurnace | USV/USH036**3*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651420 | Ground Water | WaterFurnace | USV/USH036**4*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651530 | Ground Water | WaterFurnace | USV/USH042**0*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651532 | Ground Water | WaterFurnace | USV/USH042**3*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651533 | Ground Water | WaterFurnace | USV/USH042**4*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651546 | Ground Water | WaterFurnace | USV/USH048**0*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651547 | Ground Water | WaterFurnace | USV/USH048**3*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651548 | Ground Water | WaterFurnace | USV/USH048**4*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651574 | Ground Water | WaterFurnace | USV/USH060**0*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651575 | Ground Water | WaterFurnace | USV/USH060**3*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651576 | Ground Water | WaterFurnace | USV/USH060**4*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651577 | Ground Water | WaterFurnace | USV/USH070**0*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651578 | Ground Water | WaterFurnace | USV/USH070**3*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651579 | Ground Water | WaterFurnace | USV/USH070**4*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651610 | Ground Water | GEOSTAR | ZS023**0*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651611 | Ground Water | GeoSmart Energy | ZS023**0*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651614 | Ground Water | GEOSTAR | ZS024**0*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651615 | Ground Water | GeoSmart Energy | ZS024**0*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651618 | Ground Water | GEOSTAR | ZS024**2*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651619 | Ground Water | GeoSmart Energy | ZS024**2*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651622 | Ground Water | GEOSTAR | ZS024**3*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651623 | Ground Water | GeoSmart Energy | ZS024**3*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651626 | Ground Water | GEOSTAR | ZS024**4*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651627 | Ground Water | GeoSmart Energy | ZS024**4*4 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
4651630 | Ground Water | GEOSTAR | ZS030**0*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651631 | Ground Water | GeoSmart Energy | ZS030**0*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651634 | Ground Water | GEOSTAR | ZS030**2*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651635 | Ground Water | GeoSmart Energy | ZS030**2*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651639 | Ground Water | GEOSTAR | ZS030**3*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651640 | Ground Water | GeoSmart Energy | ZS030**3*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651644 | Ground Water | GEOSTAR | ZS030**4*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651645 | Ground Water | GeoSmart Energy | ZS030**4*4 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
4651657 | Ground Water | GEOSTAR | ZS036**0*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651658 | Ground Water | GeoSmart Energy | ZS036**0*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651665 | Ground Water | GEOSTAR | ZS036**2*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651666 | Ground Water | GeoSmart Energy | ZS036**2*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651726 | Ground Water | GEOSTAR | ZS036**3*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651727 | Ground Water | GeoSmart Energy | ZS036**3*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651732 | Ground Water | GEOSTAR | ZS036**4*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
4651733 | Ground Water | GeoSmart Energy | ZS036**4*4 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
217037827 | Ground Water | GeoSmart Energy | S5SZ036BD1 | A5D(C/U)036B* | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
217037828 | Ground Water | GeoSmart Energy | S5SZ048BD1 | A5D(C/U)048B* | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
217037829 | Ground Water | GeoSmart Energy | S5SZ060BD1 | A5D(C/U)060B* | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
217037830 | Ground Water | GeoSmart Energy | S5SZ066BD1 | A5D(C/U)060B* | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
213307834 | Ground Water | GeoSmart Energy | QT038**1*(1,2)*****K |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | Yes
213307835 | Ground Water | GeoSmart Energy | QT049**1*(1,2)*****J |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | Yes
213348376 | Ground Water | ClimateMaster | TRT072D |  | 76000 | 21.3 | 72000 | 4.4 | 6.3333 | No
213351451 | Ground Water | YORK BY JOHNSON CONTROLS | YLFT048**1*4*A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | Yes
217351881 | Ground Water | HEIL | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351882 | Ground Water | HEIL | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351884 | Ground Water | HEIL | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351885 | Ground Water | HEIL | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351887 | Ground Water | HEIL | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351889 | Ground Water | HEIL | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351892 | Ground Water | KEEPRITE | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351893 | Ground Water | KEEPRITE | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351894 | Ground Water | KEEPRITE | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351895 | Ground Water | KEEPRITE | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351896 | Ground Water | KEEPRITE | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351897 | Ground Water | KEEPRITE | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351898 | Ground Water | KEEPRITE | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
203344888 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH009**0*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
203344891 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH009**9*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
203363126 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**0*1* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363127 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**0*4* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363129 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**2*1* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363130 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**2*4* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363132 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**3*1* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363133 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**3*4* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363135 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**4*1* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363136 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH030**4*4* |  | 33500 | 22.5 | 28000 | 4.2 | 2.7917 | No
203363137 | Ground Water | YORK BY JOHNSON CONTROLS | YBSV/YBSH036**0*0* |  | 40000 | 22 | 35600 | 4.2 | 3.3333 | No
7795926 | Ground Water | TETCO | TVT024*A |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | No
7795943 | Ground Water | GEOCOMFORT | GVT036 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
7795944 | Ground Water | HYDRON MODULE | HVT036 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
209180335 | Ground Water | AE Air | WSV6018B* |  | 20000 | 21.1 | 16500 | 4.1 | 1.6667 | Yes
209180336 | Ground Water | AE Air | WSV6036B* |  | 37000 | 22 | 35000 | 4.1 | 3.0833 | Yes
209180337 | Ground Water | AE Air | WSV6042B* |  | 44000 | 24 | 38500 | 4.4 | 3.6667 | Yes
209180338 | Ground Water | AE Air | WSV6048B* |  | 55500 | 23 | 47000 | 4.3 | 4.625 | Yes
209323637 | Ground Water | HYDROTECH | WSV6009B* |  | 11000 | 26 | 9000 | 4.3 | 0.91667 | Yes
209323638 | Ground Water | AE Air | WSV6009B* |  | 11000 | 26 | 9000 | 4.3 | 0.91667 | Yes
209945912 | Ground Water | WaterFurnace | NBV/NBH009**0*6 |  | 11000 | 23 | 10700 | 4.5 | 0.91667 | No
209945913 | Ground Water | WaterFurnace | NBV/NBH009**2*6 |  | 11000 | 23 | 10700 | 4.5 | 0.91667 | No
209945914 | Ground Water | WaterFurnace | NBV/NBH012**0*6 |  | 13400 | 23.5 | 12400 | 4.3 | 1.1167 | No
209945915 | Ground Water | WaterFurnace | NBV/NBH012**2*6 |  | 13400 | 23.5 | 12400 | 4.3 | 1.1167 | No
211127895 | Ground Water | WaterFurnace | NVV/NVH036D1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
211127897 | Ground Water | WaterFurnace | NVV/NVH060D1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
211127898 | Ground Water | GEOSTAR | 141/142D036**1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
211127900 | Ground Water | GEOSTAR | 141/142D060**1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
211306507 | Ground Water | WaterFurnace | NVZ033*1 | SVH033 | 37000 | 29.2 | 40700 | 4.5 | 3.0833 | Yes
211306508 | Ground Water | WaterFurnace | NVZ042*1 | SVH042 | 46200 | 28.2 | 54100 | 4.2 | 3.85 | Yes
215415814 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)015A*B |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415815 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)015A*C |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415816 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)015A*VB |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415817 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)015A*VC |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415818 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)018A*B |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415819 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)018A*C |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415820 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)018A*VB |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415821 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)018A*VC |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415822 | Ground Water | Johnson Controls | BY(L/R/B/P/T/K)024A*B |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | No
215415823 | Ground Water | SKYMARK | BY(L/R/B/P/T/K)024A*C |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | No
215415824 | Ground Water | Johnson Controls | BY(L/R/B/P/T/K)030A*B |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | No
215415825 | Ground Water | SKYMARK | BY(L/R/B/P/T/K)030A*C |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | No
215415828 | Ground Water | Johnson Controls | BY(L/R/B/P/T/K)042A*B |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | No
215415829 | Ground Water | SKYMARK | BY(L/R/B/P/T/K)042A*C |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | No
215415830 | Ground Water | Johnson Controls | BY(L/R/B/P/T/K)048A*B |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | No
215415831 | Ground Water | SKYMARK | BY(L/R/B/P/T/K)048A*C |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | No
215415832 | Ground Water | Johnson Controls | BY(L/R/B/P/T/K)060A*B |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | No
215415833 | Ground Water | SKYMARK | BY(L/R/B/P/T/K)060A*C |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | No
215415834 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215746921 | Ground Water | TRANE | GSK102A3 |  | 128411 | 25.9 | 117896 | 5.08 | 10.7009 | No
215746923 | Ground Water | TRANE | GSK036A4 |  | 43925 | 29.6 | 39058 | 5.26 | 3.6604 | No
215746924 | Ground Water | TRANE | GSK036AW |  | 43925 | 29.6 | 39058 | 5.26 | 3.6604 | No
215746925 | Ground Water | TRANE | GSK048A4 |  | 57887 | 27.2 | 51760 | 5.05 | 4.8239 | No
215746926 | Ground Water | TRANE | GSK048AW |  | 57887 | 27.2 | 51760 | 5.05 | 4.8239 | No
215746927 | Ground Water | TRANE | GSK060A4 |  | 69939 | 26.2 | 62898 | 4.9 | 5.8282 | No
215746928 | Ground Water | TRANE | GSK060AW |  | 69939 | 26.2 | 62898 | 4.9 | 5.8282 | No
215746929 | Ground Water | TRANE | GSK072A4 |  | 91819 | 27.9 | 75524 | 4.96 | 7.6516 | No
215746930 | Ground Water | TRANE | GSK072AW |  | 91819 | 27.9 | 75524 | 4.96 | 7.6516 | No
215746931 | Ground Water | TRANE | GSK090A4 |  | 107813 | 26.6 | 91385 | 4.94 | 8.9844 | No
215746932 | Ground Water | TRANE | GSK090AW |  | 107813 | 26.6 | 91385 | 4.94 | 8.9844 | No
215746933 | Ground Water | TRANE | GSK102A4 |  | 128411 | 25.9 | 117896 | 5.08 | 10.7009 | No
215746934 | Ground Water | TRANE | GSK102AW |  | 128411 | 25.9 | 117896 | 5.08 | 10.7009 | No
215748031 | Ground Water | NORDIC | R-55-HACW-X-1T-*-*DE** |  | 48000 | 22.2 | 47000 | 4.5 | 4 | No
8714940 | Ground Water | CARRIER | GZ024******1**1 | FE/V***F003*** | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8714941 | Ground Water | BRYANT | GZ024******1*X1 | FE/V***F003*** | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
8735477 | Ground Water | GEOCOMFORT | GVT048 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | Yes
8735495 | Ground Water | HYDRON MODULE | HVT048 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | Yes
8735512 | Ground Water | TETCO | TVT048 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | Yes
8735538 | Ground Water | GEOCOMFORT | GVT048*2 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735552 | Ground Water | HYDRON MODULE | HVT048*2 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735567 | Ground Water | TETCO | TVT048*2 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735607 | Ground Water | GEOCOMFORT | GVT048*3 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735711 | Ground Water | HYDRON MODULE | HVT048*3 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735721 | Ground Water | TETCO | TVT048*3 |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735754 | Ground Water | GEOCOMFORT | GVT048*A |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735767 | Ground Water | HYDRON MODULE | HVT048*A |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735778 | Ground Water | TETCO | TVT048*A |  | 54700 | 24.5 | 46900 | 4.6 | 4.5583 | No
8735903 | Ground Water | GEOCOMFORT | GVS042*****1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | Yes
8735904 | Ground Water | HYDRON MODULE | HVS042*****1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | Yes
8735905 | Ground Water | TETCO | TVS042*****1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | Yes
8735906 | Ground Water | GEOCOMFORT | GVS042*2***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8735907 | Ground Water | HYDRON MODULE | HVS042*2***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8735908 | Ground Water | TETCO | TVS042*2***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8735909 | Ground Water | GEOCOMFORT | GVS042*3***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8735910 | Ground Water | HYDRON MODULE | HVS042*3***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8735911 | Ground Water | TETCO | TVS042*3***1 |  | 47700 | 28.4 | 38300 | 5 | 3.975 | No
8737970 | Ground Water | GEOCOMFORT | GVS060*****1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | Yes
8737971 | Ground Water | HYDRON MODULE | HVS060*****1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | Yes
8737972 | Ground Water | TETCO | TVS060*****1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | Yes
8737973 | Ground Water | GEOCOMFORT | GVS060*2***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737974 | Ground Water | HYDRON MODULE | HVS060*2***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737975 | Ground Water | TETCO | TVS060*2***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737976 | Ground Water | GEOCOMFORT | GVS060*3***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737977 | Ground Water | HYDRON MODULE | HVS060*3***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
8737978 | Ground Water | TETCO | TVS060*3***1 |  | 65000 | 22.8 | 58100 | 4.6 | 5.4167 | No
207177463 | Ground Water | TRANE | EXVG0127 |  | 13700 | 27.9 | 12300 | 5 | 1.1417 | No
207177464 | Ground Water | TRANE | EXVG015A |  | 17000 | 25.8 | 15300 | 4.6 | 1.4167 | No
207177465 | Ground Water | TRANE | EXVG0157 |  | 17000 | 25.8 | 15300 | 4.6 | 1.4167 | No
207177466 | Ground Water | TRANE | EXVG018A |  | 21100 | 28.7 | 18800 | 4.9 | 1.7583 | No
207177467 | Ground Water | TRANE | EXVG0187 |  | 21100 | 28.7 | 18800 | 4.9 | 1.7583 | No
207177468 | Ground Water | TRANE | EXVG024A |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
207177469 | Ground Water | TRANE | EXVG024B |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
207177470 | Ground Water | TRANE | EXVG0244 |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
207177471 | Ground Water | TRANE | EXVG0247 |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
207177472 | Ground Water | TRANE | EXVG030A |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
207177473 | Ground Water | TRANE | EXVG030B |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
207177474 | Ground Water | TRANE | EXVG0304 |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
207177475 | Ground Water | TRANE | EXVG0307 |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
207177476 | Ground Water | TRANE | EXVG036A |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
207177477 | Ground Water | TRANE | EXVG036B |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
207177478 | Ground Water | TRANE | EXVG0364 |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
207177479 | Ground Water | TRANE | EXVG0367 |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
207177480 | Ground Water | TRANE | EXVG042A |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
207177481 | Ground Water | TRANE | EXVG042B |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
207177482 | Ground Water | TRANE | EXVG0424 |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
207177483 | Ground Water | TRANE | EXVG048A |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
207177484 | Ground Water | TRANE | EXVG048B |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
207177485 | Ground Water | TRANE | EXVG0484 |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
207177486 | Ground Water | TRANE | EXVG060A |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
207177487 | Ground Water | TRANE | EXVG060B |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
207177488 | Ground Water | TRANE | EXVG0604 |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
207177489 | Ground Water | TRANE | EXVG070A |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
207177490 | Ground Water | TRANE | EXVG070B |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
207177491 | Ground Water | TRANE | EXVG0704 |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
207177492 | Ground Water | TRANE | DXVG024A |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
207177493 | Ground Water | TRANE | DXVG024B |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
207177494 | Ground Water | TRANE | DXVG0244 |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
207177495 | Ground Water | TRANE | DXVG0247 |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
207177496 | Ground Water | TRANE | DXVG036A |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
207177497 | Ground Water | TRANE | DXVG036B |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
207177498 | Ground Water | TRANE | DXVG0364 |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
207177499 | Ground Water | TRANE | DXVG0367 |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
207177500 | Ground Water | TRANE | DXVG048A |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
207177501 | Ground Water | TRANE | DXVG048B |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
207177502 | Ground Water | TRANE | DXVG0484 |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
207177503 | Ground Water | TRANE | DXVG060A |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
207177504 | Ground Water | TRANE | DXVG060B |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
207177505 | Ground Water | TRANE | DXVG0604 |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
207177506 | Ground Water | TRANE | DXVG070A |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
207177507 | Ground Water | TRANE | DXVG070B |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
207177508 | Ground Water | TRANE | DXVG0704 |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
207178484 | Ground Water | GEOSTAR | 163H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207178485 | Ground Water | GEOSTAR | 164H049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207178486 | Ground Water | GEOSTAR | 164H049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207178487 | Ground Water | GEOSTAR | 163H072**1 | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
207178492 | Ground Water | GEOSTAR | 163J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
211594123 | Ground Water | TRANE | GEHG024A |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
211594124 | Ground Water | TRANE | GEHG030A |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
211594125 | Ground Water | TRANE | GEHG036A |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
211594126 | Ground Water | TRANE | GEHG042A |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
211594127 | Ground Water | TRANE | GEHG048A |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
211594128 | Ground Water | TRANE | GEHG060A |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
211594129 | Ground Water | TRANE | EXHG009A |  | 8800 | 25 | 8200 | 4.8 | 0.73333 | No
211594130 | Ground Water | TRANE | EXHG012A |  | 13700 | 27.9 | 12300 | 5 | 1.1417 | No
211594131 | Ground Water | TRANE | EXHG015A |  | 17000 | 25.8 | 15300 | 4.6 | 1.4167 | No
211594132 | Ground Water | TRANE | EXHG018A |  | 21100 | 28.7 | 18800 | 4.9 | 1.7583 | No
211594133 | Ground Water | TRANE | EXHG024A |  | 27400 | 27.2 | 25900 | 5 | 2.2833 | No
211594134 | Ground Water | TRANE | EXHG030A |  | 35000 | 27.2 | 31000 | 5 | 2.9167 | No
211594135 | Ground Water | TRANE | EXHG036A |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
211594136 | Ground Water | TRANE | EXHG042A |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
211594137 | Ground Water | TRANE | EXHG048A |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
211594138 | Ground Water | TRANE | EXHG060A |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
211594139 | Ground Water | TRANE | EXHG070A |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
211594212 | Ground Water | TRANE | DXHG024A |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
211594213 | Ground Water | TRANE | DXHG036A |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
211594214 | Ground Water | TRANE | DXHG048A |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
211594215 | Ground Water | TRANE | DXHG060A |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
211594216 | Ground Water | TRANE | DXHG070A |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
211594222 | Ground Water | TRANE | GEHG0067 |  | 8100 | 21.3 | 7500 | 4.1 | 0.675 | No
211594223 | Ground Water | TRANE | GEHG0097 |  | 9600 | 23.8 | 9100 | 4.7 | 0.8 | No
211594224 | Ground Water | TRANE | GEHG0127 |  | 13300 | 24.2 | 12400 | 4.6 | 1.1083 | No
211594225 | Ground Water | TRANE | GEHG0157 |  | 16600 | 23 | 15400 | 4.3 | 1.3833 | No
211594226 | Ground Water | TRANE | GEHG0187 |  | 19300 | 23.5 | 18400 | 4.4 | 1.6083 | No
211594227 | Ground Water | TRANE | GEHG024B |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
211594228 | Ground Water | TRANE | GEHG0244 |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
211594229 | Ground Water | TRANE | GEHG0247 |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
211594230 | Ground Water | TRANE | GEHG030B |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
211594231 | Ground Water | TRANE | GEHG0304 |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
211594232 | Ground Water | TRANE | GEHG0307 |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
211594233 | Ground Water | TRANE | GEHG036B |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
211594234 | Ground Water | TRANE | GEHG0364 |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
211594235 | Ground Water | TRANE | GEHG0367 |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
211594236 | Ground Water | TRANE | GEHG042B |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
211594237 | Ground Water | TRANE | GEHG0424 |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
211594238 | Ground Water | TRANE | GEHG048B |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
211594239 | Ground Water | TRANE | GEHG0484 |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
211594240 | Ground Water | TRANE | GEHG060B |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
211594241 | Ground Water | TRANE | GEHG0604 |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
211594242 | Ground Water | TRANE | EXHG0097 |  | 8800 | 25 | 8200 | 4.8 | 0.73333 | No
211594243 | Ground Water | TRANE | EXHG0127 |  | 13700 | 27.9 | 12300 | 5 | 1.1417 | No
202350498 | Ground Water | AAON, Inc. | M2-014-2-H-ACBC-C0-10-000-A |  | 135000 | 22.1 | 125000 | 4.2 | 11.25 | No
202350499 | Ground Water | AAON, Inc. | M2-014-2-H-BCBC-V0-10-000-A |  | 135000 | 22 | 124600 | 4.2 | 11.25 | No
202350500 | Ground Water | AAON, Inc. | M2-014-3-H-ACBC-C0-10-000-A |  | 135000 | 22.1 | 125000 | 4.2 | 11.25 | No
202350501 | Ground Water | AAON, Inc. | M2-014-3-H-BCBC-V0-10-000-A |  | 135000 | 22 | 124600 | 4.2 | 11.25 | No
202350502 | Ground Water | AAON, Inc. | M2-014-4-H-ACBC-C0-10-000-A |  | 135000 | 22.1 | 125000 | 4.2 | 11.25 | No
202350503 | Ground Water | AAON, Inc. | M2-014-4-H-BCBC-V0-10-000-A |  | 135000 | 22 | 124600 | 4.2 | 11.25 | No
202350512 | Ground Water | AAON, Inc. | WH-060-1-H-DCAC-C0-10-200-A |  | 66200 | 23.3 | 56800 | 4.7 | 5.5167 | No
202350513 | Ground Water | AAON, Inc. | WH-060-2-H-DCAC-C0-10-200-A |  | 66200 | 23.3 | 56800 | 4.7 | 5.5167 | No
202449818 | Ground Water | WaterFurnace | UBV/UBH060**4*1 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449819 | Ground Water | WaterFurnace | UBV/UBH060**0*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449820 | Ground Water | WaterFurnace | UBV/UBH060**3*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449821 | Ground Water | WaterFurnace | UBV/UBH060**4*4 |  | 67000 | 22 | 55000 | 4.2 | 5.5833 | No
202449826 | Ground Water | WaterFurnace | UBV/UBH070**0*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449827 | Ground Water | WaterFurnace | UBV/UBH070**3*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449828 | Ground Water | WaterFurnace | UBV/UBH070**4*1 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449829 | Ground Water | WaterFurnace | UBV/UBH070**0*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449830 | Ground Water | WaterFurnace | UBV/UBH070**3*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
202449831 | Ground Water | WaterFurnace | UBV/UBH070**4*4 |  | 75000 | 22 | 64000 | 4.2 | 6.25 | No
5646343 | Ground Water | GEOCOMFORT | GXT024D |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | Yes
5646344 | Ground Water | HYDRON MODULE | HXT024D |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | Yes
5646345 | Ground Water | TETCO | TXT024D |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | Yes
5646346 | Ground Water | GEOCOMFORT | GXT024D2 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646347 | Ground Water | HYDRON MODULE | HXT024D2 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646348 | Ground Water | TETCO | TXT024D2 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646349 | Ground Water | GEOCOMFORT | GXT024D3 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646350 | Ground Water | HYDRON MODULE | HXT024D3 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646351 | Ground Water | TETCO | TXT024D3 |  | 29600 | 26.9 | 24700 | 5.2 | 2.4667 | No
5646371 | Ground Water | GEOCOMFORT | GXT036D |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | Yes
5646372 | Ground Water | HYDRON MODULE | HXT036D |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | Yes
5646373 | Ground Water | TETCO | TXT036D |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | Yes
5646374 | Ground Water | GEOCOMFORT | GXT036D2 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
203383886 | Ground Water | CARRIER | 50PSV048***3/CA |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383887 | Ground Water | CARRIER | 50PSV048***5/EA |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383888 | Ground Water | CARRIER | 50PSV048***6/FA |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383889 | Ground Water | CARRIER | 50PSH048***3/CA |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383890 | Ground Water | CARRIER | 50PSH048***5/EA |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383891 | Ground Water | CARRIER | 50PSH048***6/FA |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383892 | Ground Water | FHP | EP018-1VT*******B |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203383893 | Ground Water | FHP | EP018-2VT*******B |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | No
203383894 | Ground Water | FHP | EP018-1HZ*******B |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203383895 | Ground Water | FHP | EP018-2HZ*******B |  | 21300 | 24.7 | 17700 | 4.4 | 1.775 | No
203383896 | Ground Water | FHP | EP042-1VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383897 | Ground Water | FHP | EP042-3VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383898 | Ground Water | FHP | EP042-4VT*******B |  | 44100 | 25.6 | 35000 | 4.65 | 3.675 | No
203383899 | Ground Water | FHP | EP042-1HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383900 | Ground Water | FHP | EP042-3HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
203383901 | Ground Water | FHP | EP042-4HZ*******B |  | 44100 | 27.2 | 35000 | 5 | 3.675 | No
217903461 | Ground Water | WaterFurnace | V5R060*D4**4* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903462 | Ground Water | WaterFurnace | V5R060*D4**5* |  | 65700 | 23.2 | 53900 | 4.5 | 5.475 | No
217903463 | Ground Water | WaterFurnace | V5R072*D4**1* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903464 | Ground Water | WaterFurnace | V5R072*D4**4* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903465 | Ground Water | WaterFurnace | V5R072*D4**5* |  | 75000 | 22.2 | 68500 | 4.4 | 6.25 | No
217903466 | Ground Water | WaterFurnace | V5R096*T4**5* |  | 96600 | 24.9 | 85800 | 4.5 | 8.05 | No
217903467 | Ground Water | WaterFurnace | V5R120*T4**5* |  | 128500 | 23.3 | 113700 | 4.5 | 10.7083 | No
202146936 | Ground Water | GEOCOMFORT | GZS018*****1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | Yes
202146939 | Ground Water | HYDRON MODULE | HZS018*****1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | Yes
202146942 | Ground Water | TETCO | TZS018*****1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | Yes
202146943 | Ground Water | GEOCOMFORT | GZS024 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | Yes
202146944 | Ground Water | GEOCOMFORT | GZS024*2 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146945 | Ground Water | GEOCOMFORT | GZS024*3 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146946 | Ground Water | GEOCOMFORT | GZS024*4 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146947 | Ground Water | GEOCOMFORT | GZS024*A |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146948 | Ground Water | GEOCOMFORT | GZS024*****1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | Yes
202146949 | Ground Water | GEOCOMFORT | GZS024*2***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146950 | Ground Water | GEOCOMFORT | GZS024*3***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146951 | Ground Water | GEOCOMFORT | GZS024*A***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146952 | Ground Water | HYDRON MODULE | HZS024 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | Yes
202146953 | Ground Water | HYDRON MODULE | HZS024*2 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146954 | Ground Water | HYDRON MODULE | HZS024*3 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146955 | Ground Water | HYDRON MODULE | HZS024*4 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146956 | Ground Water | HYDRON MODULE | HZS024*A |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146957 | Ground Water | HYDRON MODULE | HZS024*****1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | Yes
202146958 | Ground Water | HYDRON MODULE | HZS024*2***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146959 | Ground Water | HYDRON MODULE | HZS024*3***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146960 | Ground Water | HYDRON MODULE | HZS024*A***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146961 | Ground Water | TETCO | TZS024 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | Yes
202146962 | Ground Water | TETCO | TZS024*2 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146963 | Ground Water | TETCO | TZS024*3 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146964 | Ground Water | TETCO | TZS024*4 |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146965 | Ground Water | TETCO | TZS024*A |  | 27400 | 22.9 | 23700 | 4.3 | 2.2833 | No
202146966 | Ground Water | TETCO | TZS024*****1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | Yes
202146967 | Ground Water | TETCO | TZS024*2***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146968 | Ground Water | TETCO | TZS024*3***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146969 | Ground Water | TETCO | TZS024*A***1 |  | 27900 | 26.3 | 22900 | 4.8 | 2.325 | No
202146970 | Ground Water | GEOCOMFORT | GZS030 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | Yes
202146971 | Ground Water | GEOCOMFORT | GZS030*2 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146972 | Ground Water | GEOCOMFORT | GZS030*3 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146973 | Ground Water | GEOCOMFORT | GZS030*4 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146974 | Ground Water | GEOCOMFORT | GZS030*A |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146975 | Ground Water | GEOCOMFORT | GZS030*****1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | Yes
202146976 | Ground Water | GEOCOMFORT | GZS030*2***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202146977 | Ground Water | HYDRON MODULE | HZS030 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | Yes
202146978 | Ground Water | HYDRON MODULE | HZS030*2 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146979 | Ground Water | HYDRON MODULE | HZS030*3 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146980 | Ground Water | HYDRON MODULE | HZS030*4 |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146981 | Ground Water | HYDRON MODULE | HZS030*A |  | 31800 | 23.4 | 27900 | 4.5 | 2.65 | No
202146982 | Ground Water | HYDRON MODULE | HZS030*****1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | Yes
206438779 | Ground Water | FHP | EP007-2HZ/VT*-*****B |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438780 | Ground Water | FHP | EP007-1HZ/VT*-*****B |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
206438781 | Ground Water | FHP | EP009-1HZ/VT*-*****B |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438782 | Ground Water | FHP | EP009-2HZ/VT*-*****B |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
206438783 | Ground Water | FHP | EP012-1HZ/VT*-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438784 | Ground Water | FHP | EP015-1HZ/VT*-*****B |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438785 | Ground Water | FHP | EP015-2HZ/VT*-*****B |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
206438786 | Ground Water | FHP | EP030-2HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438787 | Ground Water | FHP | EP030-4HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438788 | Ground Water | FHP | EP030-3HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438789 | Ground Water | FHP | EP030-1HZ/VT*-*****B |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
206438790 | Ground Water | FHP | EP060-4HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438791 | Ground Water | FHP | EP060-3HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438792 | Ground Water | FHP | EP060-1HZ/VT*-*****B |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
206438793 | Ground Water | FHP | EP070-1HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438794 | Ground Water | FHP | EP070-3HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
206438795 | Ground Water | FHP | EP070-4HZ/VT*-*****B |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
207335253 | Ground Water | GEOSTAR | 161/162K049**1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207335255 | Ground Water | GEOSTAR | 161/162J072**1*(1,4)***** |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207335335 | Ground Water | GEOSTAR | 111J049**1*(1,2) |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | Yes
207335338 | Ground Water | GEOSTAR | 111K038**1*(1,2)* |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | Yes
207335397 | Ground Water | GeoSmart Energy | GT026**1*(1,4)*J |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207335398 | Ground Water | GeoSmart Energy | GT038**1*(1,2,4)*K |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
217351900 | Ground Water | KEEPRITE | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351901 | Ground Water | KEEPRITE | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351903 | Ground Water | KEEPRITE | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351904 | Ground Water | KEEPRITE | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351905 | Ground Water | KEEPRITE | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351906 | Ground Water | KEEPRITE | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351907 | Ground Water | KEEPRITE | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351908 | Ground Water | KEEPRITE | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351909 | Ground Water | KEEPRITE | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351911 | Ground Water | KEEPRITE | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351912 | Ground Water | KEEPRITE | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351914 | Ground Water | KEEPRITE | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351916 | Ground Water | KEEPRITE | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
10298941 | Ground Water | WaterFurnace | UVV/UVH048**0*1 |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
10298942 | Ground Water | WaterFurnace | UVV/UVH048**3*1 |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
10298943 | Ground Water | WaterFurnace | UVV/UVH048**4*1 |  | 53000 | 26 | 46000 | 4.7 | 4.4167 | No
10298944 | Ground Water | WaterFurnace | UVV/UVH060**0*1 |  | 63000 | 24 | 57000 | 4.2 | 5.25 | No
10298946 | Ground Water | WaterFurnace | UVV/UVH060**3*1 |  | 63000 | 24 | 57000 | 4.2 | 5.25 | No
10298947 | Ground Water | WaterFurnace | UVV/UVH060**4*1 |  | 63000 | 24 | 57000 | 4.2 | 5.25 | No
10304639 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10304640 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10304641 | Ground Water | GeoSmart Energy | GTZ026*1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10304642 | Ground Water | GEOSTAR | 103H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
10304646 | Ground Water | GEOSTAR | 103H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10304657 | Ground Water | GeoSmart Energy | GTZ026*1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
10305457 | Ground Water | GEOSTAR | 104H026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10305458 | Ground Water | GEOSTAR | 104H026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10316642 | Ground Water | YORK BY JOHNSON CONTROLS | YAST026**1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10316643 | Ground Water | GeoSmart Energy | GTS026*1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10316644 | Ground Water | YORK BY JOHNSON CONTROLS | YAST026**1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10316645 | Ground Water | GeoSmart Energy | GTS026*1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
10316654 | Ground Water | YORK BY JOHNSON CONTROLS | YAST049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316655 | Ground Water | GEOSTAR | 104H049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316656 | Ground Water | GeoSmart Energy | GTS049*1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316657 | Ground Water | YORK BY JOHNSON CONTROLS | YAST049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316658 | Ground Water | GeoSmart Energy | GTS049*1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316660 | Ground Water | GEOSTAR | 104H049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
10316661 | Ground Water | YORK BY JOHNSON CONTROLS | YAST064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316662 | Ground Water | GEOSTAR | 104H064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316663 | Ground Water | GeoSmart Energy | GTS064*1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316664 | Ground Water | YORK BY JOHNSON CONTROLS | YAST064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316666 | Ground Water | GEOSTAR | 104H064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316667 | Ground Water | GeoSmart Energy | GTS064*1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
10316672 | Ground Water | GeoSmart Energy | GTS072*1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10316673 | Ground Water | GEOSTAR | 104H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10316674 | Ground Water | YORK BY JOHNSON CONTROLS | YAST072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10316700 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10316701 | Ground Water | GEOSTAR | 103H072**1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10316702 | Ground Water | GeoSmart Energy | GTZ072*1 | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
10318010 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS022**1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
10318016 | Ground Water | GeoSmart Energy | GSZ022*1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
10318017 | Ground Water | GEOSTAR | 103H022**1 | SAH022* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
10318018 | Ground Water | GeoSmart Energy | GSZ022*1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | Yes
10318019 | Ground Water | GEOSTAR | 103H022**1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
10318020 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS022**1 | SRAA026* | 20400 | 26.5 | 18100 | 4.8 | 1.7 | No
10318021 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS030**1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
10318022 | Ground Water | GEOSTAR | 103H030**1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
10318023 | Ground Water | GeoSmart Energy | GSZ030*1 | SAH030* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
10318024 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS030**1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
10318025 | Ground Water | GeoSmart Energy | GSZ030*1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | Yes
10318026 | Ground Water | GEOSTAR | 103H030**1 | SRAA026* | 26900 | 25.6 | 24900 | 4.8 | 2.2417 | No
10318045 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS048**1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
10318046 | Ground Water | GeoSmart Energy | GSZ048*1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
10318047 | Ground Water | GEOSTAR | 103H048**1 | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | Yes
202330542 | Ground Water | AAON, Inc. | M2-004-4-H-BCBC-V0-10-000-A |  | 57500 | 26.1 | 46700 | 4.4 | 4.7917 | No
202330543 | Ground Water | AAON, Inc. | M2-004-4-H-DCAC-S0-10-000-A |  | 54200 | 23.5 | 45800 | 4.2 | 4.5167 | No
202330544 | Ground Water | AAON, Inc. | M2-004-4-H-DCBC-S0-10-000-A |  | 56200 | 23.9 | 46200 | 4.4 | 4.6833 | No
202330547 | Ground Water | AAON, Inc. | M2-005-1-H-DCAC-S0-10-000-A |  | 62100 | 23.7 | 50000 | 4.1 | 5.175 | No
202330548 | Ground Water | AAON, Inc. | M2-005-1-H-DCBC-S0-10-000-A |  | 65000 | 23.5 | 50400 | 4.1 | 5.4167 | No
202330551 | Ground Water | AAON, Inc. | M2-005-2-H-DCAC-S0-10-000-A |  | 62100 | 23.7 | 50000 | 4.1 | 5.175 | No
202330552 | Ground Water | AAON, Inc. | M2-005-2-H-DCBC-S0-10-000-A |  | 65000 | 23.5 | 50400 | 4.1 | 5.4167 | No
202330555 | Ground Water | AAON, Inc. | M2-005-3-H-DCAC-S0-10-000-A |  | 62100 | 23.7 | 50000 | 4.1 | 5.175 | No
202330556 | Ground Water | AAON, Inc. | M2-005-3-H-DCBC-S0-10-000-A |  | 65000 | 23.5 | 50400 | 4.1 | 5.4167 | No
202330559 | Ground Water | AAON, Inc. | M2-005-4-H-DCAC-S0-10-000-A |  | 62100 | 23.7 | 50000 | 4.1 | 5.175 | No
202330560 | Ground Water | AAON, Inc. | M2-005-4-H-DCBC-S0-10-000-A |  | 65000 | 23.5 | 50400 | 4.1 | 5.4167 | No
202330562 | Ground Water | AAON, Inc. | M2-006-2-H-ACBC-C0-10-000-A |  | 74200 | 22.7 | 54300 | 4.1 | 6.1833 | No
202330564 | Ground Water | AAON, Inc. | M2-006-2-H-BCBC-V0-10-000-A |  | 75000 | 22.6 | 54000 | 4.1 | 6.25 | No
202330566 | Ground Water | AAON, Inc. | M2-006-3-H-ACBC-C0-10-000-A |  | 74200 | 22.7 | 54300 | 4.1 | 6.1833 | No
202330568 | Ground Water | AAON, Inc. | M2-006-3-H-BCBC-V0-10-000-A |  | 75000 | 22.6 | 54000 | 4.1 | 6.25 | No
202330570 | Ground Water | AAON, Inc. | M2-006-4-H-ACBC-C0-10-000-A |  | 74200 | 22.7 | 54300 | 4.1 | 6.1833 | No
3706350 | Ground Water | GEOSTAR | ZS015**0*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
3706351 | Ground Water | GEOSTAR | ZS015**2*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
3706369 | Ground Water | GEOSTAR | ZS018**0*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
3706370 | Ground Water | GEOSTAR | ZS018**2*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
3706371 | Ground Water | GEOSTAR | ZS023**0*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3706373 | Ground Water | GEOSTAR | ZS023**2*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3706374 | Ground Water | GEOSTAR | ZS023**3*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3706375 | Ground Water | GEOSTAR | ZS023**4*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3706376 | Ground Water | GEOSTAR | ZS024**0*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
3706377 | Ground Water | GEOSTAR | ZS024**2*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
3706378 | Ground Water | GEOSTAR | ZS024**3*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
3706379 | Ground Water | GEOSTAR | ZS024**4*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
3706380 | Ground Water | GEOSTAR | ZS030**0*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3706381 | Ground Water | GEOSTAR | ZS030**2*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3706382 | Ground Water | GEOSTAR | ZS030**3*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3706383 | Ground Water | GEOSTAR | ZS030**4*1 |  | 32900 | 23.9 | 28300 | 4.4 | 2.7417 | No
3706384 | Ground Water | GEOSTAR | ZS036**0*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3706385 | Ground Water | GEOSTAR | ZS036**3*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3706387 | Ground Water | GEOSTAR | ZS036**4*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3706391 | Ground Water | GEOSTAR | ZS042**0*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3706392 | Ground Water | GEOSTAR | ZS042**3*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3706393 | Ground Water | GEOSTAR | ZS042**4*1 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
3706394 | Ground Water | GEOSTAR | ZS048**0*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3706395 | Ground Water | GEOSTAR | ZS048**3*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3706396 | Ground Water | GEOSTAR | ZS048**4*1 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
3811671 | Ground Water | WaterFurnace | USV/USH024**2*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
3811673 | Ground Water | WaterFurnace | USV/USH024**3*1 |  | 26400 | 23.4 | 22300 | 4.5 | 2.2 | No
217351757 | Ground Water | BRYANT | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351758 | Ground Water | BRYANT | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351759 | Ground Water | BRYANT | GZ036SA*C******1 | F(T,G,E)5(A,B)***36*** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351760 | Ground Water | BRYANT | GZ036SA*N******1 | F(T,G,E)5(A,B)***36*** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351761 | Ground Water | BRYANT | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351762 | Ground Water | BRYANT | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351763 | Ground Water | BRYANT | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351765 | Ground Water | BRYANT | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351766 | Ground Water | BRYANT | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351768 | Ground Water | BRYANT | GZ024SA*C******1 | CAAMP2***AMA | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351769 | Ground Water | BRYANT | GZ024SA*N******1 | CAAMP2***AMA | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351770 | Ground Water | BRYANT | GZ036SA*C******1 | CAAMP3***AMA | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351771 | Ground Water | BRYANT | GZ036SA*N******1 | CAAMP3***AMA | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351772 | Ground Water | BRYANT | GZ048SA*C******1 | CAAMP4***AMA | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351773 | Ground Water | BRYANT | GZ048SA*N******1 | CAAMP4***AMA | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351774 | Ground Water | BRYANT | GZ060SA*C******1 | CAAMP6***AMA | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351776 | Ground Water | BRYANT | GZ072SA*C******1 | CAAMP6***AMA | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351777 | Ground Water | BRYANT | GZ072SA*N******1 | CAAMP6***AMA | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351779 | Ground Water | BRYANT | GW024WA********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351781 | Ground Water | BRYANT | GW048WA********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
217351784 | Ground Water | ARCOAIRE | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351785 | Ground Water | ARCOAIRE | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351786 | Ground Water | ARCOAIRE | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
202147073 | Ground Water | TETCO | TZS060*****1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | Yes
202147074 | Ground Water | TETCO | TZS060*2***1 |  | 60500 | 22.3 | 58600 | 4.3 | 5.0417 | No
202147690 | Ground Water | GEOCOMFORT | GZT030*A |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202147691 | Ground Water | HYDRON MODULE | HZT030*A |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202147692 | Ground Water | TETCO | TZT030*A |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | No
202147693 | Ground Water | TETCO | TZT048*A |  | 52200 | 22.1 | 45900 | 4.3 | 4.35 | No
202147694 | Ground Water | GEOCOMFORT | GZT060*A |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202147695 | Ground Water | HYDRON MODULE | HZT060*A |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202147696 | Ground Water | TETCO | TZT060*A |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | No
202147697 | Ground Water | GEOCOMFORT | GZS015*A***1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | No
202147698 | Ground Water | HYDRON MODULE | HZS015*A***1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | No
202147699 | Ground Water | TETCO | TZS015*A***1 |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | No
202147700 | Ground Water | GEOCOMFORT | GZS018*A***1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | No
202147701 | Ground Water | HYDRON MODULE | HZS018*A***1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | No
202147702 | Ground Water | TETCO | TZS018*A***1 |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | No
202147703 | Ground Water | GEOCOMFORT | GZS030*3***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147704 | Ground Water | GEOCOMFORT | GZS030*A***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147705 | Ground Water | HYDRON MODULE | HZS030*3***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147706 | Ground Water | HYDRON MODULE | HZS030*A***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147707 | Ground Water | TETCO | TZS030*3***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147708 | Ground Water | TETCO | TZS030*A***1 |  | 30900 | 24.6 | 26300 | 4.7 | 2.575 | No
202147709 | Ground Water | GEOCOMFORT | GZS042*3***1 |  | 43700 | 25.6 | 37500 | 4.5 | 3.6417 | No
206570654 | Ground Water | GEOSTAR | 141/142C060**1*1 |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
206598629 | Ground Water | GeoSmart Energy | VI036**1*(1,2)** |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
206598631 | Ground Water | GeoSmart Energy | VI060**1*1* |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
206598632 | Ground Water | YORK BY JOHNSON CONTROLS | YAFV036**1*(1,2)** |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | Yes
206598634 | Ground Water | YORK BY JOHNSON CONTROLS | YAFV060**1*1* |  | 60000 | 27.1 | 66000 | 4.3 | 5 | Yes
206608717 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ048J1* | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
206608718 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ048J1* | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
206608719 | Ground Water | GEOSTAR | 103J048**1* | SAH048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
206608720 | Ground Water | GEOSTAR | 103J048**1* | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
206608721 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ060J1* | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
206608722 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ060J1* | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
206608723 | Ground Water | GEOSTAR | 103J060**1* | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
206608724 | Ground Water | GEOSTAR | 103J060**1* | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
206611110 | Ground Water | COMFORT-AIRE | HEH/V024C |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
206611111 | Ground Water | CENTURY | HEH/V024C |  | 26500 | 21.7 | 23000 | 4.1 | 2.2083 | Yes
206611114 | Ground Water | COMFORT-AIRE | HEH/V036C |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
206611115 | Ground Water | CENTURY | HEH/V036C |  | 38200 | 22.3 | 35100 | 4.3 | 3.1833 | Yes
206611116 | Ground Water | COMFORT-AIRE | HEH/V042C |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
206611117 | Ground Water | CENTURY | HEH/V042C |  | 46300 | 21.3 | 42300 | 4.1 | 3.8583 | Yes
206611120 | Ground Water | COMFORT-AIRE | HEH/V060C |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
206611121 | Ground Water | CENTURY | HEH/V060C |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
205503115 | Ground Water | BOSCH-GEO | SM024-1CS*******A | BVA-24WN1-M20 | 28600 | 22.1 | 24200 | 4.8 | 2.3833 | Yes
205503116 | Ground Water | BOSCH-GEO | SM024-1CS*******A | BMAC2430BNTD | 27400 | 23.2 | 24000 | 4.8 | 2.2833 | Yes
205503117 | Ground Water | BOSCH-GEO | SM036-1CSC-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | Yes
205503119 | Ground Water | BOSCH-GEO | LM024-1CS*******A | BVA-24WN1-M20 | 28600 | 22.1 | 24200 | 4.8 | 2.3833 | No
205503120 | Ground Water | BOSCH-GEO | LM024-1CS*******A | BMAC2430BNTD | 27400 | 23.2 | 24000 | 4.8 | 2.2833 | No
205503121 | Ground Water | BOSCH-GEO | LM036-1CSC-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | No
205503123 | Ground Water | BOSCH | SM024-1CS*******A | BVA-24WN1-M20 | 28600 | 22.1 | 24200 | 4.8 | 2.3833 | Yes
205503124 | Ground Water | BOSCH | SM024-1CS*******A | BMAC2430BNTD | 27400 | 23.2 | 24000 | 4.8 | 2.2833 | Yes
205503125 | Ground Water | BOSCH | SM036-1CSC-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | Yes
205503127 | Ground Water | FHP | LM024-1CS*******A | BVA-24WN1-M20 | 28600 | 22.1 | 24200 | 4.8 | 2.3833 | No
205503128 | Ground Water | FHP | LM024-1CS*******A | BMAC2430BNTD | 27400 | 23.2 | 24000 | 4.8 | 2.2833 | No
205503129 | Ground Water | FHP | LM036-1CSC-*****B | BVA-36WN1-M20 | 38400 | 21.3 | 36500 | 4.5 | 3.2 | No
205652453 | Ground Water | BOSCH-GEO | SM048-1CS*-*****A | BVA-48WN1-M20 | 54000 | 23.1 | 47000 | 4.8 | 4.5 | Yes
205652454 | Ground Water | BOSCH-GEO | SM060-1CS*-*****A | BVA-60WN1-M20 | 64800 | 21.8 | 62300 | 4.6 | 5.4 | Yes
205652455 | Ground Water | BOSCH-GEO | SM048-1CS*-*****A | BMAC4248CNTF | 52000 | 21.6 | 45500 | 4.5 | 4.3333 | Yes
205652457 | Ground Water | BOSCH-GEO | LM048-1CS*-*****A | BVA-48WN1-M20 | 54000 | 23.1 | 47000 | 4.8 | 4.5 | No
205652458 | Ground Water | BOSCH-GEO | LM060-1CS*-*****A | BVA-60WN1-M20 | 64800 | 21.8 | 62300 | 4.6 | 5.4 | No
205652459 | Ground Water | BOSCH-GEO | LM048-1CS*-*****A | BMAC4248CNTF | 52000 | 21.6 | 45500 | 4.5 | 4.3333 | No
205652461 | Ground Water | BOSCH | SM048-1CS*-*****A | BVA-48WN1-M20 | 54000 | 23.1 | 47000 | 4.8 | 4.5 | Yes
205652462 | Ground Water | BOSCH | SM060-1CS*-*****A | BVA-60WN1-M20 | 64800 | 21.8 | 62300 | 4.6 | 5.4 | Yes
205652463 | Ground Water | BOSCH | SM048-1CS*-*****A | BMAC4248CNTF | 52000 | 21.6 | 45500 | 4.5 | 4.3333 | Yes
205652465 | Ground Water | FHP | LM048-1CS*-*****A | BVA-48WN1-M20 | 54000 | 23.1 | 47000 | 4.8 | 4.5 | No
205652466 | Ground Water | FHP | LM060-1CS*-*****A | BVA-60WN1-M20 | 64800 | 21.8 | 62300 | 4.6 | 5.4 | No
205652467 | Ground Water | FHP | LM048-1CS*-*****A | BMAC4248CNTF | 52000 | 21.6 | 45500 | 4.5 | 4.3333 | No
214595581 | Ground Water | AAON, Inc. | SB-004-2-0-GCBC-V0-10-000-A |  | 48100 | 21.3 | 48300 | 4.1 | 4.0083 | No
4660771 | Ground Water | TRANE | GEVE0728 |  | 84800 | 22.85 | 70200 | 4.18 | 7.0667 | No
4660776 | Ground Water | TRANE | GEVE0908 |  | 98600 | 22.91 | 83600 | 4.1 | 8.2167 | No
4947178 | Ground Water | TRANE | VSVE0241 |  | 27800 | 33.24 | 24400 | 5.2 | 2.3167 | No
4947179 | Ground Water | TRANE | VSVE0242 |  | 27800 | 33.24 | 24400 | 5.2 | 2.3167 | No
4947180 | Ground Water | TRANE | VSVE0244 |  | 27800 | 33.24 | 24400 | 5.2 | 2.3167 | No
4947183 | Ground Water | TRANE | VSVE0331 |  | 36600 | 24.67 | 32400 | 4.77 | 3.05 | No
4947184 | Ground Water | TRANE | VSVE0332 |  | 36600 | 24.67 | 32400 | 4.77 | 3.05 | No
4947185 | Ground Water | TRANE | VSVE0334 |  | 36600 | 24.67 | 32400 | 4.77 | 3.05 | No
4947240 | Ground Water | TRANE | VSVE0501 |  | 57800 | 26.19 | 54600 | 4.58 | 4.8167 | No
4947241 | Ground Water | TRANE | VSVE0502 |  | 57800 | 26.19 | 54600 | 4.58 | 4.8167 | No
4947242 | Ground Water | TRANE | VSVE0504 |  | 57800 | 26.19 | 54600 | 4.58 | 4.8167 | No
215268313 | Ground Water | WaterFurnace | V3A(V/H)006*R0**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
215268316 | Ground Water | WaterFurnace | V3A(V/H)015*R0**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
6502003 | Ground Water | GEOSTAR | GBV/GBH072**0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6502004 | Ground Water | GEOSTAR | GBV/GBH072**3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6502005 | Ground Water | GEOSTAR | GBV/GBH072**3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6502006 | Ground Water | GEOSTAR | GBV/GBH072**4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6502007 | Ground Water | GEOSTAR | GBV/GBH072**4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
6674620 | Ground Water | BOSCH | LM024-1CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
6674621 | Ground Water | BOSCH | LM024-3CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
6674622 | Ground Water | BOSCH | LM024-2CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
6674623 | Ground Water | BOSCH | LM024-4CF/HZ/VT*-*****A |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
6676515 | Ground Water | BOSCH | LM036-1VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
6676516 | Ground Water | BOSCH | LM036-3VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
6676518 | Ground Water | BOSCH | LM036-2VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
6676519 | Ground Water | BOSCH | LM036-4VT/CF/HZ*-*****A |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
6677645 | Ground Water | BOSCH | LM048-1VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
6677682 | Ground Water | BOSCH | LM048-3VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
6677754 | Ground Water | BOSCH | LM048-4VT/CF/HZ*-*****A |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
6677875 | Ground Water | BOSCH | LM060-1VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
6677876 | Ground Water | BOSCH | LM060-3VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
6677878 | Ground Water | BOSCH | LM060-4VT/CF/HZ*-*****A |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
6677886 | Ground Water | BOSCH | LM070-1VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
6677887 | Ground Water | BOSCH | LM070-3VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
6677889 | Ground Water | BOSCH | LM070-4VT/CF/HZ*-*****A |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
202547467 | Ground Water | FHP | EC096-1VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202547468 | Ground Water | FHP | EC096-3VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
202547469 | Ground Water | FHP | EC096-4VT/HZN-*****B |  | 106500 | 21.15 | 94700 | 4.3 | 8.875 | No
216767332 | Ground Water | TETCO | TYT072* |  | 75400 | 21.7 | 70400 | 4.5 | 6.2833 | Yes
216767333 | Ground Water | HYDRON MODULE | HVT024* |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
216767334 | Ground Water | HYDRON MODULE | HVT030* |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
216767335 | Ground Water | HYDRON MODULE | HVT036* |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
216767336 | Ground Water | HYDRON MODULE | HVT042* |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
216767337 | Ground Water | HYDRON MODULE | HVT048* |  | 53600 | 24.5 | 48500 | 4.9 | 4.4667 | Yes
216767338 | Ground Water | HYDRON MODULE | HYT024* |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
216767339 | Ground Water | HYDRON MODULE | HYT036* |  | 42300 | 27.9 | 35500 | 5.4 | 3.525 | Yes
216767340 | Ground Water | HYDRON MODULE | HYT048* |  | 55200 | 24.9 | 46500 | 5 | 4.6 | Yes
216767341 | Ground Water | HYDRON MODULE | HVT060* |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
216767342 | Ground Water | HYDRON MODULE | HYT060* |  | 66900 | 23.8 | 60700 | 4.8 | 5.575 | Yes
216767344 | Ground Water | HYDRON MODULE | HYT072* |  | 75400 | 21.7 | 70400 | 4.5 | 6.2833 | Yes
216772562 | Ground Water | Enertech | EBS018* | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | Yes
216772563 | Ground Water | Enertech | EBT024* | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | Yes
216772564 | Ground Water | Enertech | EBT036* | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | Yes
216772565 | Ground Water | Enertech | EBT048* | EAD048 | 51500 | 22.5 | 51300 | 4.5 | 4.2917 | Yes
216772566 | Ground Water | Enertech | EVS009* |  | 11900 | 24.2 | 10150 | 4.43 | 0.99167 | Yes
216772567 | Ground Water | Enertech | EVS012* |  | 13400 | 24.1 | 12100 | 4.3 | 1.1167 | Yes
216772568 | Ground Water | Enertech | EVS018* |  | 24025 | 33.6 | 19600 | 5.32 | 2.0021 | Yes
216772569 | Ground Water | Enertech | EVT024* |  | 27825 | 27.3 | 23900 | 4.96 | 2.3188 | Yes
216772570 | Ground Water | Enertech | EVT030* |  | 35000 | 25.8 | 30300 | 4.72 | 2.9167 | Yes
216772571 | Ground Water | Enertech | EVT036* |  | 41050 | 24.3 | 36900 | 4.7 | 3.4208 | Yes
216772572 | Ground Water | Enertech | EVT042* |  | 49200 | 25.3 | 41900 | 4.89 | 4.1 | Yes
216772573 | Ground Water | Enertech | EVT048* |  | 53600 | 24.5 | 48500 | 4.9 | 4.4667 | Yes
5339321 | Ground Water | TTHERM GEO | TVA-036-1* |  | 42000 | 22.89 | 42600 | 4.28 | 3.5 | No
5339322 | Ground Water | TTHERM GEO | TVA-048-1* |  | 55400 | 22.21 | 57300 | 4.1 | 4.6167 | No
5339323 | Ground Water | TTHERM GEO | TVA-060-1* |  | 65000 | 21.4 | 63500 | 4.1 | 5.4167 | No
5440541 | Ground Water | GEOCOMFORT | GXT060D |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | Yes
5440542 | Ground Water | HYDRON MODULE | HXT060D |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | Yes
5440543 | Ground Water | TETCO | TXT060D |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | Yes
5440554 | Ground Water | GEOCOMFORT | GXT072D |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | Yes
5440555 | Ground Water | HYDRON MODULE | HXT072D |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | Yes
5440557 | Ground Water | TETCO | TXT072D |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | Yes
5440573 | Ground Water | GEOCOMFORT | GXT060D2 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440574 | Ground Water | HYDRON MODULE | HXT060D2 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440575 | Ground Water | TETCO | TXT060D2 |  | 67700 | 22.4 | 60000 | 4.5 | 5.6417 | No
5440576 | Ground Water | GEOCOMFORT | GXT072D2 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5440577 | Ground Water | HYDRON MODULE | HXT072D2 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
5440578 | Ground Water | TETCO | TXT072D2 |  | 75600 | 21.1 | 70300 | 4.3 | 6.3 | No
8737982 | Ground Water | GEOCOMFORT | GVS060 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | Yes
8737983 | Ground Water | HYDRON MODULE | HVS060 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | Yes
8737984 | Ground Water | TETCO | TVS060 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | Yes
8737985 | Ground Water | GEOCOMFORT | GVS060*2 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737986 | Ground Water | HYDRON MODULE | HVS060*2 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737987 | Ground Water | TETCO | TVS060*2 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737988 | Ground Water | GEOCOMFORT | GVS060*3 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737989 | Ground Water | HYDRON MODULE | HVS060*3 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737990 | Ground Water | TETCO | TVS060*3 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737991 | Ground Water | GEOCOMFORT | GVS060*4 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737992 | Ground Water | HYDRON MODULE | HVS060*4 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8737993 | Ground Water | TETCO | TVS060*4 |  | 63300 | 21.3 | 58700 | 4.3 | 5.275 | No
8738031 | Ground Water | GEOCOMFORT | GVT060 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
8738032 | Ground Water | HYDRON MODULE | HVT060 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
8738033 | Ground Water | TETCO | TVT060 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
8738034 | Ground Water | GEOCOMFORT | GVT060*2 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738035 | Ground Water | HYDRON MODULE | HVT060*2 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
8738036 | Ground Water | TETCO | TVT060*2 |  | 64200 | 22 | 57500 | 4.5 | 5.35 | No
203495474 | Ground Water | GEOSTAR | 103J049**1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
203696349 | Ground Water | HYDROTECH | WSV6024A |  | 25400 | 24 | 22000 | 4.1 | 2.1167 | No
203696351 | Ground Water | HYDROTECH | WSV6036A |  | 41500 | 24 | 35500 | 4.1 | 3.4583 | No
203817319 | Ground Water | BOSCH-GEO | CE061-1HZC-*****B |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | No
203818209 | Ground Water | CARRIER | GP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | No
203818210 | Ground Water | BRYANT | GP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818211 | Ground Water | HEIL | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | No
203818212 | Ground Water | ARCOAIRE | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818214 | Ground Water | KEEPRITE | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818215 | Ground Water | TEMPSTAR | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818216 | Ground Water | COMFORTMAKER | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818217 | Ground Water | DAY & NIGHT | HP060H**C***1**1 |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203818278 | Ground Water | BOSCH | CE061-1HZC-*****B |  | 68000 | 21.2 | 61000 | 4.3 | 5.6667 | Yes
203993050 | Ground Water | GEOSTAR | 111H049**1*(1,2) |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | No
203995293 | Ground Water | HYDROTECH | WSV6042A |  | 46500 | 24 | 39000 | 4.2 | 3.875 | No
212587993 | Ground Water | HYDROTECH | HRCX09*-7 |  | 11500 | 23.9 | 8800 | 4.1 | 0.95833 | No
212587994 | Ground Water | AE Air | HRCX09*-7 |  | 11500 | 23.9 | 8800 | 4.1 | 0.95833 | No
213087558 | Ground Water | WaterFurnace | NDS049J1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
213087559 | Ground Water | WaterFurnace | NDS049J1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
213087562 | Ground Water | WaterFurnace | NDS064J1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
213087563 | Ground Water | WaterFurnace | NDS064J1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
213154439 | Ground Water | GeoSmart Energy | GTS026*1******K | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
213154440 | Ground Water | GeoSmart Energy | GTS026*1******K | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
213154441 | Ground Water | GeoSmart Energy | GTS049*1******K | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
213154442 | Ground Water | GeoSmart Energy | GTS049*1******K | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
213154443 | Ground Water | GeoSmart Energy | GTS072*1******K | SRAA060* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
213154444 | Ground Water | GeoSmart Energy | GTS072*1******K | SAH066* | 70000 | 22 | 67500 | 4.1 | 5.8333 | No
213154445 | Ground Water | GeoSmart Energy | GTS064*1******K | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
216625816 | Ground Water | GeoSmart Energy | S5A(V/H)036*S4**2 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625817 | Ground Water | GeoSmart Energy | S5A(V/H)036*S4**4 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
216625818 | Ground Water | GeoSmart Energy | S5A(V/H)042*D0**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625819 | Ground Water | GeoSmart Energy | S5A(V/H)042*D0**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625820 | Ground Water | GeoSmart Energy | S5A(V/H)042*D0**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625821 | Ground Water | GeoSmart Energy | S5A(V/H)042*D2**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625822 | Ground Water | GeoSmart Energy | S5A(V/H)042*D3**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625823 | Ground Water | GeoSmart Energy | S5A(V/H)042*D3**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625824 | Ground Water | GeoSmart Energy | S5A(V/H)042*D3**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625825 | Ground Water | GeoSmart Energy | S5A(V/H)042*D4**1 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625826 | Ground Water | GeoSmart Energy | S5A(V/H)042*D4**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625827 | Ground Water | GeoSmart Energy | S5A(V/H)042*D4**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625828 | Ground Water | GeoSmart Energy | S5A(V/H)042*S0**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625829 | Ground Water | GeoSmart Energy | S5A(V/H)042*S0**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625830 | Ground Water | GeoSmart Energy | S5A(V/H)042*S0**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625831 | Ground Water | GeoSmart Energy | S5A(V/H)042*S2**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625832 | Ground Water | GeoSmart Energy | S5A(V/H)042*S3**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625833 | Ground Water | GeoSmart Energy | S5A(V/H)042*S3**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625834 | Ground Water | GeoSmart Energy | S5A(V/H)042*S3**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625835 | Ground Water | GeoSmart Energy | S5A(V/H)042*S4**1 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625836 | Ground Water | GeoSmart Energy | S5A(V/H)042*S4**2 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625837 | Ground Water | GeoSmart Energy | S5A(V/H)042*S4**4 |  | 45000 | 27 | 39000 | 5.2 | 3.75 | No
216625838 | Ground Water | GeoSmart Energy | S5A(V/H)048*D0**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
216625839 | Ground Water | GeoSmart Energy | S5A(V/H)048*D0**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
3628407 | Ground Water | WaterFurnace | USH023**0*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3628408 | Ground Water | WaterFurnace | USV/USH036**3*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3628409 | Ground Water | WaterFurnace | USV/USH036**0*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3628410 | Ground Water | WaterFurnace | USV/USH036**4*1 |  | 37700 | 23 | 33000 | 4.3 | 3.1417 | No
3628411 | Ground Water | WaterFurnace | USH023**3*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3628412 | Ground Water | WaterFurnace | USH023**2*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3628413 | Ground Water | WaterFurnace | USH023**4*1 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
3628414 | Ground Water | WaterFurnace | USV/USH018**0*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
3628415 | Ground Water | WaterFurnace | USV/USH018**2*1 |  | 20600 | 24 | 17500 | 4.4 | 1.7167 | No
3628416 | Ground Water | WaterFurnace | USV/USH015**0*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
3628417 | Ground Water | WaterFurnace | USV/USH015**2*1 |  | 16000 | 24.3 | 15000 | 4.4 | 1.3333 | No
3655222 | Ground Water | GEOSTAR | GCC/GCW/GCS/GCE15*0 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
3655223 | Ground Water | GEOSTAR | GCC/GCW/GCS/GCE15*2 |  | 16200 | 22 | 14000 | 4.1 | 1.35 | No
3696260 | Ground Water | GEOSTAR | ZS015**0*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
3696261 | Ground Water | GEOSTAR | ZS015**2*0 |  | 16000 | 24 | 15000 | 4.1 | 1.3333 | No
202330453 | Ground Water | AAON, Inc. | RQ-005-1-0-DCAY-S0-10-000-A |  | 61500 | 22.3 | 53000 | 4.6 | 5.125 | No
202330454 | Ground Water | AAON, Inc. | RQ-005-2-0-BCAY-V0-10-000-A |  | 66900 | 22 | 56500 | 4.4 | 5.575 | No
202330455 | Ground Water | AAON, Inc. | RQ-005-3-0-BCAY-V0-10-000-A |  | 66900 | 22 | 56500 | 4.4 | 5.575 | No
202330456 | Ground Water | AAON, Inc. | RQ-005-4-0-BCAY-V0-10-000-A |  | 66900 | 22 | 56500 | 4.4 | 5.575 | No
202330457 | Ground Water | AAON, Inc. | RQ-005-2-0-DCAY-S0-10-000-A |  | 61500 | 22.3 | 53000 | 4.6 | 5.125 | No
202330458 | Ground Water | AAON, Inc. | RQ-005-3-0-DCAY-S0-10-000-A |  | 61500 | 22.3 | 53000 | 4.6 | 5.125 | No
202330459 | Ground Water | AAON, Inc. | RQ-005-4-0-DCAY-S0-10-000-A |  | 61500 | 22.3 | 53000 | 4.6 | 5.125 | No
202330469 | Ground Water | AAON, Inc. | RN-006-2-0-BCAY-V0-10-000-A |  | 63300 | 22.2 | 52200 | 4.2 | 5.275 | No
202330470 | Ground Water | AAON, Inc. | RN-006-3-0-BCAY-V0-10-000-A |  | 63300 | 22.2 | 52200 | 4.2 | 5.275 | No
202330471 | Ground Water | AAON, Inc. | RN-006-4-0-BCAY-V0-10-000-A |  | 63300 | 22.2 | 52200 | 4.2 | 5.275 | No
206223143 | Ground Water | ClimateMaster | TRT036D |  | 40000 | 22.1 | 35000 | 4.6 | 3.3333 | No
206223145 | Ground Water | ClimateMaster | TRT060D |  | 70000 | 23.7 | 59200 | 4.5 | 5.8333 | No
206223146 | Ground Water | CENTURY | HZS024B | TAC026B***A* | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
206223147 | Ground Water | COMFORT-AIRE | HZS024B | TAC026B***A* | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
206223148 | Ground Water | CENTURY | HZS024B | TAC026B***B* | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
206223149 | Ground Water | COMFORT-AIRE | HZS024B | TAC026B***B* | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
206223150 | Ground Water | CENTURY | HZS036B | TAC038B | 40200 | 22.3 | 32800 | 4.4 | 3.35 | Yes
206223151 | Ground Water | COMFORT-AIRE | HZS036B | TAC038B | 40200 | 22.3 | 32800 | 4.4 | 3.35 | Yes
206223152 | Ground Water | CENTURY | HZS048B | TAC049B | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
206223153 | Ground Water | COMFORT-AIRE | HZS048B | TAC049B | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
206229666 | Ground Water | BOSCH | EP024-1HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229667 | Ground Water | BOSCH | EP024-2HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229668 | Ground Water | BOSCH | EP024-3HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229669 | Ground Water | BOSCH | EP024-4HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229670 | Ground Water | BOSCH | EP024-1HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229671 | Ground Water | BOSCH | EP024-2HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229672 | Ground Water | BOSCH | EP024-3HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229673 | Ground Water | BOSCH | EP024-4HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229674 | Ground Water | FHP | EP024-1HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229675 | Ground Water | FHP | EP024-2HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229676 | Ground Water | FHP | EP024-3HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229677 | Ground Water | FHP | EP024-4HZ/VTC-*****B |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229678 | Ground Water | FHP | EP024-1HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229679 | Ground Water | FHP | EP024-2HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229680 | Ground Water | FHP | EP024-3HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229681 | Ground Water | FHP | EP024-4HZ/VTN-*****B |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229682 | Ground Water | CARRIER | 50PSH/V024**C3/CA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229683 | Ground Water | CARRIER | 50PSH/V024**C4/DA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229684 | Ground Water | CARRIER | 50PSH/V024**C5/EA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229685 | Ground Water | CARRIER | 50PSH/V024**C6/FA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
206229686 | Ground Water | CARRIER | 50PSH/V024**N3/CA |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229687 | Ground Water | CARRIER | 50PSH/V024**N4/DA |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229688 | Ground Water | CARRIER | 50PSH/V024**N5/EA |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206229689 | Ground Water | CARRIER | 50PSH/V024**N6/FA |  | 27600 | 25.1 | 23700 | 4.15 | 2.3 | No
206262126 | Ground Water | HYDROTECH | WSV6090A |  | 101000 | 22 | 73000 | 4.1 | 8.4167 | No
206342108 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH080**3 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
206342109 | Ground Water | YORK BY JOHNSON CONTROLS | YLLH/YLXH080**4 |  | 79000 | 22.5 | 65800 | 4.2 | 6.5833 | No
7415878 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7416559 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7416688 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
7416782 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7416889 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7416979 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
7417060 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7417146 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7417250 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
7417329 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7417419 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
7417586 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7417698 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7417776 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7417867 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7417918 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7417992 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7418047 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7418154 | Ground Water | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
7418286 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
7418360 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7418435 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7418524 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*0 |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
7418635 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*1 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
7418715 | Ground Water | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*4 |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
207349404 | Ground Water | WaterFurnace | NBV/NBH064**4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349405 | Ground Water | WaterFurnace | NBV/NBH064**3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349406 | Ground Water | WaterFurnace | NBV/NBH064**0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
207349407 | Ground Water | WaterFurnace | NBV/NBH072**0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349408 | Ground Water | WaterFurnace | NBV/NBH072**3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349409 | Ground Water | WaterFurnace | NBV/NBH072**4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349410 | Ground Water | WaterFurnace | NBV/NBH072**4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349411 | Ground Water | WaterFurnace | NBV/NBH072**0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207349412 | Ground Water | WaterFurnace | NBV/NBH072**3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207530615 | Ground Water | BOSCH | CA009-1*C-*****D |  | 10000 | 22.1 | 8600 | 4.25 | 0.83333 | No
207542447 | Ground Water | FHP | CA009-1*C-*****D |  | 10000 | 22.1 | 8600 | 4.25 | 0.83333 | No
207549518 | Ground Water | CARRIER | 50PEC09***E3/CF |  | 10000 | 22.1 | 8600 | 4.25 | 0.83333 | No
205767477 | Ground Water | ClimateMaster | TEV/H/D072B |  | 77700 | 22.5 | 71400 | 4.4 | 6.475 | Yes
205767488 | Ground Water | ClimateMaster | TSH/V006A |  | 7400 | 25.5 | 6300 | 4.4 | 0.61667 | No
205767489 | Ground Water | ClimateMaster | TSH/V/D018B |  | 21300 | 24.8 | 18600 | 4.5 | 1.775 | No
205767490 | Ground Water | ClimateMaster | TSH/V/D018B*K |  | 22100 | 26.3 | 18900 | 4.9 | 1.8417 | No
205767496 | Ground Water | ClimateMaster | TCH/V015A |  | 16500 | 24 | 14100 | 4.3 | 1.375 | No
205767497 | Ground Water | ClimateMaster | TCH/V018A |  | 21500 | 22 | 17800 | 4.2 | 1.7917 | No
214595715 | Ground Water | AAON, Inc. | M2-014-2-H-GCBC-V0-10-000-A |  | 135000 | 21.6 | 119600 | 4.1 | 11.25 | No
214595716 | Ground Water | AAON, Inc. | M2-014-3-H-GCBC-V0-10-000-A |  | 135000 | 21.6 | 119600 | 4.1 | 11.25 | No
214595717 | Ground Water | AAON, Inc. | M2-014-4-H-GCBC-V0-10-000-A |  | 135000 | 21.6 | 119600 | 4.1 | 11.25 | No
214771921 | Ground Water | TRANE | GEVK009A |  | 9400 | 25.6 | 8600 | 4.94 | 0.78333 | No
214771922 | Ground Water | TRANE | GEVK012A |  | 11900 | 22.3 | 11500 | 4.45 | 0.99167 | No
214771923 | Ground Water | TRANE | GEVK015A |  | 16800 | 24.1 | 16700 | 4.69 | 1.4 | No
214771924 | Ground Water | TRANE | GEVK018A |  | 19600 | 23.4 | 19500 | 4.46 | 1.6333 | No
214771925 | Ground Water | TRANE | GEVK024A |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
214771926 | Ground Water | TRANE | GEVK030A |  | 31700 | 23.9 | 29800 | 4.31 | 2.6417 | No
214771927 | Ground Water | TRANE | GEVK036A |  | 42500 | 22.1 | 39700 | 4.17 | 3.5417 | No
214771928 | Ground Water | TRANE | GEVK042A |  | 47100 | 24.5 | 46200 | 4.14 | 3.925 | No
214771929 | Ground Water | TRANE | GEVK048A |  | 54500 | 24 | 50800 | 4.31 | 4.5417 | No
214771930 | Ground Water | TRANE | GEVK060A |  | 64300 | 23.9 | 63700 | 4.23 | 5.3583 | No
214771931 | Ground Water | TRANE | EXVK009A |  | 9600 | 29.7 | 8500 | 5.16 | 0.8 | No
214771932 | Ground Water | TRANE | EXVK012A |  | 12500 | 26.1 | 11500 | 4.98 | 1.0417 | No
214771933 | Ground Water | TRANE | EXVK015A |  | 17100 | 24.6 | 15600 | 4.6 | 1.425 | No
214771934 | Ground Water | TRANE | EXVK018A |  | 21100 | 29.6 | 18600 | 4.77 | 1.7583 | No
214771935 | Ground Water | TRANE | EXVK024A |  | 27400 | 28.4 | 25900 | 4.81 | 2.2833 | No
214771936 | Ground Water | TRANE | EXVK030A |  | 34500 | 29.3 | 30100 | 4.98 | 2.875 | No
216625507 | Ground Water | GEOSTAR | G5A(V/H)042*D4**2 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625508 | Ground Water | GEOSTAR | G5A(V/H)042*D4**4 |  | 46200 | 26.6 | 41700 | 5.2 | 3.85 | No
216625509 | Ground Water | GEOSTAR | G5A(V/H)048*S3**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625510 | Ground Water | GEOSTAR | G5A(V/H)048*S4**1 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625511 | Ground Water | GEOSTAR | G5A(V/H)048*S0**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625512 | Ground Water | GEOSTAR | G5A(V/H)048*S2**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625513 | Ground Water | GEOSTAR | G5A(V/H)048*S3**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625514 | Ground Water | GEOSTAR | G5A(V/H)048*S4**2 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
216625515 | Ground Water | GEOSTAR | G5A(V/H)048*S0**4 |  | 53500 | 26 | 48000 | 4.8 | 4.4583 | No
202324846 | Ground Water | WaterFurnace | UBV/UBH009**0*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
202324847 | Ground Water | WaterFurnace | UBV/UBH009**9*6 |  | 10300 | 22 | 9600 | 4.1 | 0.85833 | No
202326797 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ038J1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
202326829 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS038J1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
202328433 | Ground Water | BOSCH | SM048-1CSC-*****A | SM048-1AV*-*****A | 52800 | 21.25 | 46600 | 4.6 | 4.4 | Yes
202328436 | Ground Water | BOSCH | BP018-1VT*******C |  | 21300 | 25.3 | 17700 | 4.4 | 1.775 | Yes
202330331 | Ground Water | AAON, Inc. | WH-060-1-H-ACAC-C0-10-200-A |  | 67400 | 21.6 | 63500 | 4.6 | 5.6167 | No
202330332 | Ground Water | AAON, Inc. | WH-060-A-H-ACAC-C0-10-200-A |  | 67400 | 21.6 | 63500 | 4.6 | 5.6167 | No
202330335 | Ground Water | AAON, Inc. | WH-060-2-H-ACAC-C0-10-200-A |  | 67400 | 21.6 | 63500 | 4.6 | 5.6167 | No
202330336 | Ground Water | AAON, Inc. | WH-060-3-H-ACAC-C0-10-200-A |  | 67400 | 21.6 | 63500 | 4.6 | 5.6167 | No
202330345 | Ground Water | AAON, Inc. | WH-060-A-H-DCAC-C0-10-200-A |  | 66200 | 23.3 | 56800 | 4.7 | 5.5167 | No
202330346 | Ground Water | AAON, Inc. | WH-060-3-H-DCAC-C0-10-200-A |  | 66200 | 23.3 | 56800 | 4.7 | 5.5167 | No
202330411 | Ground Water | AAON, Inc. | WV-060-1-H-ACAC-C0-10-200-A |  | 65800 | 21.8 | 53700 | 4.2 | 5.4833 | No
202330412 | Ground Water | AAON, Inc. | WV-060-A-H-ACAC-C0-10-200-A |  | 65800 | 21.8 | 53700 | 4.2 | 5.4833 | No
202330415 | Ground Water | AAON, Inc. | WV-060-2-H-ACAC-C0-10-200-A |  | 65800 | 21.8 | 53700 | 4.2 | 5.4833 | No
202330416 | Ground Water | AAON, Inc. | WV-060-3-H-ACAC-C0-10-200-A |  | 65800 | 21.8 | 53700 | 4.2 | 5.4833 | No
202330436 | Ground Water | AAON, Inc. | RQ-003-1-0-BCAY-V0-10-000-A |  | 42600 | 23.1 | 37100 | 4.3 | 3.55 | No
202330438 | Ground Water | AAON, Inc. | RQ-003-2-0-BCAY-V0-10-000-A |  | 42600 | 23.1 | 37100 | 4.3 | 3.55 | No
202330439 | Ground Water | AAON, Inc. | RQ-003-3-0-BCAY-V0-10-000-A |  | 42600 | 23.1 | 37100 | 4.3 | 3.55 | No
202330440 | Ground Water | AAON, Inc. | RQ-003-4-0-BCAY-V0-10-000-A |  | 42600 | 23.1 | 37100 | 4.3 | 3.55 | No
202330444 | Ground Water | AAON, Inc. | RQ-004-1-0-BCAY-V0-10-000-A |  | 54000 | 23.5 | 45400 | 4.6 | 4.5 | No
202330445 | Ground Water | AAON, Inc. | RQ-004-1-0-DCAY-S0-10-000-A |  | 53000 | 21.8 | 44700 | 4.6 | 4.4167 | No
202330446 | Ground Water | AAON, Inc. | RQ-004-2-0-BCAY-V0-10-000-A |  | 54000 | 23.5 | 45400 | 4.6 | 4.5 | No
202330447 | Ground Water | AAON, Inc. | RQ-004-3-0-BCAY-V0-10-000-A |  | 54000 | 23.5 | 45400 | 4.6 | 4.5 | No
202330448 | Ground Water | AAON, Inc. | RQ-004-4-0-BCAY-V0-10-000-A |  | 54000 | 23.5 | 45400 | 4.6 | 4.5 | No
202330449 | Ground Water | AAON, Inc. | RQ-004-2-0-DCAY-S0-10-000-A |  | 53000 | 21.8 | 44700 | 4.6 | 4.4167 | No
202330450 | Ground Water | AAON, Inc. | RQ-004-3-0-DCAY-S0-10-000-A |  | 53000 | 21.8 | 44700 | 4.6 | 4.4167 | No
202330451 | Ground Water | AAON, Inc. | RQ-004-4-0-DCAY-S0-10-000-A |  | 53000 | 21.8 | 44700 | 4.6 | 4.4167 | No
202330452 | Ground Water | AAON, Inc. | RQ-005-1-0-BCAY-V0-10-000-A |  | 66900 | 22 | 56500 | 4.4 | 5.575 | No
215268789 | Ground Water | WaterFurnace | V5A(V/H)048*D4**1 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268790 | Ground Water | WaterFurnace | V5A(V/H)048*D2**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268791 | Ground Water | WaterFurnace | V5A(V/H)048*D4**2 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268792 | Ground Water | WaterFurnace | V5A(V/H)048*D4**4 |  | 53100 | 24.9 | 49300 | 5.1 | 4.425 | No
215268793 | Ground Water | WaterFurnace | V5A(V/H)060*D4**1 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268794 | Ground Water | WaterFurnace | V5A(V/H)060*D4**4 |  | 68400 | 24.2 | 56100 | 4.7 | 5.7 | No
215268795 | Ground Water | WaterFurnace | V5A(V/H)072*D4**1 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215268796 | Ground Water | WaterFurnace | V5A(V/H)072*D4**4 |  | 78100 | 23.1 | 71400 | 4.6 | 6.5083 | No
215270403 | Ground Water | GEO-THERMAL SPLIT | GZ024*******1**1 | FT*****36*** | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
215270405 | Ground Water | GEO-THERMAL SPLIT | GZ036*******1**2 | FT*****48*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | Yes
215270409 | Ground Water | CARRIER | GZ024*******1**1 | FT*****36*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
215270411 | Ground Water | CARRIER | GZ036*******1**2 | FT*****48*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
215270415 | Ground Water | BRYANT | GZ024*******1**1 | FT*****36*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
215270417 | Ground Water | BRYANT | GZ036*******1**2 | FT*****48*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
215270421 | Ground Water | CARRIER | GZ024*******1**1 | FE****003*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
215270423 | Ground Water | CARRIER | GZ036*******1**2 | FE****005*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
215270427 | Ground Water | BRYANT | GZ024*******1**1 | FE****003*** | 28200 | 22 | 23500 | 4.45 | 2.35 | No
215270429 | Ground Water | BRYANT | GZ036*******1**2 | FE****005*** | 41400 | 22.75 | 36700 | 4.4 | 3.45 | No
215278610 | Ground Water | WaterFurnace | W3A(V/H)024BD1**1 |  | 25700 | 21.3 | 23000 | 4.6 | 2.1417 | Yes
215285739 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)024A |  | 28600 | 26.1 | 23700 | 5 | 2.3833 | Yes
215285740 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)036A |  | 42000 | 23.9 | 36000 | 4.8 | 3.5 | Yes
215285741 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)048A |  | 55000 | 26 | 49100 | 4.6 | 4.5833 | Yes
215285742 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)060A |  | 66800 | 24.7 | 55700 | 4.7 | 5.5667 | Yes
215285743 | Ground Water | ClimateMaster | SE(L/R/B/P/D/N/T/K)072A |  | 78000 | 22.4 | 67400 | 4.4 | 6.5 | Yes
215287172 | Ground Water | GEOSTAR | G3A(V/H)024BD1**1 |  | 25700 | 21.3 | 23000 | 4.6 | 2.1417 | Yes
215287179 | Ground Water | GeoSmart Energy | S3A(V/H)024BD1**1 |  | 25700 | 21.3 | 23000 | 4.6 | 2.1417 | Yes
217351787 | Ground Water | ARCOAIRE | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351788 | Ground Water | ARCOAIRE | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351789 | Ground Water | ARCOAIRE | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351790 | Ground Water | ARCOAIRE | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351792 | Ground Water | ARCOAIRE | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351793 | Ground Water | ARCOAIRE | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351795 | Ground Water | ARCOAIRE | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351796 | Ground Water | ARCOAIRE | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351797 | Ground Water | ARCOAIRE | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351798 | Ground Water | ARCOAIRE | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
211594253 | Ground Water | TRANE | EXHG0364 |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
211594254 | Ground Water | TRANE | EXHG0367 |  | 39400 | 26.5 | 35000 | 5 | 3.2833 | No
211594255 | Ground Water | TRANE | EXHG042B |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
211594256 | Ground Water | TRANE | EXHG0424 |  | 43300 | 27.5 | 38500 | 5.5 | 3.6083 | No
211594257 | Ground Water | TRANE | EXHG048B |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
211594258 | Ground Water | TRANE | EXHG0484 |  | 50400 | 26.4 | 44800 | 5.3 | 4.2 | No
211594259 | Ground Water | TRANE | EXHG060B |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
211594260 | Ground Water | TRANE | EXHG0604 |  | 60800 | 25.7 | 55900 | 5.1 | 5.0667 | No
211594261 | Ground Water | TRANE | EXHG070B |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
211594262 | Ground Water | TRANE | EXHG0704 |  | 68900 | 24.9 | 66900 | 4.8 | 5.7417 | No
211594263 | Ground Water | TRANE | DXHG024B |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
211594264 | Ground Water | TRANE | DXHG0244 |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
211594265 | Ground Water | TRANE | DXHG0247 |  | 27500 | 24.4 | 25700 | 4.9 | 2.2917 | No
211594266 | Ground Water | TRANE | DXHG036B |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
211594267 | Ground Water | TRANE | DXHG0364 |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
211594268 | Ground Water | TRANE | DXHG0367 |  | 37100 | 25.1 | 32900 | 5.1 | 3.0917 | No
211594269 | Ground Water | TRANE | DXHG048B |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
211594270 | Ground Water | TRANE | DXHG0484 |  | 50400 | 26.4 | 44400 | 5.3 | 4.2 | No
211594271 | Ground Water | TRANE | DXHG060B |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
211594272 | Ground Water | TRANE | DXHG0604 |  | 56600 | 24.8 | 51700 | 5.2 | 4.7167 | No
211594273 | Ground Water | TRANE | DXHG070B |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
211594274 | Ground Water | TRANE | DXHG0704 |  | 69100 | 23.8 | 67400 | 4.8 | 5.7583 | No
212428693 | Ground Water | HYDROTECH | WSH6009A6* |  | 10000 | 23 | 8500 | 4.2 | 0.83333 | Yes
212428694 | Ground Water | HYDROTECH | WSH6012A6* |  | 12500 | 23.1 | 11000 | 4.6 | 1.0417 | Yes
212428695 | Ground Water | HYDROTECH | WSH6018A6* |  | 20500 | 26 | 16000 | 4.3 | 1.7083 | Yes
212428696 | Ground Water | HYDROTECH | WSH6024A6* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | Yes
212428697 | Ground Water | HYDROTECH | WSH6030A6* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | Yes
212428698 | Ground Water | HYDROTECH | WSH6036A6* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | Yes
212428699 | Ground Water | HYDROTECH | WSH6042A6* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | Yes
212428700 | Ground Water | HYDROTECH | WSH6048A6* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | Yes
212428701 | Ground Water | AE Air | WSH6009A6* |  | 10000 | 23 | 8500 | 4.2 | 0.83333 | Yes
212428702 | Ground Water | AE Air | WSH6012A6* |  | 12500 | 23.1 | 11000 | 4.6 | 1.0417 | Yes
212428703 | Ground Water | AE Air | WSH6018A6* |  | 20500 | 26 | 16000 | 4.3 | 1.7083 | Yes
212428704 | Ground Water | AE Air | WSH6024A6* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | Yes
212428705 | Ground Water | AE Air | WSH6030A6* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | Yes
212428706 | Ground Water | AE Air | WSH6036A6* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | Yes
212428707 | Ground Water | AE Air | WSH6042A6* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | Yes
212428708 | Ground Water | AE Air | WSH6048A6* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | Yes
212505502 | Ground Water | HYDROTECH | WSH6060A6* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | Yes
212505503 | Ground Water | HYDROTECH | WSH6072A6* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | Yes
212505504 | Ground Water | AE Air | WSH6030AM* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | No
212505505 | Ground Water | AE Air | WSH6060A6* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | Yes
212505506 | Ground Water | AE Air | WSH6072A6* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | Yes
212505507 | Ground Water | HYDROTECH | WSH6024AM* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | No
212505508 | Ground Water | HYDROTECH | WSH6030AM* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | No
216625879 | Ground Water | GeoSmart Energy | S5A(V/H)072*S3**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625880 | Ground Water | GeoSmart Energy | S5A(V/H)072*S4**1 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216625881 | Ground Water | GeoSmart Energy | S5A(V/H)072*S4**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
216687113 | Ground Water | WaterFurnace | W5SS024BD1 | W5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216687114 | Ground Water | WaterFurnace | W5SS036BD1 | W5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216687115 | Ground Water | WaterFurnace | W5SS048BD1 | W5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216687116 | Ground Water | WaterFurnace | W5SS060BD1 | W5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216687117 | Ground Water | WaterFurnace | W5SS066BD1 | W5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216687118 | Ground Water | WaterFurnace | W5SZ024BD1 | W5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216687119 | Ground Water | WaterFurnace | W5SZ036BD1 | W5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216687120 | Ground Water | WaterFurnace | W5SZ048BD1 | W5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216687121 | Ground Water | WaterFurnace | W5SZ060BD1 | W5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216687122 | Ground Water | WaterFurnace | W5SZ066BD1 | W5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216687731 | Ground Water | GEOSTAR | G5SS024BD1 | G5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216687732 | Ground Water | GEOSTAR | G5SS036BD1 | G5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216687733 | Ground Water | GEOSTAR | G5SS048BD1 | G5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216687734 | Ground Water | GEOSTAR | G5SS060BD1 | G5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216687735 | Ground Water | GEOSTAR | G5SS066BD1 | G5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216687736 | Ground Water | GEOSTAR | G5SZ024BD1 | G5BM024BN1**2 | 25800 | 23.8 | 22700 | 4.6 | 2.15 | Yes
216687737 | Ground Water | GEOSTAR | G5SZ036BD1 | G5BM036BN1**2 | 38100 | 25.2 | 35000 | 5 | 3.175 | Yes
216687738 | Ground Water | GEOSTAR | G5SZ048BD1 | G5BM048BN1**2 | 50900 | 24.3 | 47300 | 4.8 | 4.2417 | Yes
216687739 | Ground Water | GEOSTAR | G5SZ060BD1 | G5BM060BN1**2 | 63900 | 23.7 | 55700 | 4.4 | 5.325 | Yes
216687740 | Ground Water | GEOSTAR | G5SZ066BD1 | G5BM066BN1**2 | 70100 | 22.1 | 66100 | 4.2 | 5.8417 | Yes
216714606 | Ground Water | GEOSTAR | G3A(V/H)006*R0**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
216714607 | Ground Water | GEOSTAR | G3A(V/H)006*R2**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
7137597 | Ground Water | GEO-THERMAL SPLIT | GS024**1**1 | FE/V****003*** | 28200 | 22 | 23500 | 4.45 | 2.35 | Yes
7167375 | Ground Water | BRYANT | GB024H/V******1*X1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
7167376 | Ground Water | CARRIER | GB024H/V******1**1 |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | Yes
7167377 | Ground Water | BRYANT | GB030H/V******1*X1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
7167378 | Ground Water | CARRIER | GB030H/V******1**1 |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | Yes
7167412 | Ground Water | BRYANT | GT072C/H/V******1*X1 |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7167413 | Ground Water | CARRIER | GT072C/H/V******1**1 |  | 78700 | 21.2 | 70000 | 4.35 | 6.5583 | No
7167538 | Ground Water | CARRIER | 50PTD/H/V024***3/CA |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7167539 | Ground Water | CARRIER | 50PTD/H/V024***5/EA |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7167540 | Ground Water | CARRIER | 50PTD/H/V024***4/DA |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7167541 | Ground Water | CARRIER | 50PTD/H/V024***6/FA |  | 29000 | 26.5 | 23500 | 4.9 | 2.4167 | No
7167542 | Ground Water | CARRIER | 50PTD/H/V036***3/CA |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7167543 | Ground Water | CARRIER | 50PTD/H/V036***5/EA |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7167544 | Ground Water | CARRIER | 50PTD/H/V036***4/DA |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7167545 | Ground Water | CARRIER | 50PTD/H/V036***6/FA |  | 43300 | 26 | 35900 | 4.55 | 3.6083 | No
7167546 | Ground Water | CARRIER | 50PTD/H/V048***3/CA |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7167547 | Ground Water | CARRIER | 50PTD/H/V048***5/EA |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7167548 | Ground Water | CARRIER | 50PTD/H/V048***6/FA |  | 55300 | 23.8 | 46300 | 4.55 | 4.6083 | No
7167549 | Ground Water | CARRIER | 50PTD/H/V060***3/CA |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
7167550 | Ground Water | CARRIER | 50PTD/H/V060***5/EA |  | 70200 | 22.3 | 60300 | 4.35 | 5.85 | No
217642928 | Ground Water | GeoSmart Energy | S3A(V/H)060*S0**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642929 | Ground Water | GeoSmart Energy | S3A(V/H)060*S3**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642930 | Ground Water | GeoSmart Energy | S3A(V/H)060*S3**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642931 | Ground Water | GeoSmart Energy | S3A(V/H)060*S4**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642932 | Ground Water | GeoSmart Energy | S3A(V/H)060*S4**4 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642938 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)006*R0**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
217642941 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)015*R0**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642943 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S0**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642945 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S0**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642946 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S0**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642948 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S0**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642950 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)006*R2**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
217642953 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)015*R0**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642954 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)015*R2**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642955 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)015*R2**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642959 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S0**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642960 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S2**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642961 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S2**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642962 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S3**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642963 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S3**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642964 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S4**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642965 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S4**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642973 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S0**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642974 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S2**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642975 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S2**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642976 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S3**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642977 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S3**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642978 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S4**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642979 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S4**4 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642980 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S0**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642981 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S3**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642982 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S3**4 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
207177441 | Ground Water | TRANE | GEVG0244 |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
207177442 | Ground Water | TRANE | GEVG0247 |  | 26600 | 24.4 | 25300 | 4.6 | 2.2167 | No
207177443 | Ground Water | TRANE | GEVG030A |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
207177444 | Ground Water | TRANE | GEVG030B |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
207177445 | Ground Water | TRANE | GEVG0304 |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
207177446 | Ground Water | TRANE | GEVG0307 |  | 32300 | 23 | 30800 | 4.5 | 2.6917 | No
207177447 | Ground Water | TRANE | GEVG036A |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
207177448 | Ground Water | TRANE | GEVG036B |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
207177449 | Ground Water | TRANE | GEVG0364 |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
207177450 | Ground Water | TRANE | GEVG0367 |  | 39900 | 22.6 | 36900 | 4.4 | 3.325 | No
207177451 | Ground Water | TRANE | GEVG042A |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
207177452 | Ground Water | TRANE | GEVG042B |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
207177453 | Ground Water | TRANE | GEVG0424 |  | 45500 | 22 | 45600 | 4.2 | 3.7917 | No
207177454 | Ground Water | TRANE | GEVG048A |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
207177455 | Ground Water | TRANE | GEVG048B |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
207177456 | Ground Water | TRANE | GEVG0484 |  | 55700 | 22.8 | 50000 | 4.2 | 4.6417 | No
207177457 | Ground Water | TRANE | GEVG060A |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
207177458 | Ground Water | TRANE | GEVG060B |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
207177459 | Ground Water | TRANE | GEVG0604 |  | 61700 | 21.3 | 61200 | 4.1 | 5.1417 | No
207177460 | Ground Water | TRANE | EXVG009A |  | 8800 | 25 | 8200 | 4.8 | 0.73333 | No
207177461 | Ground Water | TRANE | EXVG0097 |  | 8800 | 25 | 8200 | 4.8 | 0.73333 | No
207177462 | Ground Water | TRANE | EXVG012A |  | 13700 | 27.9 | 12300 | 5 | 1.1417 | No
215224683 | Ground Water | BOSCH | RF012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | Yes
215224684 | Ground Water | BOSCH | RF012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | Yes
215224685 | Ground Water | BOSCH | RF015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | Yes
215224686 | Ground Water | BOSCH | RF015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | Yes
215224687 | Ground Water | BOSCH | RF018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224688 | Ground Water | BOSCH | RF018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224782 | Ground Water | CARRIER | GBA18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224783 | Ground Water | BRYANT | GBA18V/H**C******1 |  | 21300 | 24 | 18000 | 4.4 | 1.775 | Yes
215224784 | Ground Water | CARRIER | GBA18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
215224785 | Ground Water | BRYANT | GBA18V/H**N******1 |  | 21000 | 24 | 17700 | 4.4 | 1.75 | Yes
205767559 | Ground Water | ClimateMaster | TZV/H060C |  | 68000 | 22.7 | 55400 | 4.3 | 5.6667 | Yes
215893693 | Ground Water | DUAL AIR | CFF024 |  | 22804 | 21.1 | 18640 | 4.1 | 1.9003 | No
215893695 | Ground Water | DUAL AIR | CFF031 |  | 32445 | 21.1 | 24698 | 4.1 | 2.7037 | No
215893697 | Ground Water | DUAL AIR | CFF036 |  | 32908 | 21.1 | 29358 | 4.1 | 2.7423 | No
215893699 | Ground Water | DUAL AIR | CFF041 |  | 37543 | 21.1 | 34484 | 4.1 | 3.1286 | No
215893701 | Ground Water | DUAL AIR | CFF060 |  | 57937 | 21.1 | 46600 | 4.1 | 4.8281 | No
215893703 | Ground Water | MIAMI HEAT PUMP | HPF024 |  | 22804 | 21.1 | 18640 | 4.1 | 1.9003 | No
215893704 | Ground Water | MIAMI HEAT PUMP | HPF031 |  | 32445 | 21.1 | 24698 | 4.1 | 2.7037 | No
215893706 | Ground Water | MIAMI HEAT PUMP | HPF036 |  | 32908 | 21.1 | 29358 | 4.1 | 2.7423 | No
215893707 | Ground Water | MIAMI HEAT PUMP | HPF041 |  | 37543 | 21.1 | 34484 | 4.1 | 3.1286 | No
215893709 | Ground Water | MIAMI HEAT PUMP | HPF060 |  | 57937 | 21.1 | 46600 | 4.1 | 4.8281 | No
215893711 | Ground Water | DUAL AIR | CFF049 |  | 43569 | 21.1 | 37280 | 4.1 | 3.6307 | No
215893713 | Ground Water | MIAMI HEAT PUMP | HPF049 |  | 43569 | 21.1 | 37280 | 4.1 | 3.6307 | No
216014181 | Ground Water | RHEEM | RPVV/H/D036D |  | 42100 | 26.1 | 37900 | 5.2 | 3.5083 | Yes
216054107 | Ground Water | WaterFurnace | W5TV036BD1**2 |  | 41400 | 26.9 | 35700 | 5.1 | 3.45 | Yes
216054108 | Ground Water | WaterFurnace | W5TV048BD1**2 |  | 52500 | 24.5 | 47400 | 4.7 | 4.375 | Yes
216054109 | Ground Water | WaterFurnace | W5TV060BD1**2 |  | 67900 | 23.9 | 56000 | 4.6 | 5.6583 | Yes
216054110 | Ground Water | WaterFurnace | W5TV072BD1**2 |  | 77700 | 23 | 70700 | 4.5 | 6.475 | Yes
216054475 | Ground Water | GEOCOMFORT | GBS018* | EAD018 | 23700 | 29.8 | 18500 | 5 | 1.975 | Yes
216054476 | Ground Water | GEOCOMFORT | GBT024* | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | Yes
216054477 | Ground Water | GEOCOMFORT | GBT036* | EAD036 | 39700 | 24.8 | 36700 | 4.7 | 3.3083 | Yes
216054478 | Ground Water | GEOCOMFORT | GBT048* | EAD048 | 51500 | 22.5 | 51300 | 4.5 | 4.2917 | Yes
216054479 | Ground Water | GEOCOMFORT | GVS009* |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | Yes
216054480 | Ground Water | GEOCOMFORT | GVS012* |  | 13400 | 24.1 | 12100 | 4.3 | 1.1167 | Yes
216054481 | Ground Water | GEOCOMFORT | GVS018* |  | 23200 | 30.5 | 19600 | 5.3 | 1.9333 | Yes
216054482 | Ground Water | GEOCOMFORT | GVT024* |  | 27600 | 23.8 | 23900 | 4.6 | 2.3 | Yes
216054483 | Ground Water | GEOCOMFORT | GVT030* |  | 34100 | 23.1 | 30300 | 4.6 | 2.8417 | Yes
216054484 | Ground Water | GEOCOMFORT | GVT036* |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
216054485 | Ground Water | GEOCOMFORT | GVT042* |  | 49200 | 24 | 40100 | 4.6 | 4.1 | Yes
216054486 | Ground Water | GEOCOMFORT | GVT048* |  | 53600 | 24.5 | 48500 | 4.9 | 4.4667 | Yes
216054487 | Ground Water | GEOCOMFORT | GYT024* |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
216054488 | Ground Water | GEOCOMFORT | GYT036* |  | 42300 | 27.9 | 35500 | 5.4 | 3.525 | Yes
216054489 | Ground Water | GEOCOMFORT | GYT048* |  | 55200 | 24.9 | 46500 | 5 | 4.6 | Yes
216054492 | Ground Water | GEOCOMFORT | GZT024* |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | Yes
216054493 | Ground Water | GEOCOMFORT | GZT030* |  | 32600 | 21.6 | 28800 | 4.5 | 2.7167 | Yes
216054494 | Ground Water | GEOCOMFORT | GZT036* |  | 39400 | 23.6 | 34000 | 4.6 | 3.2833 | Yes
216054495 | Ground Water | GEOCOMFORT | GZT042* |  | 46000 | 23.4 | 40100 | 4.4 | 3.8333 | Yes
216054496 | Ground Water | GEOCOMFORT | GZT048* |  | 52200 | 22.1 | 45900 | 4.4 | 4.35 | Yes
216054497 | Ground Water | GEOCOMFORT | GZT060* |  | 62000 | 21.2 | 58500 | 4.2 | 5.1667 | Yes
216054498 | Ground Water | GEOCOMFORT | GVS006* |  | 7600 | 25.9 | 6500 | 4.4 | 0.63333 | Yes
216054499 | Ground Water | GEOCOMFORT | GVS015* |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | Yes
216054500 | Ground Water | GEOCOMFORT | GZS006* |  | 6900 | 22.9 | 6300 | 4.3 | 0.575 | Yes
216057509 | Ground Water | GEOCOMFORT | GBT060* | EAD060 | 65700 | 22.8 | 58300 | 4.3 | 5.475 | Yes
216057511 | Ground Water | GEOCOMFORT | GVT060* |  | 64200 | 22 | 57500 | 4.5 | 5.35 | Yes
216057512 | Ground Water | GEOCOMFORT | GYT060* |  | 66900 | 23.8 | 60700 | 4.8 | 5.575 | Yes
216057513 | Ground Water | GEOCOMFORT | GZS015* |  | 15600 | 24.9 | 14300 | 4.8 | 1.3 | Yes
216057514 | Ground Water | GEOCOMFORT | GZS017* |  | 18000 | 21.9 | 15800 | 4.1 | 1.5 | Yes
216057515 | Ground Water | GEOCOMFORT | GZS018* |  | 21400 | 26 | 17500 | 4.7 | 1.7833 | Yes
201926738 | Ground Water | WaterFurnace | URS070*4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926741 | Ground Water | WaterFurnace | URS070*4*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
201926779 | Ground Water | WaterFurnace | URD064*4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
201926783 | Ground Water | WaterFurnace | URD064*4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
201926787 | Ground Water | WaterFurnace | URD064*4*5 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
201926799 | Ground Water | WaterFurnace | URD072*4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
201926802 | Ground Water | WaterFurnace | URD072*4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
201926804 | Ground Water | WaterFurnace | URD072*4*5 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
201926809 | Ground Water | WaterFurnace | URT096*4*5 |  | 100600 | 25.9 | 89400 | 4.7 | 8.3833 | No
201930362 | Ground Water | GEOCOMFORT | GZT024 |  | 28200 | 23.7 | 22900 | 4.6 | 2.35 | Yes
217967018 | Ground Water | TRANE | VSHK024A |  | 26900 | 32.5 | 25700 | 5.6 | 2.2417 | No
217967019 | Ground Water | TRANE | VSVK024A |  | 28300 | 38.8 | 24900 | 5.6 | 2.3583 | No
217967020 | Ground Water | TRANE | VSHK033A |  | 35500 | 25.2 | 35600 | 5.1 | 2.9583 | No
217967021 | Ground Water | TRANE | VSVK033A |  | 37500 | 28.8 | 32900 | 5.3 | 3.125 | No
217967022 | Ground Water | TRANE | VSHK042A |  | 45000 | 30.2 | 41200 | 5.5 | 3.75 | No
217967023 | Ground Water | TRANE | VSVK042A |  | 46600 | 32.1 | 43400 | 5.4 | 3.8833 | No
200083701 | Ground Water | CENTURY | HZS048B | WDG048***-*B | 52800 | 23 | 45900 | 4.2 | 4.4 | Yes
200083804 | Ground Water | NORTHERN HEAT PUMP | RA-VE-061-* |  | 65000 | 21.4 | 63500 | 4.1 | 5.4167 | No
200083805 | Ground Water | NORTHSTAR SERIES | RA-VE-061-* |  | 65000 | 21.4 | 63500 | 4.1 | 5.4167 | No
201756620 | Ground Water | NORTHERN HEAT PUMP | RA-VE-041-* |  | 42000 | 22.89 | 42600 | 4.28 | 3.5 | No
201756621 | Ground Water | NORTHSTAR SERIES | RA-VE-041-* |  | 42000 | 22.89 | 42600 | 4.28 | 3.5 | No
201756622 | Ground Water | NORTHERN HEAT PUMP | RA-VE-053-* |  | 55400 | 22.21 | 57300 | 4.1 | 4.6167 | No
201756623 | Ground Water | NORTHSTAR SERIES | RA-VE-053-* |  | 55400 | 22.21 | 57300 | 4.1 | 4.6167 | No
207337449 | Ground Water | GEOSTAR | 12(1,2)A048 |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | Yes
6501891 | Ground Water | GEOSTAR | GBV/GBH015**2*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
6501892 | Ground Water | GEOSTAR | GBV/GBH015**2*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
6501893 | Ground Water | GEOSTAR | GBV/GBH018**0*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
6501894 | Ground Water | GEOSTAR | GBV/GBH018**0*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
6501895 | Ground Water | GEOSTAR | GBV/GBH018**0*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
6501896 | Ground Water | GEOSTAR | GBV/GBH018**2*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
6501897 | Ground Water | GEOSTAR | GBV/GBH018**2*1 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
6501898 | Ground Water | GEOSTAR | GBV/GBH018**2*4 |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
6501899 | Ground Water | GEOSTAR | GBV/GBH024**0*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
6501900 | Ground Water | GEOSTAR | GBV/GBH024**0*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501901 | Ground Water | GEOSTAR | GBV/GBH024**0*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501902 | Ground Water | GEOSTAR | GBV/GBH024**2*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
6501903 | Ground Water | GEOSTAR | GBV/GBH024**2*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501904 | Ground Water | GEOSTAR | GBV/GBH024**2*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501905 | Ground Water | GEOSTAR | GBV/GBH024**3*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
6501906 | Ground Water | GEOSTAR | GBV/GBH024**3*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501907 | Ground Water | GEOSTAR | GBV/GBH024**3*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501908 | Ground Water | GEOSTAR | GBV/GBH024**4*0 |  | 28100 | 24 | 23900 | 4.3 | 2.3417 | No
6501909 | Ground Water | GEOSTAR | GBV/GBH024**4*1 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501910 | Ground Water | GEOSTAR | GBV/GBH024**4*4 |  | 28100 | 27.5 | 24600 | 4.6 | 2.3417 | No
6501911 | Ground Water | GEOSTAR | GBV/GBH026**0*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501912 | Ground Water | GEOSTAR | GBV/GBH026**0*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501913 | Ground Water | GEOSTAR | GBV/GBH026**2*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501914 | Ground Water | GEOSTAR | GBV/GBH026**2*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501915 | Ground Water | GEOSTAR | GBV/GBH026**3*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501916 | Ground Water | GEOSTAR | GBV/GBH026**3*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501917 | Ground Water | GEOSTAR | GBV/GBH026**4*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
6501918 | Ground Water | GEOSTAR | GBV/GBH030**0*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
6501919 | Ground Water | GEOSTAR | GBV/GBH030**0*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501920 | Ground Water | GEOSTAR | GBV/GBH030**0*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501921 | Ground Water | GEOSTAR | GBV/GBH030**2*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
6501922 | Ground Water | GEOSTAR | GBV/GBH030**2*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501923 | Ground Water | GEOSTAR | GBV/GBH030**2*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501924 | Ground Water | GEOSTAR | GBV/GBH030**3*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
6501925 | Ground Water | GEOSTAR | GBV/GBH030**3*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501926 | Ground Water | GEOSTAR | GBV/GBH030**3*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501927 | Ground Water | GEOSTAR | GBV/GBH030**4*0 |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
6501928 | Ground Water | GEOSTAR | GBV/GBH030**4*1 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501929 | Ground Water | GEOSTAR | GBV/GBH030**4*4 |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
6501930 | Ground Water | GEOSTAR | GBV/GBH036**0*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
6501931 | Ground Water | GEOSTAR | GBV/GBH036**0*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501932 | Ground Water | GEOSTAR | GBV/GBH036**0*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501933 | Ground Water | GEOSTAR | GBV/GBH036**2*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
6501934 | Ground Water | GEOSTAR | GBV/GBH036**2*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501935 | Ground Water | GEOSTAR | GBV/GBH036**2*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501936 | Ground Water | GEOSTAR | GBV/GBH036**3*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
6501937 | Ground Water | GEOSTAR | GBV/GBH036**3*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501938 | Ground Water | GEOSTAR | GBV/GBH036**3*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501939 | Ground Water | GEOSTAR | GBV/GBH036**4*0 |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
6501940 | Ground Water | GEOSTAR | GBV/GBH036**4*1 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501941 | Ground Water | GEOSTAR | GBV/GBH036**4*4 |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
6501942 | Ground Water | GEOSTAR | GBV/GBH038**0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501943 | Ground Water | GEOSTAR | GBV/GBH038**0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501944 | Ground Water | GEOSTAR | GBV/GBH038**2*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501945 | Ground Water | GEOSTAR | GBV/GBH038**2*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
6501946 | Ground Water | GEOSTAR | GBV/GBH038**3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
206726849 | Ground Water | HYDRON MODULE | HBT060 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | Yes
206726850 | Ground Water | TETCO | TBT060 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | Yes
206726851 | Ground Water | GEOCOMFORT | GBT060*2 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
206726852 | Ground Water | HYDRON MODULE | HBT060*2 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
206726853 | Ground Water | TETCO | TBT060*2 | EED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
206726854 | Ground Water | GEOCOMFORT | GBT024 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | Yes
206726855 | Ground Water | GEOCOMFORT | GBT024 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | Yes
206726856 | Ground Water | HYDRON MODULE | HBT024 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | Yes
206726857 | Ground Water | HYDRON MODULE | HBT024 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | Yes
206726858 | Ground Water | TETCO | TBT024 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | Yes
206726859 | Ground Water | TETCO | TBT024 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | Yes
206726860 | Ground Water | GEOCOMFORT | GBT024*2 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
206726861 | Ground Water | GEOCOMFORT | GBT024*2 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | No
206726862 | Ground Water | HYDRON MODULE | HBT024*2 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
206726863 | Ground Water | HYDRON MODULE | HBT024*2 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | No
206726864 | Ground Water | TETCO | TBT024*2 | EED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
206726865 | Ground Water | TETCO | TBT024*2 | EAD024 | 27800 | 24.5 | 23900 | 4.7 | 2.3167 | No
214841665 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
214841666 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
214841668 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
214841675 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
214841676 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
214841677 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
214841678 | Ground Water | ClimateMaster | SC(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
214841679 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
214841680 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
214841682 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
214841684 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
214841686 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
214841687 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
214841688 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
214841690 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
214841697 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)015A |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
214841698 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)015A*V |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
214841699 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)018A |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
214841700 | Ground Water | ClimateMaster | SR(L/R/B/P/T/K/F)018A*V |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
214841701 | Ground Water | ClimateMaster | SZ(L/R/B/P/T/K)024A |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | Yes
214841702 | Ground Water | ClimateMaster | SZ(L/R/B/P/T/K)030A |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | Yes
214841704 | Ground Water | ClimateMaster | SZ(L/R/B/P/T/K)042A |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | Yes
214841705 | Ground Water | ClimateMaster | SZ(L/R/B/P/T/K)048A |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | Yes
214841706 | Ground Water | ClimateMaster | SZ(L/R/B/P/T/K)060A |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | Yes
214841707 | Ground Water | ClimateMaster | SY(L/R/B/P/T/K)024A |  | 27000 | 24.1 | 23500 | 4.7 | 2.25 | No
214841708 | Ground Water | ClimateMaster | SY(L/R/B/P/T/K)030A |  | 32900 | 21.7 | 28700 | 4.1 | 2.7417 | No
214841710 | Ground Water | ClimateMaster | SY(L/R/B/P/T/K)042A |  | 47500 | 22.8 | 41000 | 4.2 | 3.9583 | No
214841711 | Ground Water | ClimateMaster | SY(L/R/B/P/T/K)048A |  | 52000 | 22.9 | 45000 | 4.3 | 4.3333 | No
214841712 | Ground Water | ClimateMaster | SY(L/R/B/P/T/K)060A |  | 65000 | 22.8 | 55700 | 4.4 | 5.4167 | No
214844588 | Ground Water | WaterFurnace | W7A(V/H)024BV1**2 |  | 26300 | 37.8 | 32100 | 5 | 2.1917 | Yes
214844645 | Ground Water | WaterFurnace | W7A(V/H)036BV1**2 |  | 38200 | 28.7 | 41900 | 4.7 | 3.1833 | Yes
214844646 | Ground Water | WaterFurnace | W7A(V/H)048BV1**2 |  | 49000 | 27.4 | 54500 | 4.2 | 4.0833 | Yes
214844647 | Ground Water | WaterFurnace | W7A(V/H)060BV1**2 |  | 60700 | 23.4 | 66000 | 4.3 | 5.0583 | Yes
207348679 | Ground Water | WaterFurnace | URS070*4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348680 | Ground Water | WaterFurnace | URS070*4*5 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207348681 | Ground Water | WaterFurnace | URS060*0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
217642876 | Ground Water | GeoSmart Energy | S3A(V/H)006*R0**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
217642879 | Ground Water | GeoSmart Energy | S3A(V/H)015*R0**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642881 | Ground Water | GeoSmart Energy | S3A(V/H)024*S0**1 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
217642883 | Ground Water | GeoSmart Energy | S3A(V/H)036*S0**1 |  | 40000 | 23.5 | 35000 | 4.4 | 3.3333 | No
217642884 | Ground Water | GeoSmart Energy | S3A(V/H)042*S0**1 |  | 45000 | 23 | 41000 | 4.6 | 3.75 | No
217642886 | Ground Water | GeoSmart Energy | S3A(V/H)060*S0**1 |  | 66500 | 22 | 59000 | 4.3 | 5.5417 | No
217642888 | Ground Water | GeoSmart Energy | S3A(V/H)006*R2**6 |  | 9000 | 25 | 8000 | 4.2 | 0.75 | No
217642891 | Ground Water | GeoSmart Energy | S3A(V/H)015*R0**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642892 | Ground Water | GeoSmart Energy | S3A(V/H)015*R2**1 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642893 | Ground Water | GeoSmart Energy | S3A(V/H)015*R2**4 |  | 16500 | 23 | 13500 | 4.2 | 1.375 | No
217642897 | Ground Water | GeoSmart Energy | S3A(V/H)024*S0**4 |  | 26000 | 23 | 24000 | 4.5 | 2.1667 | No
209156961 | Ground Water | AE Air | WSV6024A |  | 25400 | 24 | 22000 | 4.1 | 2.1167 | No
209156963 | Ground Water | AE Air | WSV6036A |  | 41500 | 24 | 35500 | 4.1 | 3.4583 | No
209156964 | Ground Water | AE Air | WSV6042A |  | 46500 | 24 | 39000 | 4.2 | 3.875 | No
209156970 | Ground Water | AE Air | WSV6060A |  | 65000 | 23 | 53500 | 4.1 | 5.4167 | No
209156972 | Ground Water | AE Air | WSV6090A |  | 101000 | 22 | 73000 | 4.1 | 8.4167 | No
209156974 | Ground Water | AE Air | WSS6006*6* |  | 8600 | 26 | 7200 | 4.5 | 0.71667 | No
209156975 | Ground Water | AE Air | WSS6009*6* |  | 11200 | 26 | 8200 | 4.5 | 0.93333 | No
209156976 | Ground Water | AE Air | WSS6012*6* |  | 13800 | 26 | 10400 | 4.5 | 1.15 | No
209156977 | Ground Water | AE Air | WSS6015*6* |  | 18100 | 23.1 | 15500 | 4.3 | 1.5083 | No
209156981 | Ground Water | AE Air | WSHXE06A6* |  | 7800 | 23.5 | 6400 | 4.3 | 0.65 | No
209156987 | Ground Water | AE Air | WSHXE06A7* |  | 7800 | 23.5 | 6400 | 4.3 | 0.65 | No
209156993 | Ground Water | AE Air | WSS6006*7* |  | 8600 | 26 | 7200 | 4.5 | 0.71667 | No
209156994 | Ground Water | AE Air | WSS6009*7* |  | 11200 | 26 | 8200 | 4.5 | 0.93333 | No
209156995 | Ground Water | AE Air | WSS6012*7* |  | 13800 | 26 | 10400 | 4.5 | 1.15 | No
209156996 | Ground Water | AE Air | WSS6015*7* |  | 18100 | 23.1 | 15500 | 4.3 | 1.5083 | No
209180330 | Ground Water | HYDROTECH | WSV6018B* |  | 20000 | 21.1 | 16500 | 4.1 | 1.6667 | Yes
215415756 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)060A*VB |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
215415757 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)060A*VC |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
215415770 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)015A*B |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415771 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)015A*C |  | 16700 | 23.5 | 13800 | 4.3 | 1.3917 | No
215415772 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)015A*VB |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415773 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)015A*VC |  | 16900 | 26.2 | 13800 | 4.5 | 1.4083 | No
215415774 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)018A*B |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415775 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)018A*C |  | 20700 | 23 | 17900 | 4.2 | 1.725 | No
215415776 | Ground Water | Johnson Controls | BC(L/R/B/P/T/K/F)018A*VB |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415777 | Ground Water | SKYMARK | BC(L/R/B/P/T/K/F)018A*VC |  | 20900 | 25 | 17700 | 4.4 | 1.7417 | No
215415778 | Ground Water | Johnson Controls | BR(L/R/B/P/T/K/F)024A*B |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415779 | Ground Water | SKYMARK | BR(L/R/B/P/T/K/F)024A*C |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215224679 | Ground Water | BOSCH | RF007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | Yes
215224680 | Ground Water | BOSCH | RF007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | Yes
215224681 | Ground Water | BOSCH | RF009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | Yes
215224682 | Ground Water | BOSCH | RF009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | Yes
217014536 | Ground Water | COMFORTMAKER | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014537 | Ground Water | DAY & NIGHT | HCR72V**C******1 |  | 75000 | 22 | 71000 | 4.5 | 6.25 | Yes
217014538 | Ground Water | HEIL | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
217014539 | Ground Water | ARCOAIRE | HCR72V**N******1 |  | 74000 | 21.5 | 71000 | 4.5 | 6.1667 | Yes
10318048 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS048**1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
10318049 | Ground Water | GeoSmart Energy | GSZ048*1 | SRAA048* | 46900 | 25.5 | 41900 | 4.7 | 3.9083 | No
205767623 | Ground Water | ClimateMaster | TCH/V015A*W/K |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
205767624 | Ground Water | ClimateMaster | TRH/V015A*W/K |  | 16500 | 25 | 14100 | 4.5 | 1.375 | No
205767626 | Ground Water | ClimateMaster | TES/P038B | TAC038B | 40200 | 22.3 | 32800 | 4.4 | 3.35 | Yes
205767627 | Ground Water | ClimateMaster | TES/P049B | TAC049B | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
205780261 | Ground Water | GEOSTAR | 111J038**1*(1,2)* |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
205782086 | Ground Water | 5 SERIES INDOOR SPLITS | NSZ042J1 | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | No
205782087 | Ground Water | GEOSTAR | 103J042**1 | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
205782239 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
205782240 | Ground Water | YORK BY JOHNSON CONTROLS | YAZS042**1*J | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | No
205782241 | Ground Water | YORK BY JOHNSON CONTROLS | YAZT038**1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
205782242 | Ground Water | YORK BY JOHNSON CONTROLS | YAST038**1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
205782243 | Ground Water | GeoSmart Energy | GSZ036*1*J | SRAA036* | 33200 | 27.4 | 29600 | 4.9 | 2.7667 | Yes
205782244 | Ground Water | GeoSmart Energy | GSZ042*1*J | SRAA048* | 41300 | 25.6 | 36000 | 4.8 | 3.4417 | Yes
205782245 | Ground Water | GeoSmart Energy | GTZ038*1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
205782246 | Ground Water | GeoSmart Energy | GTS038*1*J | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
205782247 | Ground Water | GeoSmart Energy | GTS038*1*J | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
205782567 | Ground Water | YORK BY JOHNSON CONTROLS | YACT038**1*(1,2)* |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
205782571 | Ground Water | GeoSmart Energy | QT038**1*(1,2)* |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
205788273 | Ground Water | Johnson Controls | JSH/V/D018B B |  | 21300 | 24.8 | 18600 | 4.5 | 1.775 | No
205788274 | Ground Water | SKYMARK | JSH/V/D018B C |  | 21300 | 24.8 | 18600 | 4.5 | 1.775 | No
205788275 | Ground Water | Johnson Controls | JSH/V/D018B*K B |  | 22100 | 26.3 | 18900 | 4.9 | 1.8417 | No
205788276 | Ground Water | SKYMARK | JSH/V/D018B*K C |  | 22100 | 26.3 | 18900 | 4.9 | 1.8417 | No
205788277 | Ground Water | Johnson Controls | JSH/V/D024C B |  | 26500 | 24.9 | 24100 | 5 | 2.2083 | No
205788278 | Ground Water | SKYMARK | JSH/V/D024C C |  | 26500 | 24.9 | 24100 | 5 | 2.2083 | No
205788279 | Ground Water | Johnson Controls | JSH/V/D024C*K B |  | 26900 | 26.9 | 23800 | 5.2 | 2.2417 | No
205788280 | Ground Water | SKYMARK | JSH/V/D024C*K C |  | 26900 | 26.9 | 23800 | 5.2 | 2.2417 | No
205788281 | Ground Water | Johnson Controls | JSH/V/D030C B |  | 31000 | 24.9 | 28400 | 4.7 | 2.5833 | No
205788282 | Ground Water | SKYMARK | JSH/V/D030C C |  | 31000 | 24.9 | 28400 | 4.7 | 2.5833 | No
205788283 | Ground Water | Johnson Controls | JSH/V/D036C B |  | 35400 | 23.2 | 33200 | 4.7 | 2.95 | No
205788284 | Ground Water | SKYMARK | JSH/V/D036C C |  | 35400 | 23.2 | 33200 | 4.7 | 2.95 | No
205788285 | Ground Water | Johnson Controls | JSH/V/D036C*K B |  | 35400 | 24.9 | 32600 | 4.9 | 2.95 | No
205788286 | Ground Water | SKYMARK | JSH/V/D036C*K C |  | 35400 | 24.9 | 32600 | 4.9 | 2.95 | No
205788287 | Ground Water | Johnson Controls | JSH/V/D042C B |  | 43700 | 25.4 | 36200 | 4.7 | 3.6417 | No
205788288 | Ground Water | SKYMARK | JSH/V/D042C C |  | 43700 | 25.4 | 36200 | 4.7 | 3.6417 | No
205788289 | Ground Water | Johnson Controls | JSH/V/D042C*K B |  | 44400 | 29.5 | 35200 | 5.2 | 3.7 | Yes
205788290 | Ground Water | SKYMARK | JSH/V/D042C*K C |  | 44400 | 29.5 | 35200 | 5.2 | 3.7 | Yes
205788293 | Ground Water | Johnson Controls | JSH/V/D060C B |  | 68500 | 23.1 | 58200 | 4.2 | 5.7083 | No
205788294 | Ground Water | SKYMARK | JSH/V/D060C C |  | 68500 | 23.1 | 58200 | 4.2 | 5.7083 | No
214772087 | Ground Water | TRANE | EXVK042B |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214772088 | Ground Water | TRANE | EXVK0424 |  | 45300 | 27.7 | 39300 | 5.07 | 3.775 | No
214772089 | Ground Water | TRANE | EXVK048B |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214772090 | Ground Water | TRANE | EXVK0484 |  | 48300 | 26.5 | 41800 | 4.91 | 4.025 | No
214772091 | Ground Water | TRANE | EXVK060B |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214772092 | Ground Water | TRANE | EXVK0604 |  | 66800 | 26.2 | 58700 | 4.69 | 5.5667 | No
214772093 | Ground Water | TRANE | EXVK070B |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214772094 | Ground Water | TRANE | EXVK0704 |  | 67700 | 25.1 | 62200 | 4.73 | 5.6417 | No
214772095 | Ground Water | TRANE | DXVK024A |  | 27100 | 27.9 | 25000 | 5.2 | 2.2583 | No
214772096 | Ground Water | TRANE | DXVK036A |  | 36700 | 27.9 | 33600 | 5.3 | 3.0583 | No
214772097 | Ground Water | TRANE | DXVK048A |  | 49500 | 27 | 42900 | 5.3 | 4.125 | No
214772098 | Ground Water | TRANE | DXVK060A |  | 60100 | 27 | 53800 | 5.4 | 5.0083 | No
214772099 | Ground Water | TRANE | DXVK070A |  | 67000 | 22.8 | 67300 | 5 | 5.5833 | No
214772101 | Ground Water | TRANE | GEHK0097 |  | 9400 | 25.6 | 8600 | 4.94 | 0.78333 | No
214772102 | Ground Water | TRANE | GEHK0127 |  | 11900 | 22.3 | 11500 | 4.45 | 0.99167 | No
214772103 | Ground Water | TRANE | GEHK0157 |  | 16800 | 24.1 | 16700 | 4.69 | 1.4 | No
214772104 | Ground Water | TRANE | GEHK0187 |  | 19600 | 23.4 | 19500 | 4.46 | 1.6333 | No
214772105 | Ground Water | TRANE | GEHK024B |  | 27000 | 25.5 | 26000 | 4.5 | 2.25 | No
5646381 | Ground Water | GEOCOMFORT | GCT036D |  | 41700 | 23.5 | 36700 | 5 | 3.475 | Yes
5646382 | Ground Water | HYDRON MODULE | HCT036D |  | 41700 | 23.5 | 36700 | 5 | 3.475 | Yes
5646383 | Ground Water | TETCO | TCT036D |  | 41700 | 23.5 | 36700 | 5 | 3.475 | Yes
5646384 | Ground Water | GEOCOMFORT | GCT036D2 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646385 | Ground Water | HYDRON MODULE | HCT036D2 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646386 | Ground Water | TETCO | TCT036D2 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646387 | Ground Water | GEOCOMFORT | GCT036D3 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646388 | Ground Water | HYDRON MODULE | HCT036D3 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646389 | Ground Water | TETCO | TCT036D3 |  | 41700 | 23.5 | 36700 | 5 | 3.475 | No
5646391 | Ground Water | GEOCOMFORT | GXT048D |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | Yes
5646392 | Ground Water | HYDRON MODULE | HXT048D |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | Yes
5646393 | Ground Water | TETCO | TXT048D |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | Yes
5646394 | Ground Water | GEOCOMFORT | GXT048D2 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646395 | Ground Water | HYDRON MODULE | HXT048D2 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646396 | Ground Water | TETCO | TXT048D2 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646397 | Ground Water | GEOCOMFORT | GXT048D3 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646398 | Ground Water | HYDRON MODULE | HXT048D3 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646399 | Ground Water | TETCO | TXT048D3 |  | 53100 | 22.1 | 47400 | 4.6 | 4.425 | No
5646765 | Ground Water | GEOCOMFORT | GCT048D |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | Yes
5646766 | Ground Water | HYDRON MODULE | HCT048D |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | Yes
5646767 | Ground Water | TETCO | TCT048D |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | Yes
5646768 | Ground Water | GEOCOMFORT | GCT048D2 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5646769 | Ground Water | HYDRON MODULE | HCT048D2 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5646770 | Ground Water | TETCO | TCT048D2 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5646771 | Ground Water | GEOCOMFORT | GCT048D3 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5646772 | Ground Water | HYDRON MODULE | HCT048D3 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5646773 | Ground Water | TETCO | TCT048D3 |  | 53100 | 21.8 | 46700 | 4.6 | 4.425 | No
5699505 | Ground Water | TRANE | VSVE0421 |  | 50100 | 32.46 | 43600 | 5.08 | 4.175 | No
5699525 | Ground Water | TRANE | VSVE0422 |  | 50100 | 32.46 | 43600 | 5.08 | 4.175 | No
5699526 | Ground Water | TRANE | VSVE0424 |  | 50100 | 32.46 | 43600 | 5.08 | 4.175 | No
5699527 | Ground Water | TRANE | VSVE0601 |  | 70400 | 25.4 | 65400 | 4.8 | 5.8667 | No
5699534 | Ground Water | TRANE | VSVE0602 |  | 70400 | 25.4 | 65400 | 4.8 | 5.8667 | No
5699535 | Ground Water | TRANE | VSVE0604 |  | 70400 | 25.4 | 65400 | 4.8 | 5.8667 | No
5699628 | Ground Water | TRANE | VSHE0241 |  | 28400 | 31.76 | 24300 | 5.33 | 2.3667 | No
5699631 | Ground Water | TRANE | VSHE0242 |  | 28400 | 31.76 | 24300 | 5.33 | 2.3667 | No
5699633 | Ground Water | TRANE | VSHE0244 |  | 28400 | 31.76 | 24300 | 5.33 | 2.3667 | No
5699634 | Ground Water | TRANE | VSHE0331 |  | 37900 | 25.01 | 32300 | 4.98 | 3.1583 | No
5699635 | Ground Water | TRANE | VSHE0332 |  | 37900 | 25.01 | 32300 | 4.98 | 3.1583 | No
5699637 | Ground Water | TRANE | VSHE0334 |  | 37900 | 25.01 | 32300 | 4.98 | 3.1583 | No
5699639 | Ground Water | TRANE | VSHE0421 |  | 47300 | 30.9 | 42000 | 5.6 | 3.9417 | No
5699644 | Ground Water | TRANE | VSHE0422 |  | 47300 | 30.9 | 42000 | 5.6 | 3.9417 | No
5699650 | Ground Water | TRANE | VSHE0424 |  | 47300 | 30.9 | 42000 | 5.6 | 3.9417 | No
5699652 | Ground Water | TRANE | VSHE0501 |  | 56200 | 26 | 52500 | 5.1 | 4.6833 | No
5699653 | Ground Water | TRANE | VSHE0502 |  | 56200 | 26 | 52500 | 5.1 | 4.6833 | No
5699654 | Ground Water | TRANE | VSHE0504 |  | 56200 | 26 | 52500 | 5.1 | 4.6833 | No
5699655 | Ground Water | TRANE | VSHE0601 |  | 67300 | 22.8 | 66800 | 4.7 | 5.6083 | No
5699656 | Ground Water | TRANE | VSHE0602 |  | 67300 | 22.8 | 66800 | 4.7 | 5.6083 | No
5699657 | Ground Water | TRANE | VSHE0604 |  | 67300 | 22.8 | 66800 | 4.7 | 5.6083 | No
6501883 | Ground Water | GEOSTAR | GBV/GBH009**0*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
6501884 | Ground Water | GEOSTAR | GBV/GBH009**2*0 |  | 10800 | 22.2 | 10600 | 4.4 | 0.9 | No
6501885 | Ground Water | GEOSTAR | GBV/GBH012**0*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
6501886 | Ground Water | GEOSTAR | GBV/GBH012**2*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
6501887 | Ground Water | GEOSTAR | GBV/GBH015**0*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
6501888 | Ground Water | GEOSTAR | GBV/GBH015**0*1 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
6501889 | Ground Water | GEOSTAR | GBV/GBH015**0*4 |  | 16700 | 27 | 15500 | 4.7 | 1.3917 | No
6501890 | Ground Water | GEOSTAR | GBV/GBH015**2*0 |  | 16700 | 26 | 15500 | 4.5 | 1.3917 | No
7795945 | Ground Water | TETCO | TVT036 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | Yes
7795946 | Ground Water | GEOCOMFORT | GVT036*2 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795947 | Ground Water | HYDRON MODULE | HVT036*2 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795948 | Ground Water | TETCO | TVT036*2 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795949 | Ground Water | GEOCOMFORT | GVT036*3 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795950 | Ground Water | HYDRON MODULE | HVT036*3 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795951 | Ground Water | TETCO | TVT036*3 |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795952 | Ground Water | GEOCOMFORT | GVT036*A |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795953 | Ground Water | HYDRON MODULE | HVT036*A |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
7795954 | Ground Water | TETCO | TVT036*A |  | 40000 | 22.8 | 36900 | 4.6 | 3.3333 | No
8000290 | Ground Water | GEOCOOL | GCHP01024 |  | 22804 | 21.1 | 18640 | 4.1 | 1.9003 | No
8000291 | Ground Water | GEOCOOL | GCHP01031 |  | 32445 | 21.1 | 24698 | 4.1 | 2.7037 | No
8000292 | Ground Water | GEOCOOL | GCHP01036 |  | 32908 | 21.1 | 29358 | 4.1 | 2.7423 | No
8000293 | Ground Water | GEOCOOL | GCHP01041 |  | 37543 | 21.1 | 34484 | 4.1 | 3.1286 | No
8077723 | Ground Water | GEOCOMFORT | GYT060 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | Yes
8077724 | Ground Water | HYDRON MODULE | HYT060 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | Yes
8077725 | Ground Water | TETCO | TYT060 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | Yes
8077726 | Ground Water | GEOCOMFORT | GYT060*2 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077727 | Ground Water | HYDRON MODULE | HYT060*2 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077728 | Ground Water | TETCO | TYT060*2 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077729 | Ground Water | GEOCOMFORT | GYT060*3 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077730 | Ground Water | HYDRON MODULE | HYT060*3 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077731 | Ground Water | TETCO | TYT060*3 |  | 68700 | 24.8 | 61700 | 4.9 | 5.725 | No
8077735 | Ground Water | GEOCOMFORT | GYT072 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | Yes
8077736 | Ground Water | HYDRON MODULE | HYT072 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | Yes
8077737 | Ground Water | TETCO | TYT072 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | Yes
8077738 | Ground Water | GEOCOMFORT | GYT072*2 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8077739 | Ground Water | HYDRON MODULE | HYT072*2 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8077740 | Ground Water | TETCO | TYT072*2 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8077741 | Ground Water | GEOCOMFORT | GYT072*3 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8077742 | Ground Water | HYDRON MODULE | HYT072*3 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
8077743 | Ground Water | TETCO | TYT072*3 |  | 77600 | 23.2 | 71100 | 4.6 | 6.4667 | No
215415835 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)024A |  | 27500 | 23.3 | 24200 | 4.4 | 2.2917 | No
215415836 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415837 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)024A*V |  | 27800 | 24 | 24000 | 4.5 | 2.3167 | No
215415840 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415841 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)030A*V |  | 32800 | 23.5 | 28800 | 4.3 | 2.7333 | No
215415844 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415845 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)036A*V |  | 39200 | 25.2 | 35800 | 4.2 | 3.2667 | No
215415848 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415849 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)042A*V |  | 46000 | 22.9 | 39900 | 4.3 | 3.8333 | No
215415850 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415851 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)048A |  | 53000 | 21.5 | 48000 | 4.1 | 4.4167 | No
215415852 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415853 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)048A*V |  | 53500 | 22.8 | 47700 | 4.2 | 4.4583 | No
215415856 | Ground Water | CENTURY | MC(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
215415857 | Ground Water | COMFORT-AIRE | MC(L/R/B/P/T/K/F)060A*V |  | 67000 | 21.5 | 57100 | 4.2 | 5.5833 | No
204100658 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ064J1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204100659 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ064J1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
204100660 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS064J1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204100661 | Ground Water | 5 SERIES OUTDOOR SPLITS | NDS064J1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204101161 | Ground Water | 5 SERIES | NDV/NDH064J1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
204117015 | Ground Water | GEOSTAR | 101/102J064**1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
204117016 | Ground Water | GEOSTAR | 103J064**1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
204117017 | Ground Water | GEOSTAR | 103J064**1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
204140569 | Ground Water | GEO-THERMAL SPLIT | GZ024*******1**1 | CAP**24**AL* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140570 | Ground Water | CARRIER | GZ024*******1**1 | CAP**24**AL* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | No
204140571 | Ground Water | BRYANT | GZ024*******1**1 | CAP**24**AL* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140572 | Ground Water | HEIL | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | No
204140573 | Ground Water | ARCOAIRE | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140574 | Ground Water | KEEPRITE | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140575 | Ground Water | TEMPSTAR | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140576 | Ground Water | COMFORTMAKER | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
204140577 | Ground Water | DAY & NIGHT | HS024*******1**1 | EAM4X24L**A* | 28000 | 22.5 | 23900 | 4.3 | 2.3333 | Yes
214839009 | Ground Water | FHP | EC072-1VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214839010 | Ground Water | FHP | EC072-3VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214839011 | Ground Water | FHP | EC072-4VT/HZ*-*****C |  | 85100 | 24.4 | 69900 | 4.55 | 7.0917 | No
214839012 | Ground Water | FHP | EC096-1VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214839013 | Ground Water | FHP | EC096-3VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
214839014 | Ground Water | FHP | EC096-4VT/HZ*-*****C |  | 109100 | 24.45 | 102600 | 4.65 | 9.0917 | No
216625648 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D3**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625649 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D3**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625650 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D4**1 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625651 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D4**4 |  | 35200 | 27.5 | 31100 | 4.8 | 2.9333 | No
216625652 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S0**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625653 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S0**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625654 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S2**1 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
216625655 | Ground Water | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S2**4 |  | 33000 | 28 | 30000 | 4.5 | 2.75 | No
207178493 | Ground Water | GEOSTAR | 164J038**1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | No
4651865 | Ground Water | GEOSTAR | ZS023**2*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651866 | Ground Water | GeoSmart Energy | ZS023**2*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651869 | Ground Water | GEOSTAR | ZS023**3*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651870 | Ground Water | GeoSmart Energy | ZS023**3*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651873 | Ground Water | GEOSTAR | ZS023**4*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651874 | Ground Water | GeoSmart Energy | ZS023**4*4 |  | 25400 | 23 | 21900 | 4.3 | 2.1167 | No
4651882 | Ground Water | GEOSTAR | ZS042**0*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651883 | Ground Water | GeoSmart Energy | ZS042**0*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651888 | Ground Water | GEOSTAR | ZS042**3*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651889 | Ground Water | GeoSmart Energy | ZS042**3*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651894 | Ground Water | GEOSTAR | ZS042**4*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651895 | Ground Water | GeoSmart Energy | ZS042**4*4 |  | 45800 | 23.5 | 37000 | 4.3 | 3.8167 | No
4651936 | Ground Water | GEOSTAR | ZS048**0*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651937 | Ground Water | GeoSmart Energy | ZS048**0*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651942 | Ground Water | GeoSmart Energy | ZS048**3*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651943 | Ground Water | GEOSTAR | ZS048**3*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651948 | Ground Water | GEOSTAR | ZS048**4*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651949 | Ground Water | GeoSmart Energy | ZS048**4*4 |  | 52000 | 23.4 | 45900 | 4.2 | 4.3333 | No
4651954 | Ground Water | GEOSTAR | ZS060**0*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651955 | Ground Water | GeoSmart Energy | ZS060**0*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651966 | Ground Water | GEOSTAR | ZS060**4*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651967 | Ground Water | GeoSmart Energy | ZS060**4*4 |  | 65500 | 23 | 58400 | 4.1 | 5.4583 | No
4651972 | Ground Water | GEOSTAR | ZS070**0*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651973 | Ground Water | GeoSmart Energy | ZS070**0*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651978 | Ground Water | GEOSTAR | ZS070**3*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651979 | Ground Water | GeoSmart Energy | ZS070**3*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651984 | Ground Water | GEOSTAR | ZS070**4*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4651985 | Ground Water | GeoSmart Energy | ZS070**4*4 |  | 70000 | 21.1 | 64100 | 4.1 | 5.8333 | No
4659826 | Ground Water | TRANE | GEVE0721 |  | 84800 | 22.85 | 70200 | 4.18 | 7.0667 | No
4659827 | Ground Water | TRANE | GEVE0722 |  | 84800 | 22.85 | 70200 | 4.18 | 7.0667 | No
4659829 | Ground Water | TRANE | GEVE0724 |  | 84800 | 22.85 | 70200 | 4.18 | 7.0667 | No
4659831 | Ground Water | TRANE | GEVE0904 |  | 98600 | 22.91 | 83600 | 4.1 | 8.2167 | No
4659834 | Ground Water | TRANE | GEHE0721 |  | 83200 | 21.9 | 69100 | 4.2 | 6.9333 | No
4659835 | Ground Water | TRANE | GEHE0722 |  | 83200 | 21.9 | 69100 | 4.2 | 6.9333 | No
4659836 | Ground Water | TRANE | GEHE0728 |  | 83200 | 21.9 | 69100 | 4.2 | 6.9333 | No
4659837 | Ground Water | TRANE | GEHE0724 |  | 83200 | 21.9 | 69100 | 4.2 | 6.9333 | No
207200558 | Ground Water | GeoSmart Energy | GT064**1*(1,4)*J |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207200565 | Ground Water | GeoSmart Energy | GS060**1*(1,4)*H |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
207200566 | Ground Water | GeoSmart Energy | GS060**1*0*H |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
207200576 | Ground Water | GeoSmart Energy | GTZ026*1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207200577 | Ground Water | GeoSmart Energy | GTZ026*1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
207200578 | Ground Water | GeoSmart Energy | GTS026*1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
5315761 | Ground Water | WaterFurnace | NBV/NBH048**0*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315762 | Ground Water | WaterFurnace | NBV/NBH048**3*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315763 | Ground Water | WaterFurnace | NBV/NBH048**4*4 |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
5315774 | Ground Water | WaterFurnace | NBV/NBH060**0*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
5315776 | Ground Water | WaterFurnace | NBV/NBH060**3*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
5315777 | Ground Water | WaterFurnace | NBV/NBH060**4*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
5315778 | Ground Water | WaterFurnace | NBV/NBH060**5*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
5315780 | Ground Water | WaterFurnace | NBV/NBH060**0*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5315781 | Ground Water | WaterFurnace | NBV/NBH060**3*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5315782 | Ground Water | WaterFurnace | NBV/NBH060**4*1 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5315783 | Ground Water | WaterFurnace | NBV/NBH060**0*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5315784 | Ground Water | WaterFurnace | NBV/NBH060**3*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5315785 | Ground Water | WaterFurnace | NBV/NBH060**4*4 |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
5316500 | Ground Water | WaterFurnace | NBV/NBH070**0*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316501 | Ground Water | WaterFurnace | NBV/NBH070**3*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316502 | Ground Water | WaterFurnace | NBV/NBH070**4*1 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316503 | Ground Water | WaterFurnace | NBV/NBH070**0*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316504 | Ground Water | WaterFurnace | NBV/NBH070**3*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316505 | Ground Water | WaterFurnace | NBV/NBH070**4*4 |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
5316510 | Ground Water | WaterFurnace | NBV/NBH026**0*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316511 | Ground Water | WaterFurnace | NBV/NBH026**3*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316512 | Ground Water | WaterFurnace | NBV/NBH026**2*1 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316513 | Ground Water | WaterFurnace | NBV/NBH026**0*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316514 | Ground Water | WaterFurnace | NBV/NBH026**3*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316515 | Ground Water | WaterFurnace | NBV/NBH026**4*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5316516 | Ground Water | WaterFurnace | NBV/NBH026**2*4 |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
5317193 | Ground Water | WaterFurnace | NBV/NBH038**0*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317194 | Ground Water | WaterFurnace | NBV/NBH038**3*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317195 | Ground Water | WaterFurnace | NBV/NBH038**2*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317196 | Ground Water | WaterFurnace | NBV/NBH038**4*1 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317197 | Ground Water | WaterFurnace | NBV/NBH038**0*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317198 | Ground Water | WaterFurnace | NBV/NBH038**3*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317199 | Ground Water | WaterFurnace | NBV/NBH038**4*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317200 | Ground Water | WaterFurnace | NBV/NBH038**2*4 |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5317201 | Ground Water | WaterFurnace | NBV/NBH049**0*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317202 | Ground Water | WaterFurnace | NBV/NBH049**3*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317203 | Ground Water | WaterFurnace | NBV/NBH049**4*4 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317205 | Ground Water | WaterFurnace | NBV/NBH049**0*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317206 | Ground Water | WaterFurnace | NBV/NBH049**3*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317207 | Ground Water | WaterFurnace | NBV/NBH049**4*1 |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
5317209 | Ground Water | WaterFurnace | NBV/NBH064**0*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317210 | Ground Water | WaterFurnace | NBV/NBH064**3*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317211 | Ground Water | WaterFurnace | NBV/NBH064**4*1 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317270 | Ground Water | WaterFurnace | NBV/NBH064**4*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317328 | Ground Water | WaterFurnace | NBV/NBH064**3*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317329 | Ground Water | WaterFurnace | NBV/NBH064**0*4 |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | No
5317330 | Ground Water | WaterFurnace | NBV/NBH072**0*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5317331 | Ground Water | WaterFurnace | NBV/NBH072**3*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5317332 | Ground Water | WaterFurnace | NBV/NBH072**4*1 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5317333 | Ground Water | WaterFurnace | NBV/NBH072**4*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5317334 | Ground Water | WaterFurnace | NBV/NBH072**3*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
5317335 | Ground Water | WaterFurnace | NBV/NBH072**0*4 |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
215268733 | Ground Water | WaterFurnace | V5A(V/H)072*S4**4 |  | 76000 | 23 | 68000 | 4.4 | 6.3333 | No
215268734 | Ground Water | WaterFurnace | V5A(V/H)036*S2**1 |  | 39000 | 29 | 32000 | 5 | 3.25 | No
215268735 | Ground Water | WaterFurnace | V5A(V/H)018*D0**1 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
215268736 | Ground Water | WaterFurnace | V5A(V/H)018*D0**4 |  | 20800 | 27 | 18900 | 5 | 1.7333 | No
215268737 | Ground Water | WaterFurnace | V5A(V/H)024*D0**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268738 | Ground Water | WaterFurnace | V5A(V/H)024*D2**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268739 | Ground Water | WaterFurnace | V5A(V/H)024*D3**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
215268740 | Ground Water | WaterFurnace | V5A(V/H)024*D4**1 |  | 26400 | 25.2 | 23300 | 4.9 | 2.2 | No
5646375 | Ground Water | HYDRON MODULE | HXT036D2 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646376 | Ground Water | TETCO | TXT036D2 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646377 | Ground Water | GEOCOMFORT | GXT036D3 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646378 | Ground Water | HYDRON MODULE | HXT036D3 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
5646379 | Ground Water | TETCO | TXT036D3 |  | 42200 | 24 | 37000 | 5.1 | 3.5167 | No
207312016 | Ground Water | WaterFurnace | SDV049J1*(1,2) |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | Yes
207312019 | Ground Water | WaterFurnace | SDV038K1*(1,2) |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | Yes
207312171 | Ground Water | WaterFurnace | NDV/NDH026J1*(1,4) |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | Yes
207312172 | Ground Water | WaterFurnace | NDV/NDH038K1*(1,2,4) |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | Yes
207312173 | Ground Water | WaterFurnace | NDV/NDH049K1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | Yes
207312174 | Ground Water | WaterFurnace | NDV/NDH072J1*(1,4) |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | Yes
207312176 | Ground Water | WaterFurnace | NDV/NDH064K1*(1,4) |  | 69000 | 23.9 | 60400 | 4.6 | 5.75 | Yes
207312224 | Ground Water | WaterFurnace | NSV/NSH018J1*(1,4) |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | Yes
207312225 | Ground Water | WaterFurnace | NSV/NSH030J1*(1,4) |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | Yes
207312226 | Ground Water | WaterFurnace | NSV/NSH036K1*(1,2,4) |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | Yes
207312227 | Ground Water | WaterFurnace | NSV/NSH042K1*(1,2,4) |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | Yes
207312228 | Ground Water | WaterFurnace | NSV/NSH048K1*(1,2,4) |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | Yes
207312229 | Ground Water | WaterFurnace | NSV/NSH060K1*(1,4)* |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | Yes
207312230 | Ground Water | WaterFurnace | NSV/NSH070J1*(1,4) |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | Yes
207312262 | Ground Water | WaterFurnace | NSV/NSH012J1*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | Yes
207312263 | Ground Water | WaterFurnace | NSV/NSH018J1*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | Yes
207312265 | Ground Water | WaterFurnace | NSV/NSH030J1*(0,3) |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | Yes
207312266 | Ground Water | WaterFurnace | NSV/NSH036K1*(0,3) |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | Yes
207312267 | Ground Water | WaterFurnace | NSV/NSH042K1*(0,3) |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | Yes
207312268 | Ground Water | WaterFurnace | NSV/NSH048K1*(0,3) |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | Yes
207312269 | Ground Water | WaterFurnace | NSV/NSH060K1*0* |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | Yes
207312271 | Ground Water | WaterFurnace | NSV/NSH022J1*(1,4) |  | 21900 | 27.5 | 19500 | 5 | 1.825 | Yes
207318098 | Ground Water | WaterFurnace | LD(V,H)048A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | Yes
207323881 | Ground Water | WaterFurnace | NDZ026H1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
207323882 | Ground Water | WaterFurnace | NDZ026H1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | Yes
207323883 | Ground Water | WaterFurnace | NDS026H1 | SAH026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207323884 | Ground Water | WaterFurnace | NDS026H1 | SRAA026* | 25800 | 23 | 23300 | 4.6 | 2.15 | No
207323885 | Ground Water | WaterFurnace | NDZ038J1 | SAH036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207323886 | Ground Water | WaterFurnace | NDZ038J1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207323887 | Ground Water | WaterFurnace | NDS038J1 | SRAA036* | 38200 | 24.2 | 35100 | 4.7 | 3.1833 | Yes
207323888 | Ground Water | WaterFurnace | NDZ049J1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
207323889 | Ground Water | WaterFurnace | NDZ049J1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
207323890 | Ground Water | WaterFurnace | NDS049H1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207323891 | Ground Water | WaterFurnace | NDS049H1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
207323892 | Ground Water | WaterFurnace | NDZ064J1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
207323893 | Ground Water | WaterFurnace | NDZ064J1 | SRAA060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | Yes
207323894 | Ground Water | WaterFurnace | NDS064H1 | SAH060* | 63200 | 22.5 | 56000 | 4.4 | 5.2667 | No
215287184 | Ground Water | YORK BY JOHNSON CONTROLS | Y3A(V/H)024BD1**1 |  | 25700 | 21.3 | 23000 | 4.6 | 2.1417 | Yes
215310891 | Ground Water | GEOSTAR | G7A(V/H)024BV1**2 |  | 26300 | 37.8 | 32100 | 5 | 2.1917 | Yes
215310892 | Ground Water | GEOSTAR | G7A(V/H)036BV1**2 |  | 38200 | 28.7 | 41900 | 4.7 | 3.1833 | Yes
215310893 | Ground Water | GEOSTAR | G7A(V/H)048BV1**2 |  | 49000 | 27.4 | 54500 | 4.2 | 4.0833 | Yes
215310895 | Ground Water | GEOSTAR | G7A(V/H)060BV1**2 |  | 60700 | 23.4 | 66000 | 4.3 | 5.0583 | Yes
215310990 | Ground Water | GeoSmart Energy | S7A(V/H)024BV1**2 |  | 26300 | 37.8 | 32100 | 5 | 2.1917 | Yes
215224477 | Ground Water | FHP | CF007-1VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224478 | Ground Water | FHP | CF007-1VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224479 | Ground Water | FHP | CF009-1VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224480 | Ground Water | FHP | CF009-1VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224481 | Ground Water | FHP | CF012-1VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224482 | Ground Water | FHP | CF012-1VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224483 | Ground Water | FHP | CF015-1VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224484 | Ground Water | FHP | CF015-1VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
215224485 | Ground Water | FHP | CF018-1VT/HZC-*****A |  | 21300 | 24 | 18000 | 4.4 | 1.775 | No
215224486 | Ground Water | FHP | CF018-1VT/HZN-*****A |  | 21000 | 24 | 17700 | 4.4 | 1.75 | No
215224487 | Ground Water | FHP | CF007-2VT/HZC-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224488 | Ground Water | FHP | CF007-2VT/HZN-*****A |  | 8000 | 24 | 7000 | 4.7 | 0.66667 | No
215224489 | Ground Water | FHP | CF009-2VT/HZC-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224490 | Ground Water | FHP | CF009-2VT/HZN-*****A |  | 9800 | 23 | 8400 | 4.5 | 0.81667 | No
215224491 | Ground Water | FHP | CF012-2VT/HZC-*****A |  | 13500 | 23 | 12000 | 4.3 | 1.125 | No
215224492 | Ground Water | FHP | CF012-2VT/HZN-*****A |  | 13500 | 23 | 11700 | 4.3 | 1.125 | No
215224493 | Ground Water | FHP | CF015-2VT/HZC-*****A |  | 16700 | 24 | 14000 | 4.3 | 1.3917 | No
215224494 | Ground Water | FHP | CF015-2VT/HZN-*****A |  | 16700 | 23.5 | 14000 | 4.3 | 1.3917 | No
203383902 | Ground Water | FHP | EP048-1VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383903 | Ground Water | FHP | EP048-3VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383904 | Ground Water | FHP | EP048-4VT*******B |  | 51100 | 24 | 40500 | 4.3 | 4.2583 | No
203383905 | Ground Water | FHP | EP048-1HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383906 | Ground Water | FHP | EP048-3HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203383907 | Ground Water | FHP | EP048-4HZ*******B |  | 51100 | 24 | 40500 | 4.5 | 4.2583 | No
203459712 | Ground Water | BOSCH-GEO | LM036-1CSC-*****B | LM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | No
203459713 | Ground Water | BOSCH-GEO | LM036-1CSN-*****B | LM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | No
203459714 | Ground Water | BOSCH-GEO | LM048-1CSC-*****A | LM048-1AV/AH*-*****A | 52800 | 21.25 | 46600 | 4.6 | 4.4 | No
203459725 | Ground Water | FHP | LM036-1CSC-*****B | LM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | No
203459726 | Ground Water | FHP | LM036-1CSN-*****B | LM036-1AH*-*****B | 40900 | 22.2 | 35200 | 4.5 | 3.4083 | No
203459727 | Ground Water | FHP | LM048-1CSC-*****A | LM048-1AV/AH*-*****A | 52800 | 21.25 | 46600 | 4.6 | 4.4 | No
203459750 | Ground Water | BOSCH | LM024-1CS*-*****A | LM024-1AV/AH*****A*A | 28500 | 22.2 | 22200 | 4.5 | 2.375 | No
203459757 | Ground Water | FHP | LM024-1CS*-*****A | LM024-1AV/AH*****A*A | 28500 | 22.2 | 22200 | 4.5 | 2.375 | No
203466717 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ049J1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
203471325 | Ground Water | 5 SERIES INDOOR SPLITS | NDZ049J1 | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
203490411 | Ground Water | GeoSmart Energy | GTZ049*1*J | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
203490420 | Ground Water | GeoSmart Energy | GTZ049*1*J | SRAA048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | Yes
203495469 | Ground Water | GEOSTAR | 101/102J049**1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
203495470 | Ground Water | GEOSTAR | 103J049**1 | SAH048* | 51000 | 24.2 | 47100 | 4.6 | 4.25 | No
212505509 | Ground Water | HYDROTECH | WSH6036AM* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | No
212505510 | Ground Water | HYDROTECH | WSH6042AM* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | No
212505511 | Ground Water | HYDROTECH | WSH6048AM* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | No
212505512 | Ground Water | AE Air | WSH6024AM* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | No
212505513 | Ground Water | AE Air | WSH6036AM* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | No
212505514 | Ground Water | AE Air | WSH6042AM* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | No
212505515 | Ground Water | AE Air | WSH6048AM* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | No
212508378 | Ground Water | HYDROTECH | WSH6024AN* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | No
212508380 | Ground Water | HYDROTECH | WSH6030AN* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | No
212508382 | Ground Water | HYDROTECH | WSH6036AN* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | No
212508384 | Ground Water | HYDROTECH | WSH6042AN* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | No
212508386 | Ground Water | HYDROTECH | WSH6048AN* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | No
212508387 | Ground Water | HYDROTECH | WSH6060AM* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | No
212508388 | Ground Water | HYDROTECH | WSH6060AN* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | No
212508389 | Ground Water | HYDROTECH | WSH6072AM* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | No
212508390 | Ground Water | HYDROTECH | WSH6072AN* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | No
212508395 | Ground Water | AE Air | WSH6024AN* |  | 28500 | 25.8 | 23000 | 4.3 | 2.375 | No
212508397 | Ground Water | AE Air | WSH6030AN* |  | 32000 | 24 | 26000 | 4.2 | 2.6667 | No
212508399 | Ground Water | AE Air | WSH6036AN* |  | 39000 | 23.2 | 34000 | 4.1 | 3.25 | No
212508401 | Ground Water | AE Air | WSH6042AN* |  | 44500 | 23.3 | 40000 | 4.3 | 3.7083 | No
212508403 | Ground Water | AE Air | WSH6048AN* |  | 53000 | 23.6 | 46000 | 4.2 | 4.4167 | No
212508404 | Ground Water | AE Air | WSH6072AM* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | No
212508405 | Ground Water | AE Air | WSH6072AN* |  | 79000 | 21.8 | 69000 | 4.1 | 6.5833 | No
212509300 | Ground Water | AE Air | WSH6060AM* |  | 67000 | 23.5 | 55500 | 4.3 | 5.5833 | No
206438813 | Ground Water | FHP | EP012-1VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438814 | Ground Water | FHP | EP012-1HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438815 | Ground Water | FHP | EP012-1VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438816 | Ground Water | FHP | EP012-1HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438817 | Ground Water | FHP | EP012-0VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438818 | Ground Water | FHP | EP012-2VTC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438819 | Ground Water | FHP | EP012-0HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438820 | Ground Water | FHP | EP012-2HZC-*****B |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
206438821 | Ground Water | FHP | EP012-0VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438822 | Ground Water | FHP | EP012-2VTN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438823 | Ground Water | FHP | EP012-0HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
206438824 | Ground Water | FHP | EP012-2HZN-*****B |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
217351919 | Ground Water | TEMPSTAR | HS024SR*C******1 | F(C,T)MA5*36**** | 28200 | 24.2 | 23400 | 4.9 | 2.35 | Yes
217351920 | Ground Water | TEMPSTAR | HS024SR*N******1 | F(C,T)MA5*36**** | 27600 | 23.7 | 23000 | 4.8 | 2.3 | Yes
217351921 | Ground Water | TEMPSTAR | HS036SR*C******1 | F(C,T)MA5*36**** | 40000 | 21.7 | 36600 | 4.6 | 3.3333 | Yes
217351922 | Ground Water | TEMPSTAR | HS036SR*N******1 | F(C,T)MA5*36**** | 39000 | 21.3 | 35800 | 4.5 | 3.25 | Yes
217351923 | Ground Water | TEMPSTAR | HS036SR*C******1 | F(C,T)MA5*48**** | 41000 | 22.8 | 34800 | 4.8 | 3.4167 | Yes
217351924 | Ground Water | TEMPSTAR | HS036SR*N******1 | F(C,T)MA5*48**** | 40500 | 22.3 | 34200 | 4.7 | 3.375 | Yes
217351925 | Ground Water | TEMPSTAR | HS048SR*C******1 | F(C,T)MA5*48**** | 52000 | 21.5 | 46500 | 4.6 | 4.3333 | Yes
217351927 | Ground Water | TEMPSTAR | HS060SR*C******1 | F(C,T)MA5*60**** | 63500 | 21.7 | 60000 | 4.4 | 5.2917 | Yes
217351928 | Ground Water | TEMPSTAR | HS060SR*N******1 | F(C,T)MA5*60**** | 62500 | 21.3 | 59000 | 4.3 | 5.2083 | Yes
217351930 | Ground Water | TEMPSTAR | HS024SR*C******1 | EAM5*2*M*** | 27200 | 24.8 | 23900 | 4.5 | 2.2667 | Yes
217351931 | Ground Water | TEMPSTAR | HS024SR*N******1 | EAM5*2*M*** | 26700 | 24.3 | 23400 | 4.4 | 2.225 | Yes
217351932 | Ground Water | TEMPSTAR | HS036SR*C******1 | EAM5*3*M*** | 40300 | 22.8 | 34500 | 4.4 | 3.3583 | Yes
217351933 | Ground Water | TEMPSTAR | HS036SR*N******1 | EAM5*3*M*** | 39500 | 22.3 | 33800 | 4.3 | 3.2917 | Yes
217351934 | Ground Water | TEMPSTAR | HS048SR*C******1 | EAM5*4*M*** | 54600 | 22.3 | 46600 | 4.6 | 4.55 | Yes
217351935 | Ground Water | TEMPSTAR | HS048SR*N******1 | EAM5*4*M*** | 53500 | 21.9 | 45600 | 4.5 | 4.4583 | Yes
217351936 | Ground Water | TEMPSTAR | HS060SR*C******1 | EAM5*6*M*** | 66400 | 21.2 | 58800 | 4.3 | 5.5333 | Yes
217351938 | Ground Water | TEMPSTAR | HS072SR*C******1 | EAM5*6*M*** | 74500 | 22.2 | 68100 | 4.2 | 6.2083 | Yes
217351939 | Ground Water | TEMPSTAR | HS072SR*N******1 | EAM5*6*M*** | 73000 | 21.8 | 66700 | 4.1 | 6.0833 | Yes
217351941 | Ground Water | TEMPSTAR | HW024WR********1 |  | 24400 | 24.4 | 25600 | 4.25 | 2.0333 | Yes
217351943 | Ground Water | TEMPSTAR | HW048WR********1 |  | 44000 | 21.5 | 50000 | 4.25 | 3.6667 | Yes
8332268 | Ground Water | GEOCOMFORT | GYT024 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
8332358 | Ground Water | HYDRON MODULE | HYT024 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
8332380 | Ground Water | TETCO | TYT024 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | Yes
8332431 | Ground Water | GEOCOMFORT | GYT024*2 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8332452 | Ground Water | HYDRON MODULE | HYT024*2 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8332472 | Ground Water | TETCO | TYT024*2 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8332525 | Ground Water | GEOCOMFORT | GYT024*3 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8332545 | Ground Water | HYDRON MODULE | HYT024*3 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8332563 | Ground Water | TETCO | TYT024*3 |  | 29200 | 25.7 | 23400 | 5.3 | 2.4333 | No
8560797 | Ground Water | 5 SERIES | NSV/NSH060H1*0 |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
8560805 | Ground Water | 5 SERIES | NSV/NSH060H1*(1,4) |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
8560913 | Ground Water | GEOCOMFORT | GVS009 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | Yes
8560914 | Ground Water | HYDRON MODULE | HVS009 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | Yes
8560915 | Ground Water | TETCO | TVS009 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | Yes
8560916 | Ground Water | GEOCOMFORT | GVS009*A |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560917 | Ground Water | HYDRON MODULE | HVS009*A |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560918 | Ground Water | TETCO | TVS009*A |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560919 | Ground Water | GEOCOMFORT | GVS009*9 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560920 | Ground Water | HYDRON MODULE | HVS009*9 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560921 | Ground Water | TETCO | TVS009*9 |  | 11900 | 22.1 | 10600 | 4.4 | 0.99167 | No
8560930 | Ground Water | GEOCOMFORT | GVS012 |  | 13400 | 24.1 | 12100 | 4.3 | 1.1167 | Yes
8560931 | Ground Water | HYDRON MODULE | HVS012 |  | 13400 | 24.1 | 12100 | 4.3 | 1.1167 | Yes
8560932 | Ground Water | TETCO | TVS012 |  | 13400 | 24.1 | 12100 | 4.3 | 1.1167 | Yes
8560938 | Ground Water | GEOCOMFORT | GVS015 |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | Yes
8560939 | Ground Water | HYDRON MODULE | HVS015 |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | Yes
8560940 | Ground Water | TETCO | TVS015 |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | Yes
8560941 | Ground Water | GEOCOMFORT | GVS015*A |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | No
8560942 | Ground Water | HYDRON MODULE | HVS015*A |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | No
8560943 | Ground Water | TETCO | TVS015*A |  | 17500 | 28.8 | 14600 | 5.1 | 1.4583 | No
8560946 | Ground Water | GEOCOMFORT | GVS015*****1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | Yes
8560947 | Ground Water | HYDRON MODULE | HVS015*****1 |  | 17400 | 31.6 | 14400 | 5.4 | 1.45 | Yes
205993181 | Ground Water | TETCO | TBT060 | TAD060 | 65700 | 23.5 | 58300 | 4.4 | 5.475 | No
205993182 | Ground Water | GEOCOMFORT | GBT060*2 | GAD060 | 65700 | 23.5 | 58300 | 4.4 | 5.475 | No
205993183 | Ground Water | HYDRON MODULE | HBT060*2 | HAD060 | 65700 | 23.5 | 58300 | 4.4 | 5.475 | No
10447650 | Ground Water | RHEEM | RPVS/EC025 | RCFL-HM2621 | 26400 | 22.5 | 22900 | 4.5 | 2.2 | Yes
10447662 | Ground Water | RHEEM | RPVS/EC036 | RCFL-HM38** | 40200 | 22.3 | 32800 | 4.4 | 3.35 | Yes
10447665 | Ground Water | RHEEM | RPVS/EC048 | RCFL-HM48** | 52000 | 21.3 | 46100 | 4.2 | 4.3333 | Yes
10581108 | Ground Water | 5 SERIES | NDP026H1*1 |  | 26200 | 22.5 | 23800 | 4.7 | 2.1833 | No
10581109 | Ground Water | 5 SERIES | NDP038H1*(1,2) |  | 40000 | 24.4 | 34700 | 4.8 | 3.3333 | No
10581110 | Ground Water | 5 SERIES | NDP049H1*1 |  | 53800 | 24.3 | 46900 | 4.5 | 4.4833 | No
204031802 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,2,4)*J |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
204031806 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS048**1*(0,3)*J |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
204031808 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS048**1*(1,2,4)*J |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
4219428 | Ground Water | NORDIC | RH25HACW-P-1T-*-SDE** |  | 26200 | 22 | 22500 | 4.2 | 2.1833 | No
4219442 | Ground Water | NORDIC | RS25HACW-P-1T-* | AH-25-P-1-***** | 26800 | 23.1 | 23100 | 4.4 | 2.2333 | No
202391445 | Ground Water | CARRIER | 50PSV012**C3/CA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391446 | Ground Water | CARRIER | 50PSH012**C3/CA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391447 | Ground Water | CARRIER | 50PSV012**N3/CA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391448 | Ground Water | CARRIER | 50PSH012**N3/CA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391449 | Ground Water | CARRIER | 50PSV012**C0/BA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391450 | Ground Water | CARRIER | 50PSV012**C4/DA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391451 | Ground Water | CARRIER | 50PSH012**C0/BA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
7499460 | Ground Water | FHP | EP024-1HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7499461 | Ground Water | FHP | EP024-2HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7499463 | Ground Water | FHP | EP024-3HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7499464 | Ground Water | FHP | EP024-4HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7499465 | Ground Water | FHP | EP030-1HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7499466 | Ground Water | FHP | EP030-2HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7499467 | Ground Water | FHP | EP030-3HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
202330326 | Ground Water | AAON, Inc. | WH-048-3-H-ACAC-C0-10-100-A |  | 57100 | 21.3 | 52100 | 4.2 | 4.7583 | No
202330327 | Ground Water | AAON, Inc. | WH-048-2-H-ACAC-C0-10-200-A |  | 59400 | 24.4 | 52000 | 4.3 | 4.95 | No
202330328 | Ground Water | AAON, Inc. | WH-048-3-H-ACAC-C0-10-200-A |  | 59400 | 24.4 | 52000 | 4.3 | 4.95 | No
202330339 | Ground Water | AAON, Inc. | WH-036-A-H-DCAC-C0-10-200-A |  | 39800 | 21.9 | 33500 | 4.1 | 3.3167 | No
207178494 | Ground Water | GEOSTAR | 161/162J049**1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207178526 | Ground Water | GEOSTAR | 161/162H026**1*(1,4)***** |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
207178527 | Ground Water | GEOSTAR | 161/162J038**1*(1,2,4)***** |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
5296250 | Ground Water | TRANE | EXVF0301 |  | 31500 | 25.1 | 27400 | 4.8 | 2.625 | No
5296251 | Ground Water | TRANE | EXVF0302 |  | 31500 | 25.1 | 27400 | 4.8 | 2.625 | No
5296252 | Ground Water | TRANE | EXVF0307 |  | 31500 | 25.1 | 27400 | 4.8 | 2.625 | No
5296253 | Ground Water | TRANE | EXVF0361 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
5296254 | Ground Water | TRANE | EXVF0362 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
5296255 | Ground Water | TRANE | EXVF0363 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
5296256 | Ground Water | TRANE | EXVF0364 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
10268252 | Ground Water | TETCO | TBT048 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268253 | Ground Water | GEOCOMFORT | GBT048*2 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268254 | Ground Water | HYDRON MODULE | HBT048*2 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268255 | Ground Water | TETCO | TBT048*2 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268260 | Ground Water | GEOCOMFORT | GBT060 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
10268261 | Ground Water | HYDRON MODULE | HBT060 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
10268262 | Ground Water | TETCO | TBT060 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
202443467 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS042**1*(0,3)*J |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
202443468 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS036**1*(1,2,4)*J |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
202443469 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*J |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
202607199 | Ground Water | WHALEN | CASH*054AB**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
8786547 | Ground Water | GEOSTAR | 101/102H072**1*(1,4)***** |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
8786548 | Ground Water | GeoSmart Energy | GT072**1*(1,4)********H |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
8786549 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT072**1*(1,4)****H |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
8786552 | Ground Water | GEOSTAR | 101/102H012**1*0***** |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
8786553 | Ground Water | GeoSmart Energy | GS012**1*0********H |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
8786554 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS012**1*0****H |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
8786557 | Ground Water | GEOSTAR | 101/102H018**1*(1,4)***** |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
8103479 | Ground Water | TRANE | DXHF0241 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
8105907 | Ground Water | TRANE | DXHF0242 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
8105909 | Ground Water | TRANE | DXHF0243 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
8105911 | Ground Water | TRANE | DXHF0244 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
8105912 | Ground Water | TRANE | DXHF0247 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
202350414 | Ground Water | AAON, Inc. | RN-009-2-0-ACAY-C0-10-000-A |  | 113000 | 25.5 | 99600 | 5 | 9.4167 | No
202350415 | Ground Water | AAON, Inc. | RN-009-3-0-ACAY-C0-10-000-A |  | 113000 | 25.5 | 99600 | 5 | 9.4167 | No
202350416 | Ground Water | AAON, Inc. | RN-009-4-0-ACAY-C0-10-000-A |  | 113000 | 25.5 | 99600 | 5 | 9.4167 | No
202330407 | Ground Water | AAON, Inc. | WV-048-2-H-ACAC-C0-10-200-A |  | 55100 | 25.4 | 52200 | 4.5 | 4.5917 | No
202330408 | Ground Water | AAON, Inc. | WV-048-3-H-ACAC-C0-10-200-A |  | 55100 | 25.4 | 52200 | 4.5 | 4.5917 | No
202330417 | Ground Water | AAON, Inc. | WV-024-A-H-DCAC-C0-10-200-A |  | 27500 | 22.3 | 23400 | 4.4 | 2.2917 | No
202330418 | Ground Water | AAON, Inc. | WV-024-A-H-DCAC-C0-10-D00-A |  | 29000 | 22.7 | 21800 | 4.4 | 2.4167 | No
202330419 | Ground Water | AAON, Inc. | WV-024-3-H-DCAC-C0-10-200-A |  | 27500 | 22.3 | 23400 | 4.4 | 2.2917 | No
202330379 | Ground Water | AAON, Inc. | WV-030-1-H-ACAC-C0-10-200-A |  | 29600 | 21.8 | 28400 | 4.2 | 2.4667 | No
202330380 | Ground Water | AAON, Inc. | WV-030-A-H-ACAC-C0-10-200-A |  | 29600 | 21.8 | 28400 | 4.2 | 2.4667 | No
202330383 | Ground Water | AAON, Inc. | WV-030-2-H-ACAC-C0-10-200-A |  | 29600 | 21.8 | 28400 | 4.2 | 2.4667 | No
202330284 | Ground Water | AAON, Inc. | WH-018-A-H-ACAC-C0-10-200-A |  | 19500 | 26.5 | 16100 | 4.8 | 1.625 | No
6581203 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS022**1*(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
202330271 | Ground Water | AAON, Inc. | WH-009-B-H-ACAC-C0-10-200-A |  | 10300 | 23.3 | 8800 | 4.2 | 0.85833 | No
202330272 | Ground Water | AAON, Inc. | WH-009-1-H-ACAC-C0-10-200-A |  | 10300 | 23.3 | 8800 | 4.2 | 0.85833 | No
202330273 | Ground Water | AAON, Inc. | WH-009-A-H-ACAC-C0-10-200-A |  | 10300 | 23.3 | 8800 | 4.2 | 0.85833 | No
204344184 | Ground Water | 7 SERIES | NVV/NVH036B1*(1,2) |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
4230750 | Ground Water | DAIKIN | WCCW4024*E*04* |  | 29600 | 23.5 | 23600 | 4.4 | 2.4667 | No
4230752 | Ground Water | DAIKIN | WCCW4024*F*04* |  | 29600 | 23.5 | 23600 | 4.4 | 2.4667 | No
4230754 | Ground Water | DAIKIN | WCCW4024*J*04* |  | 29600 | 23.5 | 23600 | 4.4 | 2.4667 | No
4231098 | Ground Water | DAIKIN | WCCW4024*K*04* |  | 29600 | 23.5 | 23600 | 4.4 | 2.4667 | No
202391379 | Ground Water | AQUARIUS | EP012-0HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391380 | Ground Water | AQUARIUS | EP012-2HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391433 | Ground Water | FHP | EP012-2HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391434 | Ground Water | FHP | EP012-0HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391435 | Ground Water | FHP | EP012-2VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391436 | Ground Water | FHP | EP012-0VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391437 | Ground Water | FHP | EP012-2HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
8105979 | Ground Water | TRANE | DXVF0602 |  | 65700 | 22.7 | 65400 | 4.8 | 5.475 | No
8105980 | Ground Water | TRANE | DXVF0603 |  | 65700 | 22.7 | 65400 | 4.8 | 5.475 | No
8105981 | Ground Water | TRANE | DXVF0604 |  | 65700 | 22.7 | 65400 | 4.8 | 5.475 | No
8105982 | Ground Water | TRANE | DXVF0608 |  | 65700 | 22.7 | 65400 | 4.8 | 5.475 | No
8105983 | Ground Water | TRANE | DXVF0701 |  | 74600 | 22.5 | 75000 | 4.5 | 6.2167 | No
8105984 | Ground Water | TRANE | DXVF0702 |  | 74600 | 22.5 | 75000 | 4.5 | 6.2167 | No
8105985 | Ground Water | TRANE | DXVF0703 |  | 74600 | 22.5 | 75000 | 4.5 | 6.2167 | No
202350506 | Ground Water | AAON, Inc. | WH-036-1-H-DCAC-C0-10-200-A |  | 39800 | 21.9 | 33500 | 4.1 | 3.3167 | No
202350507 | Ground Water | AAON, Inc. | WH-036-2-H-DCAC-C0-10-200-A |  | 39800 | 21.9 | 33500 | 4.1 | 3.3167 | No
202350510 | Ground Water | AAON, Inc. | WH-048-1-H-DCAC-C0-10-200-A |  | 56200 | 27.3 | 46200 | 4.4 | 4.6833 | No
202350511 | Ground Water | AAON, Inc. | WH-048-2-H-DCAC-C0-10-200-A |  | 56200 | 27.3 | 46200 | 4.4 | 4.6833 | No
202350514 | Ground Water | AAON, Inc. | WV-024-1-H-DCAC-C0-10-200-A |  | 27500 | 22.3 | 23400 | 4.4 | 2.2917 | No
5696567 | Ground Water | 5 SERIES | NSV/NSH022G1*(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
5708463 | Ground Water | AMERICAN STANDARD | A1GX022***1**(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
5708493 | Ground Water | TRANE/AMERICAN STANDARD | T1GX022***1**(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
5708550 | Ground Water | GEOSTAR | 101/102A022**1*(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
5708623 | Ground Water | GeoSmart Energy | GS022**1*(0,3) |  | 23000 | 28 | 18100 | 4.6 | 1.9167 | No
5731224 | Ground Water | BARD | GTC36S2-A | GTA3600UD1AA+GTB1-A | 41000 | 21.6 | 37500 | 4.8 | 3.4167 | No
5296257 | Ground Water | TRANE | EXVF0367 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
5296258 | Ground Water | TRANE | EXVF0368 |  | 38600 | 24.4 | 35100 | 4.51 | 3.2167 | No
5296259 | Ground Water | TRANE | EXVF0421 |  | 45400 | 23.4 | 41200 | 4.6 | 3.7833 | No
5296260 | Ground Water | TRANE | EXVF0422 |  | 45400 | 23.4 | 41200 | 4.6 | 3.7833 | No
5296261 | Ground Water | TRANE | EXVF0423 |  | 45400 | 23.4 | 41200 | 4.6 | 3.7833 | No
5296262 | Ground Water | TRANE | EXVF0424 |  | 45400 | 23.4 | 41200 | 4.6 | 3.7833 | No
5296263 | Ground Water | TRANE | EXVF0488 |  | 50300 | 23.58 | 46400 | 4.76 | 4.1917 | No
5295943 | Ground Water | TRANE | EXHF0241 |  | 25900 | 23.8 | 24100 | 4.5 | 2.1583 | No
5295946 | Ground Water | TRANE | EXHF0242 |  | 25900 | 23.8 | 24100 | 4.5 | 2.1583 | No
5295949 | Ground Water | TRANE | EXHF0247 |  | 25900 | 23.8 | 24100 | 4.5 | 2.1583 | No
202391438 | Ground Water | FHP | EP012-0HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391439 | Ground Water | FHP | EP012-2VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391440 | Ground Water | FHP | EP012-0VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391441 | Ground Water | FHP | EP012-1HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391442 | Ground Water | FHP | EP012-1VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391443 | Ground Water | FHP | EP012-1HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391444 | Ground Water | FHP | EP012-1VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
8106144 | Ground Water | TRANE | DXVF0704 |  | 74600 | 22.5 | 75000 | 4.5 | 6.2167 | No
8106145 | Ground Water | TRANE | DXVF0708 |  | 74600 | 22.5 | 75000 | 4.5 | 6.2167 | No
202330472 | Ground Water | AAON, Inc. | RN-007-2-0-ACAY-C0-10-000-A |  | 84500 | 21.6 | 72300 | 4.4 | 7.0417 | No
202330473 | Ground Water | AAON, Inc. | RN-007-3-0-ACAY-C0-10-000-A |  | 84500 | 21.6 | 72300 | 4.4 | 7.0417 | No
202330474 | Ground Water | AAON, Inc. | RN-007-4-0-ACAY-C0-10-000-A |  | 84500 | 21.6 | 72300 | 4.4 | 7.0417 | No
202330573 | Ground Water | AAON, Inc. | WH-006-B-H-ACAC-C0-10-200-A |  | 7100 | 24.2 | 5900 | 4.1 | 0.59167 | No
202330574 | Ground Water | AAON, Inc. | WH-006-1-H-ACAC-C0-10-200-A |  | 7100 | 24.2 | 5900 | 4.1 | 0.59167 | No
202330575 | Ground Water | AAON, Inc. | WH-006-A-H-ACAC-C0-10-200-A |  | 7100 | 24.2 | 5900 | 4.1 | 0.59167 | No
202330576 | Ground Water | AAON, Inc. | WV-006-B-H-ACAC-C0-10-200-A |  | 6900 | 24.2 | 7000 | 5.1 | 0.575 | No
202330391 | Ground Water | AAON, Inc. | WV-036-2-H-ACAC-C0-10-200-A |  | 40400 | 23 | 35600 | 4.3 | 3.3667 | No
202330392 | Ground Water | AAON, Inc. | WV-036-3-H-ACAC-C0-10-200-A |  | 40400 | 23 | 35600 | 4.3 | 3.3667 | No
202330395 | Ground Water | AAON, Inc. | WV-042-1-H-ACAC-C0-10-200-A |  | 47600 | 23.4 | 43900 | 4.2 | 3.9667 | No
202330396 | Ground Water | AAON, Inc. | WV-042-A-H-ACAC-C0-10-200-A |  | 47600 | 23.4 | 43900 | 4.2 | 3.9667 | No
202330297 | Ground Water | AAON, Inc. | WH-030-1-H-DCAC-C0-10-200-A |  | 34100 | 21.5 | 31200 | 4.1 | 2.8417 | No
205536324 | Ground Water | AAON, Inc. | WH-072-2-H-DCAC-C0-10-200-A |  | 91000 | 24 | 75800 | 4.3 | 7.5833 | No
205536327 | Ground Water | AAON, Inc. | WH-072-3-H-DCAC-C0-10-200-A |  | 91000 | 24 | 75800 | 4.3 | 7.5833 | No
205536344 | Ground Water | AAON, Inc. | WV-072-2-0-DCAC-C0-10-200-A |  | 90800 | 25 | 79800 | 4.9 | 7.5667 | No
205536348 | Ground Water | AAON, Inc. | WV-072-3-0-DCAC-C0-10-200-A |  | 90800 | 25 | 79800 | 4.9 | 7.5667 | No
9951968 | Ground Water | BARD | GV27S3AA |  | 26600 | 22.8 | 26200 | 5 | 2.2167 | No
9951969 | Ground Water | BARD | GV38S3AA |  | 41400 | 22 | 38600 | 4.7 | 3.45 | No
9951970 | Ground Water | BARD | GV51S3AA |  | 53500 | 21.7 | 49500 | 4.45 | 4.4583 | No
8789582 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS022**1*(0,3)****H |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
8789586 | Ground Water | GEOSTAR | 101/102H022**1*(1,4)***** |  | 21900 | 27.5 | 19500 | 5 | 1.825 | No
8789591 | Ground Water | GEOSTAR | 101/102H030**1*(0,3)***** |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
8789592 | Ground Water | GeoSmart Energy | GS030**1*(0,3)********H |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
8789593 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS030**1*(0,3)****H |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
8789596 | Ground Water | GEOSTAR | 101/102H030**1*(1,4)***** |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
8789597 | Ground Water | GeoSmart Energy | GS030**1*(1,4)********H |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
8105913 | Ground Water | TRANE | DXHF0248 |  | 29100 | 26 | 25600 | 4.7 | 2.425 | No
8105914 | Ground Water | TRANE | DXHF0361 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
8105916 | Ground Water | TRANE | DXHF0362 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
8105922 | Ground Water | TRANE | DXHF0363 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
8105923 | Ground Water | TRANE | DXHF0364 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
8105924 | Ground Water | TRANE | DXHF0367 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
8105925 | Ground Water | TRANE | DXHF0368 |  | 41800 | 24.1 | 39500 | 4.7 | 3.4833 | No
202350426 | Ground Water | AAON, Inc. | RN-011-2-0-ACAY-C0-10-000-A |  | 129000 | 22 | 123200 | 4.6 | 10.75 | No
202350427 | Ground Water | AAON, Inc. | RN-011-3-0-ACAY-C0-10-000-A |  | 129000 | 22 | 123200 | 4.6 | 10.75 | No
202350428 | Ground Water | AAON, Inc. | RN-011-4-0-ACAY-C0-10-000-A |  | 129000 | 22 | 123200 | 4.6 | 10.75 | No
202330420 | Ground Water | AAON, Inc. | WV-030-A-H-DCAC-C0-10-200-A |  | 33600 | 22.3 | 30800 | 4.3 | 2.8 | No
202330421 | Ground Water | AAON, Inc. | WV-030-3-H-DCAC-C0-10-200-A |  | 33600 | 22.3 | 30800 | 4.3 | 2.8 | No
202330422 | Ground Water | AAON, Inc. | WV-036-A-H-DCAC-C0-10-200-A |  | 41500 | 23.6 | 36600 | 4.5 | 3.4583 | No
202330424 | Ground Water | AAON, Inc. | WV-036-3-H-DCAC-C0-10-200-A |  | 41500 | 23.6 | 36600 | 4.5 | 3.4583 | No
202330425 | Ground Water | AAON, Inc. | WV-042-A-H-DCAC-C0-10-200-A |  | 48000 | 22.7 | 41300 | 4.4 | 4 | No
202330426 | Ground Water | AAON, Inc. | WV-042-3-H-DCAC-C0-10-200-A |  | 48000 | 22.7 | 41300 | 4.4 | 4 | No
202330384 | Ground Water | AAON, Inc. | WV-030-3-H-ACAC-C0-10-200-A |  | 29600 | 21.8 | 28400 | 4.2 | 2.4667 | No
202330387 | Ground Water | AAON, Inc. | WV-036-1-H-ACAC-C0-10-200-A |  | 40400 | 23 | 35600 | 4.3 | 3.3667 | No
202330388 | Ground Water | AAON, Inc. | WV-036-A-H-ACAC-C0-10-200-A |  | 40400 | 23 | 35600 | 4.3 | 3.3667 | No
202330305 | Ground Water | AAON, Inc. | WH-036-1-H-ACAC-C0-10-100-A |  | 39800 | 22.3 | 35900 | 4.1 | 3.3167 | No
202330306 | Ground Water | AAON, Inc. | WH-036-A-H-ACAC-C0-10-100-A |  | 39800 | 22.3 | 35900 | 4.1 | 3.3167 | No
202330307 | Ground Water | AAON, Inc. | WH-036-1-H-ACAC-C0-10-200-A |  | 40700 | 24.3 | 36400 | 4.4 | 3.3917 | No
202330308 | Ground Water | AAON, Inc. | WH-036-A-H-ACAC-C0-10-200-A |  | 40700 | 24.3 | 36400 | 4.4 | 3.3917 | No
202330309 | Ground Water | AAON, Inc. | WH-036-2-H-ACAC-C0-10-100-A |  | 39800 | 22.3 | 35900 | 4.1 | 3.3167 | No
202330310 | Ground Water | AAON, Inc. | WH-036-3-H-ACAC-C0-10-100-A |  | 39800 | 22.3 | 35900 | 4.1 | 3.3167 | No
202330311 | Ground Water | AAON, Inc. | WH-036-2-H-ACAC-C0-10-200-A |  | 40700 | 24.3 | 36400 | 4.4 | 3.3917 | No
205993156 | Ground Water | GEOCOMFORT | GBT024 | GAD024 | 28900 | 26.9 | 23900 | 4.7 | 2.4083 | No
205993157 | Ground Water | HYDRON MODULE | HBT024 | HED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
205993158 | Ground Water | HYDRON MODULE | HBT024 | HAD024 | 28900 | 26.9 | 23900 | 4.7 | 2.4083 | No
204452547 | Ground Water | GeoSmart Energy | VI036**1*(1,2)* |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
204457696 | Ground Water | YORK BY JOHNSON CONTROLS | YAFV036**1*(1,2)* |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
204474784 | Ground Water | GEOSTAR | 141/142B036**1*(1,2) |  | 38000 | 31.5 | 41000 | 4.6 | 3.1667 | No
214855068 | Ground Water | WHALEN | CASH*036AD**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855069 | Ground Water | WHALEN | CASH*036AJ**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855070 | Ground Water | WHALEN | CASH*036AM**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855071 | Ground Water | WHALEN | CASV*036AB**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855072 | Ground Water | WHALEN | CASV*036AD**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855073 | Ground Water | WHALEN | CASV*036AJ**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
214855074 | Ground Water | WHALEN | CASV*036AM**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
7499468 | Ground Water | FHP | EP030-4HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7499480 | Ground Water | FHP | EP060-1HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7499482 | Ground Water | FHP | EP060-3HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7499483 | Ground Water | FHP | EP060-4HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7499484 | Ground Water | FHP | EP070-1HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
7499485 | Ground Water | FHP | EP070-3HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
7499487 | Ground Water | FHP | EP070-4HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
214855061 | Ground Water | WHALEN | CASH*030AJ**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855062 | Ground Water | WHALEN | CASH*030AM**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855063 | Ground Water | WHALEN | CASV*030AB**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855064 | Ground Water | WHALEN | CASV*030AD**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855065 | Ground Water | WHALEN | CASV*030AJ**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855066 | Ground Water | WHALEN | CASV*030AM**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855067 | Ground Water | WHALEN | CASH*036AB**B**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330298 | Ground Water | AAON, Inc. | WH-030-A-H-DCAC-C0-10-200-A |  | 34100 | 21.5 | 31200 | 4.1 | 2.8417 | No
202330303 | Ground Water | AAON, Inc. | WH-030-2-H-DCAC-C0-10-200-A |  | 34100 | 21.5 | 31200 | 4.1 | 2.8417 | No
202330304 | Ground Water | AAON, Inc. | WH-030-3-H-DCAC-C0-10-200-A |  | 34100 | 21.5 | 31200 | 4.1 | 2.8417 | No
207200555 | Ground Water | GeoSmart Energy | GT072**1*(1,4)*H |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207200556 | Ground Water | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
207200557 | Ground Water | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
207200559 | Ground Water | GeoSmart Energy | GS012**1*0*H |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
207200560 | Ground Water | GeoSmart Energy | GS018**1*(1,4)*H |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
207200561 | Ground Water | GeoSmart Energy | GS018**1*0*H |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
207200562 | Ground Water | GeoSmart Energy | GS022**1*(0,3)*H |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
206599757 | Ground Water | 5 SERIES | NSV/NSH060J1*0* |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
205993121 | Ground Water | HYDRON MODULE | HBS018*2 | HED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
205993122 | Ground Water | HYDRON MODULE | HBS018*2 | HAD018 | 24300 | 31.6 | 18700 | 5 | 2.025 | No
205993123 | Ground Water | TETCO | TBS018*2 | TED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
205993124 | Ground Water | TETCO | TBS018*2 | TAD018 | 24300 | 31.6 | 18700 | 5 | 2.025 | No
205993125 | Ground Water | GEOCOMFORT | GBT036 | GED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
205993126 | Ground Water | GEOCOMFORT | GBT036 | GAD036 | 39700 | 24.8 | 37200 | 4.7 | 3.3083 | No
205993127 | Ground Water | HYDRON MODULE | HBT036 | HED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
205993139 | Ground Water | HYDRON MODULE | HBT048 | HED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
205993140 | Ground Water | HYDRON MODULE | HBT048 | HAD048 | 54200 | 25.4 | 50800 | 4.8 | 4.5167 | No
205993141 | Ground Water | TETCO | TBT048 | TED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
10268263 | Ground Water | GEOCOMFORT | GBT060*2 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
10268264 | Ground Water | HYDRON MODULE | HBT060*2 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
10268265 | Ground Water | TETCO | TBT060*2 | MPD060 | 66200 | 22.7 | 57000 | 4.2 | 5.5167 | No
10268268 | Ground Water | GEOCOMFORT | GBT060 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268269 | Ground Water | HYDRON MODULE | HBT060 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268270 | Ground Water | TETCO | TBT060 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268271 | Ground Water | GEOCOMFORT | GBT060*2 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
202391369 | Ground Water | AQUARIUS | EP012-1VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391370 | Ground Water | AQUARIUS | EP012-1HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391371 | Ground Water | AQUARIUS | EP012-1VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
8105972 | Ground Water | TRANE | DXVF0368 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
8105973 | Ground Water | TRANE | DXVF0481 |  | 54200 | 24.8 | 50400 | 4.9 | 4.5167 | No
8105974 | Ground Water | TRANE | DXVF0482 |  | 54200 | 24.8 | 50400 | 4.9 | 4.5167 | No
8105975 | Ground Water | TRANE | DXVF0483 |  | 54200 | 24.8 | 50400 | 4.9 | 4.5167 | No
8105976 | Ground Water | TRANE | DXVF0484 |  | 54200 | 24.8 | 50400 | 4.9 | 4.5167 | No
8105977 | Ground Water | TRANE | DXVF0488 |  | 54200 | 24.8 | 50400 | 4.9 | 4.5167 | No
8105978 | Ground Water | TRANE | DXVF0601 |  | 65700 | 22.7 | 65400 | 4.8 | 5.475 | No
202330577 | Ground Water | AAON, Inc. | WV-006-1-H-ACAC-C0-10-200-A |  | 6900 | 24.2 | 7000 | 5.1 | 0.575 | No
202330578 | Ground Water | AAON, Inc. | WV-006-A-H-ACAC-C0-10-200-A |  | 6900 | 24.2 | 7000 | 5.1 | 0.575 | No
202330738 | Ground Water | WHALEN | CASH*024AB**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330739 | Ground Water | WHALEN | CASV*024AB**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330740 | Ground Water | WHALEN | CASH*024AD**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330741 | Ground Water | WHALEN | CASV*024AD**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330742 | Ground Water | WHALEN | CASH*030AB**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
207348743 | Ground Water | WaterFurnace | URT096*3*5 |  | 100600 | 25.9 | 89400 | 4.7 | 8.3833 | No
207348744 | Ground Water | WaterFurnace | URT096*4*5 |  | 100600 | 25.9 | 89400 | 4.7 | 8.3833 | No
202607200 | Ground Water | WHALEN | CASV*054AB**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607201 | Ground Water | WHALEN | CASH*054AD**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607202 | Ground Water | WHALEN | CASV*054AD**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607203 | Ground Water | WHALEN | CASH*054AJ**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607204 | Ground Water | WHALEN | CASV*054AJ**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607205 | Ground Water | WHALEN | CASH*054AM**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
202607206 | Ground Water | WHALEN | CASV*054AM**A**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
8560542 | Ground Water | 5 SERIES | NSV/NSH012H1*0 |  | 13200 | 23.1 | 12000 | 4.2 | 1.1 | No
8560785 | Ground Water | 5 SERIES | NSV/NSH018H1*0 |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
8560786 | Ground Water | 5 SERIES | NSV/NSH022H1*(0,3) |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
8560787 | Ground Water | 5 SERIES | NSV/NSH030H1*(0,3) |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
8560799 | Ground Water | 5 SERIES | NSV/NSH018H1*(1,4) |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
8560800 | Ground Water | 5 SERIES | NSV/NSH022H1*(1,4) |  | 21900 | 27.5 | 19500 | 5 | 1.825 | No
214855082 | Ground Water | WHALEN | CASV*042AM**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855083 | Ground Water | WHALEN | CASH*048AB**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855084 | Ground Water | WHALEN | CASH*048AD**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855085 | Ground Water | WHALEN | CASH*048AJ**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855086 | Ground Water | WHALEN | CASH*048AM**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855087 | Ground Water | WHALEN | CASV*048AB**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855088 | Ground Water | WHALEN | CASV*048AD**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330371 | Ground Water | AAON, Inc. | WV-024-1-H-ACAC-C0-10-200-A |  | 24900 | 23.4 | 22200 | 4.1 | 2.075 | No
202330372 | Ground Water | AAON, Inc. | WV-024-A-H-ACAC-C0-10-200-A |  | 24900 | 23.4 | 22200 | 4.1 | 2.075 | No
202330375 | Ground Water | AAON, Inc. | WV-024-2-H-ACAC-C0-10-200-A |  | 24900 | 23.4 | 22200 | 4.1 | 2.075 | No
202330376 | Ground Water | AAON, Inc. | WV-024-3-H-ACAC-C0-10-200-A |  | 24900 | 23.4 | 22200 | 4.1 | 2.075 | No
202330277 | Ground Water | AAON, Inc. | WH-015-1-H-ACAC-C0-10-100-A |  | 16500 | 26.1 | 14600 | 4.9 | 1.375 | No
202330278 | Ground Water | AAON, Inc. | WH-015-A-H-ACAC-C0-10-100-A |  | 16500 | 26.1 | 14600 | 4.9 | 1.375 | No
202330279 | Ground Water | AAON, Inc. | WH-015-1-H-ACAC-C0-10-200-A |  | 17100 | 29.9 | 14400 | 5.2 | 1.425 | No
202330280 | Ground Water | AAON, Inc. | WH-015-A-H-ACAC-C0-10-200-A |  | 17100 | 29.9 | 14400 | 5.2 | 1.425 | No
202330281 | Ground Water | AAON, Inc. | WH-018-1-H-ACAC-C0-10-100-A |  | 19600 | 23.5 | 17600 | 4.6 | 1.6333 | No
202330282 | Ground Water | AAON, Inc. | WH-018-A-H-ACAC-C0-10-100-A |  | 19600 | 23.5 | 17600 | 4.6 | 1.6333 | No
202330283 | Ground Water | AAON, Inc. | WH-018-1-H-ACAC-C0-10-200-A |  | 19500 | 26.5 | 16100 | 4.8 | 1.625 | No
5612208 | Ground Water | GeoSmart Energy | VI060**1*1 |  | 60000 | 28.6 | 65000 | 4.3 | 5 | No
5613676 | Ground Water | GEOSTAR | 141/142A048**1*1 |  | 49000 | 31.7 | 55000 | 4.3 | 4.0833 | No
5613677 | Ground Water | GEOSTAR | 141/142A060**1*1 |  | 60000 | 28.6 | 65000 | 4.3 | 5 | No
202350515 | Ground Water | AAON, Inc. | WV-024-1-H-DCAC-C0-10-D00-A |  | 29000 | 22.7 | 21800 | 4.4 | 2.4167 | No
202350516 | Ground Water | AAON, Inc. | WV-024-2-H-DCAC-C0-10-200-A |  | 27500 | 22.3 | 23400 | 4.4 | 2.2917 | No
202350517 | Ground Water | AAON, Inc. | WV-030-1-H-DCAC-C0-10-200-A |  | 33600 | 22.3 | 30800 | 4.3 | 2.8 | No
202350518 | Ground Water | AAON, Inc. | WV-030-2-H-DCAC-C0-10-200-A |  | 33600 | 22.3 | 30800 | 4.3 | 2.8 | No
202350519 | Ground Water | AAON, Inc. | WV-036-1-H-DCAC-C0-10-200-A |  | 41500 | 23.6 | 36600 | 4.5 | 3.4583 | No
202350521 | Ground Water | AAON, Inc. | WV-036-2-H-DCAC-C0-10-200-A |  | 41500 | 23.6 | 36600 | 4.5 | 3.4583 | No
7493326 | Ground Water | YORK BY JOHNSON CONTROLS | YLFT048*A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | No
7167333 | Ground Water | CARRIER | 50PSH/V007***3/CA |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
7167334 | Ground Water | CARRIER | 50PSH/V009***3/CA |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
7167335 | Ground Water | CARRIER | 50PSH/V009***4/DA |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
7167337 | Ground Water | CARRIER | 50PSH/V012***3/CA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
7167338 | Ground Water | CARRIER | 50PSH/V015***3/CA |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
7167339 | Ground Water | CARRIER | 50PSH/V015***4/DA |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
7167342 | Ground Water | CARRIER | 50PSH/V024***3/CA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
205993178 | Ground Water | TETCO | TBT072*2 | TAD072 | 70700 | 21.1 | 70500 | 4.1 | 5.8917 | No
205993179 | Ground Water | GEOCOMFORT | GBT060 | GAD060 | 65700 | 23.5 | 58300 | 4.4 | 5.475 | No
205993180 | Ground Water | HYDRON MODULE | HBT060 | HAD060 | 65700 | 23.5 | 58300 | 4.4 | 5.475 | No
8786558 | Ground Water | GeoSmart Energy | GS018**1*(1,4)********H |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
8786559 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS018**1*(1,4)****H |  | 20600 | 26 | 18700 | 4.6 | 1.7167 | No
8786562 | Ground Water | GEOSTAR | 101/102H018**1*0***** |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
8786563 | Ground Water | GeoSmart Energy | GS018**1*0********H |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
8786564 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS018**1*0****H |  | 20600 | 24.7 | 18700 | 4.3 | 1.7167 | No
8789580 | Ground Water | GEOSTAR | 101/102H022**1*(0,3)***** |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
8789581 | Ground Water | GeoSmart Energy | GS022**1*(0,3)********H |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
202330765 | Ground Water | WHALEN | CASH*024AM**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330766 | Ground Water | WHALEN | CASV*024AM**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330767 | Ground Water | WHALEN | CASH*030AJ**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330768 | Ground Water | WHALEN | CASV*030AJ**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330769 | Ground Water | WHALEN | CASH*030AM**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330770 | Ground Water | WHALEN | CASV*030AM**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330771 | Ground Water | WHALEN | CASH*036AJ**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
7167555 | Ground Water | CARRIER | 50PSH/V024***5/EA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7167556 | Ground Water | CARRIER | 50PSH/V024***6/FA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
202330340 | Ground Water | AAON, Inc. | WH-036-3-H-DCAC-C0-10-200-A |  | 39800 | 21.9 | 33500 | 4.1 | 3.3167 | No
202330343 | Ground Water | AAON, Inc. | WH-048-A-H-DCAC-C0-10-200-A |  | 56200 | 27.3 | 46200 | 4.4 | 4.6833 | No
202330344 | Ground Water | AAON, Inc. | WH-048-3-H-DCAC-C0-10-200-A |  | 56200 | 27.3 | 46200 | 4.4 | 4.6833 | No
202330347 | Ground Water | AAON, Inc. | WV-009-B-H-ACAC-C0-10-200-A |  | 11200 | 25.3 | 10300 | 4.7 | 0.93333 | No
202330348 | Ground Water | AAON, Inc. | WV-009-1-H-ACAC-C0-10-200-A |  | 11200 | 25.3 | 10300 | 4.7 | 0.93333 | No
6966727 | Ground Water | TRANE | EXVF0121 |  | 14200 | 25.37 | 12400 | 4.5 | 1.1833 | No
6966753 | Ground Water | TRANE | EXVF0122 |  | 14200 | 25.37 | 12400 | 4.5 | 1.1833 | No
6580833 | Ground Water | YORK BY JOHNSON CONTROLS | YAFV048**1*1 |  | 49000 | 31.7 | 55000 | 4.3 | 4.0833 | No
6580857 | Ground Water | YORK BY JOHNSON CONTROLS | YAFV060**1*1 |  | 60000 | 28.6 | 65000 | 4.3 | 5 | No
201846902 | Ground Water | GEOSTAR | 111H038**1*(1,2) |  | 38200 | 23.8 | 33200 | 4.5 | 3.1833 | No
10268279 | Ground Water | TETCO | TBT060*2 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10318053 | Ground Water | GEOSTAR | 103H060**1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
10443493 | Ground Water | GEOCOMFORT | GBS018 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443494 | Ground Water | HYDRON MODULE | HBS018 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443495 | Ground Water | TETCO | TBS018 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443496 | Ground Water | GEOCOMFORT | GBS018*2 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
3920297 | Ground Water | AQUARIUS | EP030-2HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
3920298 | Ground Water | AQUARIUS | EP030-4HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
3920299 | Ground Water | AQUARIUS | EP030-3HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
3920300 | Ground Water | AQUARIUS | EP030-1HZ/VT |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
3920500 | Ground Water | AQUARIUS | EP060-4HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
3920501 | Ground Water | AQUARIUS | EP060-3HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
3920502 | Ground Water | AQUARIUS | EP060-1HZ/VT |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
8789598 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****H |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
8791888 | Ground Water | GEOSTAR | 101/102H070**1*(1,4)***** |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
8791889 | Ground Water | GeoSmart Energy | GS070**1*(1,4)********H |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
8791890 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS070**1*(1,4)****H |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
8105926 | Ground Water | TRANE | DXHF0481 |  | 56600 | 24.7 | 50800 | 4.8 | 4.7167 | No
8105927 | Ground Water | TRANE | DXHF0482 |  | 56600 | 24.7 | 50800 | 4.8 | 4.7167 | No
8105928 | Ground Water | TRANE | DXHF0483 |  | 56600 | 24.7 | 50800 | 4.8 | 4.7167 | No
8105929 | Ground Water | TRANE | DXHF0484 |  | 56600 | 24.7 | 50800 | 4.8 | 4.7167 | No
8105930 | Ground Water | TRANE | DXHF0488 |  | 56600 | 24.7 | 50800 | 4.8 | 4.7167 | No
8105931 | Ground Water | TRANE | DXHF0701 |  | 74100 | 22.1 | 72700 | 4.5 | 6.175 | No
8105932 | Ground Water | TRANE | DXHF0702 |  | 74100 | 22.1 | 72700 | 4.5 | 6.175 | No
202330779 | Ground Water | WHALEN | CASH*048AJ**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330780 | Ground Water | WHALEN | CASV*048AJ**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330781 | Ground Water | WHALEN | CASH*048AM**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330782 | Ground Water | WHALEN | CASV*048AM**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330783 | Ground Water | WHALEN | CASH*060AJ**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330784 | Ground Water | WHALEN | CASV*060AJ**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330785 | Ground Water | WHALEN | CASH*060AM**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
7492839 | Ground Water | 3 SERIES | LD(V,H)048A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | No
202330367 | Ground Water | AAON, Inc. | WV-019-1-H-ACAC-C0-10-200-A |  | 21400 | 27 | 17000 | 4.1 | 1.7833 | No
202330368 | Ground Water | AAON, Inc. | WV-019-A-H-ACAC-C0-10-200-A |  | 21400 | 27 | 17000 | 4.1 | 1.7833 | No
202391372 | Ground Water | AQUARIUS | EP012-1HZN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391373 | Ground Water | AQUARIUS | EP012-0VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391374 | Ground Water | AQUARIUS | EP012-2VTC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391375 | Ground Water | AQUARIUS | EP012-0HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391376 | Ground Water | AQUARIUS | EP012-2HZC |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391377 | Ground Water | AQUARIUS | EP012-0VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391378 | Ground Water | AQUARIUS | EP012-2VTN |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
8105965 | Ground Water | TRANE | DXVF0247 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
8105966 | Ground Water | TRANE | DXVF0248 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
8105967 | Ground Water | TRANE | DXVF0361 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
8105968 | Ground Water | TRANE | DXVF0362 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
8105969 | Ground Water | TRANE | DXVF0363 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
8105970 | Ground Water | TRANE | DXVF0364 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
8105971 | Ground Water | TRANE | DXVF0367 |  | 40700 | 24.1 | 38800 | 4.7 | 3.3917 | No
214855043 | Ground Water | WHALEN | CASH*015AB**B**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
214855044 | Ground Water | WHALEN | CASH*015AD**B**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
214855045 | Ground Water | WHALEN | CASV*015AB**B**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
214855046 | Ground Water | WHALEN | CASV*015AD**B**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
202330750 | Ground Water | WHALEN | CASH*042AB**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330751 | Ground Water | WHALEN | CASV*042AB**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330752 | Ground Water | WHALEN | CASH*042AD**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330753 | Ground Water | WHALEN | CASV*042AD**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330754 | Ground Water | WHALEN | CASH*048AB**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330755 | Ground Water | WHALEN | CASV*048AB**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330756 | Ground Water | WHALEN | CASH*048AD**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330312 | Ground Water | AAON, Inc. | WH-036-3-H-ACAC-C0-10-200-A |  | 40700 | 24.3 | 36400 | 4.4 | 3.3917 | No
202330315 | Ground Water | AAON, Inc. | WH-042-1-H-ACAC-C0-10-200-A |  | 47800 | 22.9 | 39700 | 4.4 | 3.9833 | No
202330316 | Ground Water | AAON, Inc. | WH-042-A-H-ACAC-C0-10-200-A |  | 47800 | 22.9 | 39700 | 4.4 | 3.9833 | No
206599760 | Ground Water | 5 SERIES | NSV/NSH060J1*(1,4)* |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
206599762 | Ground Water | GEOSTAR | 101/102J060**1*0****** |  | 66600 | 22.8 | 57300 | 4.4 | 5.55 | No
206599765 | Ground Water | GEOSTAR | 101/102J060**1*(1,4)****** |  | 66900 | 24.3 | 59200 | 4.7 | 5.575 | No
205993135 | Ground Water | TETCO | TBT036*2 | TED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
205993136 | Ground Water | TETCO | TBT036*2 | TAD036 | 39700 | 24.8 | 37200 | 4.7 | 3.3083 | No
205993137 | Ground Water | GEOCOMFORT | GBT048 | GED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
205993138 | Ground Water | GEOCOMFORT | GBT048 | GAD048 | 54200 | 25.4 | 50800 | 4.8 | 4.5167 | No
205536354 | Ground Water | AAON, Inc. | WV-096-2-0-DCAC-C0-10-200-A |  | 108200 | 23.2 | 99200 | 4.5 | 9.0167 | No
205536369 | Ground Water | AAON, Inc. | WV-096-3-0-DCAC-C0-10-200-A |  | 108200 | 23.2 | 99200 | 4.5 | 9.0167 | No
205782568 | Ground Water | YORK BY JOHNSON CONTROLS | YACT049**1*(1,2)* |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | No
205782572 | Ground Water | GeoSmart Energy | QT049**1*(1,2)* |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | No
205993113 | Ground Water | GEOCOMFORT | GBS018 | GED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
10268203 | Ground Water | TETCO | TBT036*2 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268204 | Ground Water | GEOCOMFORT | GBT036 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268205 | Ground Water | HYDRON MODULE | HBT036 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268206 | Ground Water | TETCO | TBT036 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268207 | Ground Water | GEOCOMFORT | GBT036*2 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268208 | Ground Water | HYDRON MODULE | HBT036*2 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268209 | Ground Water | TETCO | TBT036*2 | ACD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
202443457 | Ground Water | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202443458 | Ground Water | GeoSmart Energy | GS036**1*(0,3)*J |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
202443459 | Ground Water | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
202443460 | Ground Water | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
202443465 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,2,4)*J |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202443466 | Ground Water | YORK BY JOHNSON CONTROLS | YAFS036**1*(0,3)*J |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
8786527 | Ground Water | GEOSTAR | 101/102H026**1*(1,4)***** |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
8786528 | Ground Water | GeoSmart Energy | GT026**1*(1,4)********H |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
8786529 | Ground Water | YORK BY JOHNSON CONTROLS | YAFT026**1*(1,4)****H |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
202330772 | Ground Water | WHALEN | CASV*036AJ**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330773 | Ground Water | WHALEN | CASH*036AM**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330774 | Ground Water | WHALEN | CASV*036AM**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330775 | Ground Water | WHALEN | CASH*042AJ**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330776 | Ground Water | WHALEN | CASV*042AJ**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330777 | Ground Water | WHALEN | CASH*042AM**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
202330778 | Ground Water | WHALEN | CASV*042AM**A**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
7167343 | Ground Water | CARRIER | 50PSH/V024***4/DA |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7167344 | Ground Water | CARRIER | 50PSH/V030***4/DA |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7167345 | Ground Water | CARRIER | 50PSH/V030***6/FA |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7167346 | Ground Water | CARRIER | 50PSH/V030***5/EA |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7167347 | Ground Water | CARRIER | 50PSH/V030***3/CA |  | 31000 | 27 | 25000 | 4.95 | 2.5833 | No
7167357 | Ground Water | CARRIER | 50PSH/V060***6/FA |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7167358 | Ground Water | CARRIER | 50PSH/V060***5/EA |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
6936993 | Ground Water | BARD | GTC60S2-A | HE49948D210B2705AW | 67500 | 21.56 | 61500 | 4.3 | 5.625 | No
5295957 | Ground Water | TRANE | EXHF0368 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
5295958 | Ground Water | TRANE | EXHF0364 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
5295959 | Ground Water | TRANE | EXHF0421 |  | 45800 | 23.3 | 42000 | 4.7 | 3.8167 | No
5295961 | Ground Water | TRANE | EXHF0422 |  | 45800 | 23.3 | 42000 | 4.7 | 3.8167 | No
5295963 | Ground Water | TRANE | EXHF0423 |  | 45800 | 23.3 | 42000 | 4.7 | 3.8167 | No
5295965 | Ground Water | TRANE | EXHF0424 |  | 45800 | 23.3 | 42000 | 4.7 | 3.8167 | No
5295967 | Ground Water | TRANE | EXHF0428 |  | 45800 | 23.3 | 42000 | 4.7 | 3.8167 | No
10443497 | Ground Water | HYDRON MODULE | HBS018*2 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443498 | Ground Water | TETCO | TBS018*2 | MCD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443499 | Ground Water | GEOCOMFORT | GBS018 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443500 | Ground Water | HYDRON MODULE | HBS018 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443501 | Ground Water | TETCO | TBS018 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443502 | Ground Water | GEOCOMFORT | GBS018*2 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443503 | Ground Water | HYDRON MODULE | HBS018*2 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10206404 | Ground Water | BARD | GTC36S2-A | HE37942D210B2505AW | 42000 | 23.9 | 38000 | 5 | 3.5 | No
10206405 | Ground Water | BARD | GTC36S2-A | HE37942D175B2505AW | 42000 | 23.9 | 38000 | 5 | 3.5 | No
214855103 | Ground Water | WHALEN | CASV*060AB**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855104 | Ground Water | WHALEN | CASV*060AD**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855105 | Ground Water | WHALEN | CASV*060AJ**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855106 | Ground Water | WHALEN | CASV*060AM**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330757 | Ground Water | WHALEN | CASV*048AD**A**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
202330758 | Ground Water | WHALEN | CASH*060AB**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330759 | Ground Water | WHALEN | CASV*060AB**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330760 | Ground Water | WHALEN | CASH*060AD**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330761 | Ground Water | WHALEN | CASV*060AD**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202330763 | Ground Water | WHALEN | CASH*024AJ**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330764 | Ground Water | WHALEN | CASV*024AJ**A**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855047 | Ground Water | WHALEN | CASH*018AB**B**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
214855048 | Ground Water | WHALEN | CASH*018AD**B**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
214855049 | Ground Water | WHALEN | CASV*018AB**B**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
214855050 | Ground Water | WHALEN | CASV*018AD**B**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
214855051 | Ground Water | WHALEN | CASH*024AB**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855052 | Ground Water | WHALEN | CASH*024AD**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855053 | Ground Water | WHALEN | CASH*024AJ**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
202330743 | Ground Water | WHALEN | CASV*030AB**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330744 | Ground Water | WHALEN | CASH*030AD**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330745 | Ground Water | WHALEN | CASV*030AD**A**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
202330746 | Ground Water | WHALEN | CASH*036AB**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330747 | Ground Water | WHALEN | CASV*036AB**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330748 | Ground Water | WHALEN | CASH*036AD**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330749 | Ground Water | WHALEN | CASV*036AD**A**(D,E) |  | 39000 | 25 | 36000 | 4.2 | 3.25 | No
202330319 | Ground Water | AAON, Inc. | WH-042-2-H-ACAC-C0-10-200-A |  | 47800 | 22.9 | 39700 | 4.4 | 3.9833 | No
202330320 | Ground Water | AAON, Inc. | WH-042-3-H-ACAC-C0-10-200-A |  | 47800 | 22.9 | 39700 | 4.4 | 3.9833 | No
202330321 | Ground Water | AAON, Inc. | WH-048-1-H-ACAC-C0-10-100-A |  | 57100 | 21.3 | 52100 | 4.2 | 4.7583 | No
202330322 | Ground Water | AAON, Inc. | WH-048-A-H-ACAC-C0-10-100-A |  | 57100 | 21.3 | 52100 | 4.2 | 4.7583 | No
202330323 | Ground Water | AAON, Inc. | WH-048-1-H-ACAC-C0-10-200-A |  | 59400 | 24.4 | 52000 | 4.3 | 4.95 | No
202330324 | Ground Water | AAON, Inc. | WH-048-A-H-ACAC-C0-10-200-A |  | 59400 | 24.4 | 52000 | 4.3 | 4.95 | No
202330325 | Ground Water | AAON, Inc. | WH-048-2-H-ACAC-C0-10-100-A |  | 57100 | 21.3 | 52100 | 4.2 | 4.7583 | No
206315253 | Ground Water | WHALEN | CASH*018AB**A**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
206315254 | Ground Water | WHALEN | CASV*018AB**A**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
206315255 | Ground Water | WHALEN | CASH*018AD**A**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
206315256 | Ground Water | WHALEN | CASV*018AD**A**(G,E) |  | 21000 | 25 | 18000 | 4.5 | 1.75 | No
207178547 | Ground Water | GEOSTAR | 161/162H072**1*(1,4)***** |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
207200554 | Ground Water | GeoSmart Energy | GT026**1*(1,4)*H |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
205993163 | Ground Water | HYDRON MODULE | HBT024*2 | HED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
205993164 | Ground Water | HYDRON MODULE | HBT024*2 | HAD024 | 28900 | 26.9 | 23900 | 4.7 | 2.4083 | No
205993165 | Ground Water | TETCO | TBT024*2 | TED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
205993166 | Ground Water | TETCO | TBT024*2 | TAD024 | 28900 | 26.9 | 23900 | 4.7 | 2.4083 | No
205993168 | Ground Water | GEOCOMFORT | GBT072 | GAD072 | 70700 | 21.1 | 70500 | 4.1 | 5.8917 | No
10443584 | Ground Water | HYDRON MODULE | HBT024 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443585 | Ground Water | TETCO | TBT024 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443586 | Ground Water | GEOCOMFORT | GBT024*2 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443587 | Ground Water | HYDRON MODULE | HBT024*2 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443588 | Ground Water | TETCO | TBT024*2 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443593 | Ground Water | GEOCOMFORT | GBT024 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10443594 | Ground Water | HYDRON MODULE | HBT024 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
203495471 | Ground Water | GEOSTAR | 101/102J048**1*(0,3) |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
8560801 | Ground Water | 5 SERIES | NSV/NSH030H1*(1,4) |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
8560806 | Ground Water | 5 SERIES | NSV/NSH070H1*(1,4) |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
8570181 | Ground Water | 5 SERIES | NDV/NDH072H1*(1,4) |  | 79000 | 22 | 71000 | 4.3 | 6.5833 | No
214855089 | Ground Water | WHALEN | CASV*048AJ**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855090 | Ground Water | WHALEN | CASV*048AM**B**(D,E) |  | 53800 | 22 | 46200 | 4.1 | 4.4833 | No
214855091 | Ground Water | WHALEN | CASH*054AB**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855092 | Ground Water | WHALEN | CASH*054AD**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855093 | Ground Water | WHALEN | CASH*054AJ**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855094 | Ground Water | WHALEN | CASH*054AM**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855095 | Ground Water | WHALEN | CASH*060AB**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
7167359 | Ground Water | CARRIER | 50PSH/V060***3/CA |  | 66500 | 23.25 | 56700 | 4.85 | 5.5417 | No
7167360 | Ground Water | CARRIER | 50PSH/V070***3/CA |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
7167361 | Ground Water | CARRIER | 50PSH/V070***5/EA |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
7167362 | Ground Water | CARRIER | 50PSH/V070***6/FA |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
202330349 | Ground Water | AAON, Inc. | WV-009-A-H-ACAC-C0-10-200-A |  | 11200 | 25.3 | 10300 | 4.7 | 0.93333 | No
202330350 | Ground Water | AAON, Inc. | WV-012-B-H-ACAC-C0-10-200-A |  | 15100 | 22.9 | 14400 | 4.4 | 1.2583 | No
202330351 | Ground Water | AAON, Inc. | WV-012-1-H-ACAC-C0-10-200-A |  | 15100 | 22.9 | 14400 | 4.4 | 1.2583 | No
202330352 | Ground Water | AAON, Inc. | WV-012-A-H-ACAC-C0-10-200-A |  | 15100 | 22.9 | 14400 | 4.4 | 1.2583 | No
202330355 | Ground Water | AAON, Inc. | WV-015-1-H-ACAC-C0-10-200-A |  | 16600 | 25.7 | 14700 | 4.2 | 1.3833 | No
6965857 | Ground Water | TRANE | EXHF0121 |  | 14000 | 25.08 | 11900 | 4.31 | 1.1667 | No
6965858 | Ground Water | TRANE | EXHF0122 |  | 14000 | 25.08 | 11900 | 4.31 | 1.1667 | No
6965859 | Ground Water | TRANE | EXHF0127 |  | 14000 | 25.08 | 11900 | 4.31 | 1.1667 | No
5360714 | Ground Water | BARD | GTC36S2-A | GTADP-3642-* | 42000 | 23.9 | 38000 | 5 | 3.5 | No
5360715 | Ground Water | BARD | GTC48S2-A | GTADP-4860-C | 54500 | 23.5 | 48000 | 4.55 | 4.5417 | No
5360791 | Ground Water | BARD | GTC60S2-A | GTADP-4860-C | 67500 | 21.56 | 61500 | 4.3 | 5.625 | No
5440741 | Ground Water | 7 SERIES | NVV/NVH048A1*1 |  | 49000 | 31.7 | 55000 | 4.3 | 4.0833 | No
5440778 | Ground Water | 7 SERIES | NVV/NVH060A1*1 |  | 60000 | 28.6 | 65000 | 4.3 | 5 | No
202923075 | Ground Water | GEOSTAR | 101/102J038**1*(1,2,4)***** |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
203113881 | Ground Water | GEOSTAR | 101/102J036**1*(0,3)***** |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
203113882 | Ground Water | GEOSTAR | 101/102J036**1*(1,2,4)***** |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
203113884 | Ground Water | GEOSTAR | 101/102J042**1*(0,3)***** |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
8849312 | Ground Water | 5 SERIES | NDV/NDH026H1*(1,4) |  | 27700 | 24 | 23900 | 4.8 | 2.3083 | No
202330786 | Ground Water | WHALEN | CASV*060AM**A**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
202350093 | Ground Water | 5 SERIES | NSV/NSH036J1*(0,3) |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
202350094 | Ground Water | 5 SERIES | NSV/NSH042J1*(0,3) |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
202350095 | Ground Water | 5 SERIES | NSV/NSH036J1*(1,2,4) |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
202350096 | Ground Water | 5 SERIES | NSV/NSH042J1*(1,2,4) |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
202350098 | Ground Water | 5 SERIES | NDV/NDH038J1*(1,2,4) |  | 40000 | 24.4 | 35000 | 4.9 | 3.3333 | No
202330399 | Ground Water | AAON, Inc. | WV-042-2-H-ACAC-C0-10-200-A |  | 47600 | 23.4 | 43900 | 4.2 | 3.9667 | No
202330400 | Ground Water | AAON, Inc. | WV-042-3-H-ACAC-C0-10-200-A |  | 47600 | 23.4 | 43900 | 4.2 | 3.9667 | No
202330403 | Ground Water | AAON, Inc. | WV-048-1-H-ACAC-C0-10-200-A |  | 55100 | 25.4 | 52200 | 4.5 | 4.5917 | No
202330404 | Ground Water | AAON, Inc. | WV-048-A-H-ACAC-C0-10-200-A |  | 55100 | 25.4 | 52200 | 4.5 | 4.5917 | No
202330356 | Ground Water | AAON, Inc. | WV-015-A-H-ACAC-C0-10-200-A |  | 16600 | 25.7 | 14700 | 4.2 | 1.3833 | No
202330359 | Ground Water | AAON, Inc. | WV-016-1-H-ACAC-C0-10-200-A |  | 17200 | 27.1 | 14800 | 4.2 | 1.4333 | No
202330360 | Ground Water | AAON, Inc. | WV-016-A-H-ACAC-C0-10-200-A |  | 17200 | 27.1 | 14800 | 4.2 | 1.4333 | No
206315249 | Ground Water | WHALEN | CASH*015AB**A**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
206315250 | Ground Water | WHALEN | CASV*015AB**A**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
206315251 | Ground Water | WHALEN | CASH*015AD**A**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
206315252 | Ground Water | WHALEN | CASV*015AD**A**(G,E) |  | 17000 | 25 | 15400 | 4.5 | 1.4167 | No
205993184 | Ground Water | TETCO | TBT060*2 | TAD060 | 65700 | 23.5 | 58300 | 4.4 | 5.475 | No
206199262 | Ground Water | RHEEM | RPVV/H/D026D |  | 28500 | 26.4 | 25800 | 5.3 | 2.375 | No
206199264 | Ground Water | RHEEM | RPVV/H/D049D |  | 55000 | 25.3 | 46800 | 4.6 | 4.5833 | No
206199265 | Ground Water | RHEEM | RPVV/H/D064D |  | 71500 | 24.4 | 63200 | 4.8 | 5.9583 | No
206199266 | Ground Water | RHEEM | RPVV/H/D072D |  | 77700 | 22.5 | 71400 | 4.4 | 6.475 | No
10581111 | Ground Water | 5 SERIES | NDP064H1*1 |  | 67500 | 23.1 | 58200 | 4.5 | 5.625 | No
10581112 | Ground Water | 5 SERIES | NDP072H1*1 |  | 77400 | 21.5 | 70600 | 4.3 | 6.45 | No
10581113 | Ground Water | YORK BY JOHNSON CONTROLS | YAPT026**1*1******H |  | 26200 | 22.5 | 23800 | 4.7 | 2.1833 | No
10581114 | Ground Water | YORK BY JOHNSON CONTROLS | YAPT038**1*(1,2)******H |  | 40000 | 24.4 | 34700 | 4.8 | 3.3333 | No
10581115 | Ground Water | YORK BY JOHNSON CONTROLS | YAPT049**1*1******H |  | 53800 | 24.3 | 46900 | 4.5 | 4.4833 | No
10581116 | Ground Water | YORK BY JOHNSON CONTROLS | YAPT064**1*1******H |  | 67500 | 23.1 | 58200 | 4.5 | 5.625 | No
10581117 | Ground Water | YORK BY JOHNSON CONTROLS | YAPT072**1*1******H |  | 77400 | 21.5 | 70600 | 4.3 | 6.45 | No
207200570 | Ground Water | GeoSmart Energy | GS036**1*(0,3)*J |  | 35100 | 24.4 | 29200 | 4.5 | 2.925 | No
207200571 | Ground Water | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 36800 | 28.8 | 29200 | 4.9 | 3.0667 | No
205993142 | Ground Water | TETCO | TBT048 | TAD048 | 54200 | 25.4 | 50800 | 4.8 | 4.5167 | No
205993143 | Ground Water | GEOCOMFORT | GBT048*2 | GED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
205993144 | Ground Water | GEOCOMFORT | GBT048*2 | GAD048 | 54200 | 25.4 | 50800 | 4.8 | 4.5167 | No
205993145 | Ground Water | HYDRON MODULE | HBT048*2 | HED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
205993146 | Ground Water | HYDRON MODULE | HBT048*2 | HAD048 | 54200 | 25.4 | 50800 | 4.8 | 4.5167 | No
205993147 | Ground Water | TETCO | TBT048*2 | TED048 | 55000 | 24.9 | 50800 | 4.9 | 4.5833 | No
205993148 | Ground Water | TETCO | TBT048*2 | TAD048 | 54200 | 25.4 | 50800 | 4.8 | 4.5167 | No
5295970 | Ground Water | TRANE | EXHF0481 |  | 50600 | 22.4 | 46900 | 4.56 | 4.2167 | No
5295971 | Ground Water | TRANE | EXHF0482 |  | 50600 | 22.4 | 46900 | 4.56 | 4.2167 | No
5295972 | Ground Water | TRANE | EXHF0483 |  | 50600 | 22.4 | 46900 | 4.56 | 4.2167 | No
5295973 | Ground Water | TRANE | EXHF0484 |  | 50600 | 22.4 | 46900 | 4.56 | 4.2167 | No
5295974 | Ground Water | TRANE | EXHF0488 |  | 50600 | 22.4 | 46900 | 4.56 | 4.2167 | No
205993159 | Ground Water | TETCO | TBT024 | TED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
205993160 | Ground Water | TETCO | TBT024 | TAD024 | 28900 | 26.9 | 23900 | 4.7 | 2.4083 | No
205993161 | Ground Water | GEOCOMFORT | GBT024*2 | GED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
205993162 | Ground Water | GEOCOMFORT | GBT024*2 | GAD024 | 28900 | 26.9 | 23900 | 4.7 | 2.4083 | No
10443577 | Ground Water | GEOCOMFORT | GBT024 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443578 | Ground Water | HYDRON MODULE | HBT024 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443579 | Ground Water | TETCO | TBT024 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443580 | Ground Water | GEOCOMFORT | GBT024*2 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443581 | Ground Water | HYDRON MODULE | HBT024*2 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443582 | Ground Water | TETCO | TBT024*2 | MCD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
10443583 | Ground Water | GEOCOMFORT | GBT024 | ACD024 | 26000 | 22.9 | 22700 | 4.3 | 2.1667 | No
205993128 | Ground Water | HYDRON MODULE | HBT036 | HAD036 | 39700 | 24.8 | 37200 | 4.7 | 3.3083 | No
205993129 | Ground Water | TETCO | TBT036 | TED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
205993130 | Ground Water | TETCO | TBT036 | TAD036 | 39700 | 24.8 | 37200 | 4.7 | 3.3083 | No
205993131 | Ground Water | GEOCOMFORT | GBT036*2 | GED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
205993132 | Ground Water | GEOCOMFORT | GBT036*2 | GAD036 | 39700 | 24.8 | 37200 | 4.7 | 3.3083 | No
205993133 | Ground Water | HYDRON MODULE | HBT036*2 | HED036 | 40500 | 24.6 | 36800 | 4.7 | 3.375 | No
205993134 | Ground Water | HYDRON MODULE | HBT036*2 | HAD036 | 39700 | 24.8 | 37200 | 4.7 | 3.3083 | No
10268233 | Ground Water | GEOCOMFORT | GBT048 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268234 | Ground Water | HYDRON MODULE | HBT048 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268235 | Ground Water | TETCO | TBT048 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268236 | Ground Water | GEOCOMFORT | GBT048*2 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268237 | Ground Water | HYDRON MODULE | HBT048*2 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268238 | Ground Water | TETCO | TBT048*2 | MPD060 | 55700 | 26.2 | 45700 | 4.6 | 4.6417 | No
10268244 | Ground Water | GEOCOMFORT | GBT048 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268198 | Ground Water | GEOCOMFORT | GBT036 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268199 | Ground Water | HYDRON MODULE | HBT036 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268200 | Ground Water | TETCO | TBT036 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268201 | Ground Water | GEOCOMFORT | GBT036*2 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
10268202 | Ground Water | HYDRON MODULE | HBT036*2 | MCD036 | 35000 | 21.7 | 35100 | 4.2 | 2.9167 | No
214855075 | Ground Water | WHALEN | CASH*042AB**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855076 | Ground Water | WHALEN | CASH*042AD**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855077 | Ground Water | WHALEN | CASH*042AJ**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855078 | Ground Water | WHALEN | CASH*042AM**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855079 | Ground Water | WHALEN | CASV*042AB**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855080 | Ground Water | WHALEN | CASV*042AD**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
214855081 | Ground Water | WHALEN | CASV*042AJ**B**(D,E) |  | 46700 | 22 | 41500 | 4.1 | 3.8917 | No
7499447 | Ground Water | FHP | EP007-1HZ/VT |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
7499448 | Ground Water | FHP | EP007-2HZ/VT |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
7499450 | Ground Water | FHP | EP009-1HZ/VT |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
7499451 | Ground Water | FHP | EP009-2HZ/VT |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
7499453 | Ground Water | FHP | EP012-1HZ/VT |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
7499455 | Ground Water | FHP | EP015-1HZ/VT |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
7499456 | Ground Water | FHP | EP015-2HZ/VT |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
214855054 | Ground Water | WHALEN | CASH*024AM**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855055 | Ground Water | WHALEN | CASV*024AB**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855056 | Ground Water | WHALEN | CASV*024AD**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855057 | Ground Water | WHALEN | CASV*024AJ**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855058 | Ground Water | WHALEN | CASV*024AM**B**(D,E) |  | 27400 | 24 | 23000 | 4.3 | 2.2833 | No
214855059 | Ground Water | WHALEN | CASH*030AB**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
214855060 | Ground Water | WHALEN | CASH*030AD**B**(D,E) |  | 32400 | 23 | 27612 | 4.2 | 2.7 | No
207200624 | Ground Water | GeoSmart Energy | VI048**1*1 |  | 49000 | 31.7 | 55000 | 4.3 | 4.0833 | No
207200625 | Ground Water | GeoSmart Energy | VI060**1*1 |  | 60000 | 28.6 | 65000 | 4.3 | 5 | No
207213249 | Ground Water | GeoSmart Energy | YT048*A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | No
5505441 | Ground Water | BARD | GTC36S2-A | HE37942D175B2505AW/HE37942D210B2505AW | 40500 | 24 | 34000 | 4.85 | 3.375 | No
5612204 | Ground Water | GeoSmart Energy | VI048**1*1 |  | 49000 | 31.7 | 55000 | 4.3 | 4.0833 | No
203466716 | Ground Water | 5 SERIES | NDV/NDH049J1*(1,2,4) |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
203470605 | Ground Water | 5 SERIES | NSV/NSH048J1*(0,3) |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
203470607 | Ground Water | 5 SERIES | NSV/NSH048J1*(1,2,4) |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
203490410 | Ground Water | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 54100 | 24.5 | 47200 | 4.6 | 4.5083 | No
203490414 | Ground Water | GeoSmart Energy | GS048**1*(0,3)*J |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
203490416 | Ground Water | GeoSmart Energy | GS048**1*(1,2,4)*J |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
203494005 | Ground Water | GEOSTAR | 101/102J048**1*(1,2,4) |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
3920503 | Ground Water | AQUARIUS | EP070-1HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
3920504 | Ground Water | AQUARIUS | EP070-3HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
3920505 | Ground Water | AQUARIUS | EP070-4HZ/VT |  | 71400 | 22.4 | 71400 | 5 | 5.95 | No
202391452 | Ground Water | CARRIER | 50PSH012**C4/DA |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
202391453 | Ground Water | CARRIER | 50PSV012**N0/BA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391454 | Ground Water | CARRIER | 50PSV012**N4/DA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391455 | Ground Water | CARRIER | 50PSH012**N0/BA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202391456 | Ground Water | CARRIER | 50PSH012**N4/DA |  | 14200 | 22.7 | 12000 | 4.1 | 1.1833 | No
202443455 | Ground Water | GeoSmart Energy | GS042**1*(0,3)*J |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
3919846 | Ground Water | AQUARIUS | EP007-2HZ/VT |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
3919847 | Ground Water | AQUARIUS | EP007-1HZ/VT |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
214855096 | Ground Water | WHALEN | CASH*060AD**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855097 | Ground Water | WHALEN | CASH*060AJ**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855098 | Ground Water | WHALEN | CASH*060AM**B**(D,E) |  | 64000 | 22 | 60000 | 4.1 | 5.3333 | No
214855099 | Ground Water | WHALEN | CASV*054AB**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855100 | Ground Water | WHALEN | CASV*054AD**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855101 | Ground Water | WHALEN | CASV*054AJ**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
214855102 | Ground Water | WHALEN | CASV*054AM**B**(D,E) |  | 60000 | 22 | 42000 | 4.1 | 5 | No
6945298 | Ground Water | BARD | GTC48S2-A | HE49948D210B2705AW | 54500 | 23.5 | 48000 | 4.55 | 4.5417 | No
205993170 | Ground Water | HYDRON MODULE | HBT072 | HAD072 | 70700 | 21.1 | 70500 | 4.1 | 5.8917 | No
205993172 | Ground Water | TETCO | TBT072 | TAD072 | 70700 | 21.1 | 70500 | 4.1 | 5.8917 | No
205993174 | Ground Water | GEOCOMFORT | GBT072*2 | GAD072 | 70700 | 21.1 | 70500 | 4.1 | 5.8917 | No
205993176 | Ground Water | HYDRON MODULE | HBT072*2 | HAD072 | 70700 | 21.1 | 70500 | 4.1 | 5.8917 | No
10443595 | Ground Water | TETCO | TBT024 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10443596 | Ground Water | GEOCOMFORT | GBT024*2 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10443597 | Ground Water | HYDRON MODULE | HBT024*2 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10443598 | Ground Water | TETCO | TBT024*2 | MPD024 | 26800 | 22.7 | 23000 | 4.2 | 2.2333 | No
10445242 | Ground Water | WaterFurnace | SDV049H1*(1,2) |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | No
10447649 | Ground Water | RHEEM | RPVS/EC025 | RCFL-HM2417 | 25200 | 22.4 | 22300 | 4.5 | 2.1 | Yes
5296247 | Ground Water | TRANE | EXVF0241 |  | 26700 | 25.2 | 24800 | 4.7 | 2.225 | No
5296248 | Ground Water | TRANE | EXVF0242 |  | 26700 | 25.2 | 24800 | 4.7 | 2.225 | No
5296249 | Ground Water | TRANE | EXVF0247 |  | 26700 | 25.2 | 24800 | 4.7 | 2.225 | No
205993149 | Ground Water | GEOCOMFORT | GBT060 | GED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
205993150 | Ground Water | HYDRON MODULE | HBT060 | HED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
205993151 | Ground Water | TETCO | TBT060 | TED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
205993152 | Ground Water | GEOCOMFORT | GBT060*2 | GED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
205993153 | Ground Water | HYDRON MODULE | HBT060*2 | HED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
205993154 | Ground Water | TETCO | TBT060*2 | TED060 | 63600 | 21.9 | 60200 | 4.5 | 5.3 | No
205993155 | Ground Water | GEOCOMFORT | GBT024 | GED024 | 28800 | 25.3 | 24400 | 4.8 | 2.4 | No
10443504 | Ground Water | TETCO | TBS018*2 | ACD024 | 21700 | 25.5 | 18500 | 4.5 | 1.8083 | No
10443509 | Ground Water | GEOCOMFORT | GBS018 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10443510 | Ground Water | HYDRON MODULE | HBS018 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10443511 | Ground Water | TETCO | TBS018 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10443512 | Ground Water | GEOCOMFORT | GBS018*2 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10443513 | Ground Water | HYDRON MODULE | HBS018*2 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
10443514 | Ground Water | TETCO | TBS018*2 | MPD024 | 22000 | 25.3 | 18500 | 4.5 | 1.8333 | No
5295950 | Ground Water | TRANE | EXHF0301 |  | 32200 | 24.3 | 28000 | 4.6 | 2.6833 | No
5295951 | Ground Water | TRANE | EXHF0302 |  | 32200 | 24.3 | 28000 | 4.6 | 2.6833 | No
5295952 | Ground Water | TRANE | EXHF0307 |  | 32200 | 24.3 | 28000 | 4.6 | 2.6833 | No
5295953 | Ground Water | TRANE | EXHF0361 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
5295954 | Ground Water | TRANE | EXHF0362 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
5295955 | Ground Water | TRANE | EXHF0367 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
5295956 | Ground Water | TRANE | EXHF0363 |  | 39700 | 25.8 | 35500 | 4.8 | 3.3083 | No
10268245 | Ground Water | HYDRON MODULE | HBT048 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268246 | Ground Water | TETCO | TBT048 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268247 | Ground Water | GEOCOMFORT | GBT048*2 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268248 | Ground Water | HYDRON MODULE | HBT048*2 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268249 | Ground Water | TETCO | TBT048*2 | ACD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268250 | Ground Water | GEOCOMFORT | GBT048 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
10268251 | Ground Water | HYDRON MODULE | HBT048 | MCD060 | 54100 | 24.9 | 46500 | 4.6 | 4.5083 | No
3919848 | Ground Water | AQUARIUS | EP009-1HZ/VT |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
3919850 | Ground Water | AQUARIUS | EP009-2HZ/VT |  | 10500 | 24.35 | 9000 | 4.5 | 0.875 | No
3919853 | Ground Water | AQUARIUS | EP012-1HZ/VT |  | 14200 | 22.7 | 12000 | 4.3 | 1.1833 | No
3919854 | Ground Water | AQUARIUS | EP015-1HZ/VT |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
3919855 | Ground Water | AQUARIUS | EP015-2HZ/VT |  | 17000 | 27.25 | 13000 | 4.28 | 1.4167 | No
3919884 | Ground Water | AQUARIUS | EP024-1HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
3919931 | Ground Water | AQUARIUS | EP024-2HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
8105933 | Ground Water | TRANE | DXHF0703 |  | 74100 | 22.1 | 72700 | 4.5 | 6.175 | No
8105934 | Ground Water | TRANE | DXHF0704 |  | 74100 | 22.1 | 72700 | 4.5 | 6.175 | No
8105935 | Ground Water | TRANE | DXHF0708 |  | 74100 | 22.1 | 72700 | 4.5 | 6.175 | No
8105950 | Ground Water | TRANE | DXVF0241 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
8105955 | Ground Water | TRANE | DXVF0242 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
8105956 | Ground Water | TRANE | DXVF0243 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
8105960 | Ground Water | TRANE | DXVF0244 |  | 28000 | 25.8 | 25400 | 4.9 | 2.3333 | No
202330427 | Ground Water | AAON, Inc. | WV-048-A-H-DCAC-C0-10-200-A |  | 53300 | 21.7 | 50300 | 4.4 | 4.4417 | No
202330428 | Ground Water | AAON, Inc. | WV-048-A-H-DCAC-C0-10-D00-A |  | 54500 | 22 | 54200 | 4.8 | 4.5417 | No
202330429 | Ground Water | AAON, Inc. | WV-048-3-H-DCAC-C0-10-200-A |  | 53300 | 21.7 | 50300 | 4.4 | 4.4417 | No
202330431 | Ground Water | AAON, Inc. | WV-060-A-H-DCAC-C0-10-D00-A |  | 64000 | 21.7 | 65000 | 4.9 | 5.3333 | No
202330466 | Ground Water | AAON, Inc. | RN-006-2-0-ACAY-C0-10-000-A |  | 67300 | 22.7 | 58200 | 4.2 | 5.6083 | No
202330467 | Ground Water | AAON, Inc. | RN-006-3-0-ACAY-C0-10-000-A |  | 67300 | 22.7 | 58200 | 4.2 | 5.6083 | No
202330468 | Ground Water | AAON, Inc. | RN-006-4-0-ACAY-C0-10-000-A |  | 67300 | 22.7 | 58200 | 4.2 | 5.6083 | No
207334461 | Ground Water | WaterFurnace | NDP072H1*1 |  | 77400 | 21.5 | 70600 | 4.3 | 6.45 | No
207334462 | Ground Water | WaterFurnace | NDP064H1*1 |  | 67500 | 23.1 | 58200 | 4.5 | 5.625 | No
207335405 | Ground Water | GeoSmart Energy | GS022**1*(0,3)*J |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
207337519 | Ground Water | GEOSTAR | 103H060**1 | SAH060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
207337520 | Ground Water | GEOSTAR | 103H060**1 | SRAA060* | 61700 | 23.6 | 54500 | 4.3 | 5.1417 | No
207200572 | Ground Water | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
207200573 | Ground Water | GeoSmart Energy | GS048**1*(0,3)*J |  | 48900 | 22.3 | 44700 | 4.2 | 4.075 | No
207200574 | Ground Water | GeoSmart Energy | GS048**1*(1,2,4)*J |  | 50300 | 25.9 | 44700 | 4.7 | 4.1917 | No
207200617 | Ground Water | GeoSmart Energy | VI036**1*(1,2)* |  | 38000 | 31.2 | 41700 | 4.5 | 3.1667 | No
207200622 | Ground Water | GeoSmart Energy | QT049**1*(1,2)* |  | 50200 | 23.1 | 46900 | 4.5 | 4.1833 | No
207200563 | Ground Water | GeoSmart Energy | GS030**1*(0,3)*H |  | 30800 | 27.1 | 26000 | 4.7 | 2.5667 | No
207200564 | Ground Water | GeoSmart Energy | GS030**1*(1,4)*H |  | 31200 | 29.5 | 26000 | 4.8 | 2.6 | No
207200567 | Ground Water | GeoSmart Energy | GS070**1*(1,4)*H |  | 75000 | 22.9 | 68000 | 4.4 | 6.25 | No
207200569 | Ground Water | GeoSmart Energy | GS042**1*(0,3)*J |  | 42300 | 23.3 | 36000 | 4.3 | 3.525 | No
10268272 | Ground Water | HYDRON MODULE | HBT060*2 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268273 | Ground Water | TETCO | TBT060*2 | ACD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268274 | Ground Water | GEOCOMFORT | GBT060 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268275 | Ground Water | HYDRON MODULE | HBT060 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268276 | Ground Water | TETCO | TBT060 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268277 | Ground Water | GEOCOMFORT | GBT060*2 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
10268278 | Ground Water | HYDRON MODULE | HBT060*2 | MCD060 | 65100 | 22.5 | 56600 | 4.3 | 5.425 | No
203113887 | Ground Water | GEOSTAR | 101/102J042**1*(1,2,4)***** |  | 43900 | 28.1 | 36100 | 4.9 | 3.6583 | No
202350522 | Ground Water | AAON, Inc. | WV-042-1-H-DCAC-C0-10-200-A |  | 48000 | 22.7 | 41300 | 4.4 | 4 | No
202350523 | Ground Water | AAON, Inc. | WV-042-2-H-DCAC-C0-10-200-A |  | 48000 | 22.7 | 41300 | 4.4 | 4 | No
202350524 | Ground Water | AAON, Inc. | WV-048-1-H-DCAC-C0-10-200-A |  | 53300 | 21.7 | 50300 | 4.4 | 4.4417 | No
202350526 | Ground Water | AAON, Inc. | WV-048-2-H-DCAC-C0-10-200-A |  | 53300 | 21.7 | 50300 | 4.4 | 4.4417 | No
7493299 | Ground Water | GeoSmart Energy | YT048*A |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | No
7493316 | Ground Water | GEOSTAR | 12(1,2)A048 |  | 52300 | 21.8 | 45000 | 4.3 | 4.3583 | No
7167332 | Ground Water | CARRIER | 50PSH/V007***4/DA |  | 8400 | 25.1 | 6900 | 4.7 | 0.7 | No
6966789 | Ground Water | TRANE | EXVF0127 |  | 14200 | 25.37 | 12400 | 4.5 | 1.1833 | No
6966837 | Ground Water | TRANE | EXVF0151 |  | 17100 | 24.05 | 15300 | 4.3 | 1.425 | No
6966860 | Ground Water | TRANE | EXVF0152 |  | 17100 | 24.05 | 15300 | 4.3 | 1.425 | No
6966875 | Ground Water | TRANE | EXVF0157 |  | 17100 | 24.05 | 15300 | 4.3 | 1.425 | No
7076986 | Ground Water | AQUARIUS | EP024-3HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
7076987 | Ground Water | AQUARIUS | EP024-4HZ/VT |  | 28400 | 27.35 | 23700 | 4.5 | 2.3667 | No
207312264 | Ground Water | WaterFurnace | NSV/NSH022J1*(0,3) |  | 20100 | 25.5 | 19400 | 4.8 | 1.675 | No
207324061 | Ground Water | WaterFurnace | NVZ033A1 | SVH033 | 37000 | 29.2 | 40700 | 4.5 | 3.0833 | No
207324062 | Ground Water | WaterFurnace | NVZ042A1 | SVH042 | 46200 | 28.2 | 54100 | 4.2 | 3.85 | No
207334458 | Ground Water | WaterFurnace | NDP026H1*1 |  | 26200 | 22.5 | 23800 | 4.7 | 2.1833 | No
207334459 | Ground Water | WaterFurnace | NDP038H1*(1,2) |  | 40000 | 24.4 | 34700 | 4.8 | 3.3333 | No
207334460 | Ground Water | WaterFurnace | NDP049H1*1 |  | 53800 | 24.3 | 46900 | 4.5 | 4.4833 | No
205448524 | Ground Water | 7 SERIES INDOOR SPLITS | NVZ033A1 | SVH033 | 37000 | 29.2 | 40700 | 4.5 | 3.0833 | No
205448525 | Ground Water | 7 SERIES INDOOR SPLITS | NVZ042A1 | SVH042 | 46200 | 28.2 | 54100 | 4.2 | 3.85 | No
205993114 | Ground Water | GEOCOMFORT | GBS018 | GAD018 | 24300 | 31.6 | 18700 | 5 | 2.025 | No
205993115 | Ground Water | HYDRON MODULE | HBS018 | HED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
205993116 | Ground Water | HYDRON MODULE | HBS018 | HAD018 | 24300 | 31.6 | 18700 | 5 | 2.025 | No
205993117 | Ground Water | TETCO | TBS018 | TED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
205993118 | Ground Water | TETCO | TBS018 | TAD018 | 24300 | 31.6 | 18700 | 5 | 2.025 | No
205993119 | Ground Water | GEOCOMFORT | GBS018*2 | GED018 | 24200 | 30.5 | 18600 | 5 | 2.0167 | No
205993120 | Ground Water | GEOCOMFORT | GBS018*2 | GAD018 | 24300 | 31.6 | 18700 | 5 | 2.025 | No
5296264 | Ground Water | TRANE | EXVF0428 |  | 45400 | 23.4 | 41200 | 4.6 | 3.7833 | No
5296265 | Ground Water | TRANE | EXVF0481 |  | 50300 | 23.58 | 46400 | 4.76 | 4.1917 | No
5296266 | Ground Water | TRANE | EXVF0482 |  | 50300 | 23.58 | 46400 | 4.76 | 4.1917 | No
5296267 | Ground Water | TRANE | EXVF0483 |  | 50300 | 23.58 | 46400 | 4.76 | 4.1917 | No
5296268 | Ground Water | TRANE | EXVF0484 |  | 50300 | 23.58 | 46400 | 4.76 | 4.1917 | No
10581118 | Ground Water | GEOSTAR | 107H026**1*1 |  | 26200 | 22.5 | 23800 | 4.7 | 2.1833 | No
10581119 | Ground Water | GEOSTAR | 107H038**1*(1,2) |  | 40000 | 24.4 | 34700 | 4.8 | 3.3333 | No
10581120 | Ground Water | GEOSTAR | 107H049**1*1 |  | 53800 | 24.3 | 46900 | 4.5 | 4.4833 | No
10581122 | Ground Water | GEOSTAR | 107H072**1*1 |  | 77400 | 21.5 | 70600 | 4.3 | 6.45 | No

## Commercial Ground Loop HP
AHRI Certified Reference Number | Equipment Type | Outdoor Unit Brand Name | Outdoor Unit Model Number | Indoor Unit Model Number | Full Load Cooling Capacity (Btuh) | EER | Full Load Heating Capacity (Btuh) | COP | Tonnage
215224539 | Ground Loop | FHP | CF024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224540 | Ground Loop | FHP | CF024-3VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224541 | Ground Loop | FHP | CF024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224542 | Ground Loop | FHP | CF024-3VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
216057517 | Ground Loop | GEOCOMFORT | GYT072* |  | 70300 | 17.1 | 57800 | 3.8 | 5.8583
216128491 | Ground Loop | GEOSTAR | G5TV036BD1**2 |  | 38000 | 20.1 | 29300 | 4.3 | 3.1667
216128493 | Ground Loop | GEOSTAR | G5TV048BD1**2 |  | 49100 | 18.5 | 38400 | 4.1 | 4.0917
216128495 | Ground Loop | GEOSTAR | G5TV060BD1**2 |  | 63700 | 17.9 | 47300 | 4 | 5.3083
216128497 | Ground Loop | GEOSTAR | G5TV072BD1**2 |  | 71500 | 17.8 | 56100 | 3.9 | 5.9583
216411469 | Ground Loop | ClimateMaster | SJ/PN024A | SAN024A | 23900 | 19 | 17900 | 4 | 1.9917
216411470 | Ground Loop | ClimateMaster | SJ/PN036A | SAN036A | 38300 | 18.4 | 26900 | 4 | 3.1917
216411471 | Ground Loop | ClimateMaster | SJ/PN048A | SAN048A | 49000 | 18.1 | 35500 | 3.7 | 4.0833
216411472 | Ground Loop | ClimateMaster | SJ/PN060A | SAN060A | 60200 | 17.6 | 45000 | 3.7 | 5.0167
216419856 | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333
216419857 | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15
216419860 | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417
216419863 | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333
216419880 | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667
216419883 | Ground Loop | Whalen | WC(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167
216419898 | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333
216419899 | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15
216419902 | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417
216419904 | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333
4219425 | Ground Loop | NORDIC | R55HACW-P-1T-*-SDE** |  | 45400 | 17 | 35600 | 3.8 | 3.7833
4219430 | Ground Loop | NORDIC | RH55HACW-P-1T-*-SDE** |  | 44400 | 17 | 34700 | 3.6 | 3.7
4219434 | Ground Loop | NORDIC | TF55HACW-P-1T-*-SDE** |  | 45400 | 17.1 | 35400 | 3.8 | 3.7833
4219444 | Ground Loop | NORDIC | RS55HACW-P-1T-* | AH-55-P-1-***** | 45400 | 17 | 35600 | 3.8 | 3.7833
4230311 | Ground Loop | DAIKIN | WCCW4015*E*01* |  | 16700 | 18.7 | 11400 | 3.7 | 1.3917
4230745 | Ground Loop | DAIKIN | WCCW4019*E*01* |  | 22600 | 17.3 | 14700 | 3.6 | 1.8833
4230747 | Ground Loop | DAIKIN | WCCW4019*J*01* |  | 22600 | 17.3 | 14700 | 3.6 | 1.8833
4233405 | Ground Loop | DAIKIN | WVFW1042*E***01 |  | 45400 | 17 | 35100 | 3.6 | 3.7833
4233406 | Ground Loop | DAIKIN | WVFW1042*F***01 |  | 45400 | 17 | 35100 | 3.6 | 3.7833
4233407 | Ground Loop | DAIKIN | WVFW1042*K***01 |  | 45400 | 17 | 35100 | 3.6 | 3.7833
4233408 | Ground Loop | DAIKIN | WVFW1042*L***01 |  | 45400 | 17 | 35100 | 3.6 | 3.7833
206185652 | Ground Loop | DAIKIN | WGCH048K1*G/J*T |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917
206185653 | Ground Loop | DAIKIN | WGCH048K1*G/J*C |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917
9100357 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**0*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
9100358 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**0*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
9100359 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**2*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
9100361 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**3*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
9100362 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**3*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
9100364 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**4*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
9100365 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH036**4*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
9100367 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**0*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
9100368 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**0*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
9100370 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**3*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
9100371 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**3*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
9100373 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**4*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
9100374 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH042**4*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
9100377 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**0*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
9100378 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**0*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
9100380 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**3*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
9100381 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**3*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
9100383 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**4*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
9100384 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH048**4*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
9100390 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**0*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
9100391 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**0*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
9100393 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**3*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
9100394 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**3*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
9100396 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**4*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
9100397 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH060**4*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
9100400 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**0*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
9100401 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**0*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
9100403 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**3*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
9100404 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**3*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
9100417 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**4*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
9100431 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH070**4*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
215837601 | Ground Loop | DAIKIN | WSCH048F3*G/J*T |  | 49200 | 17.36 | 37500 | 3.6 | 4.1
215837603 | Ground Loop | DAIKIN | WSCH048K3*G/J*T |  | 49200 | 17.36 | 37500 | 3.6 | 4.1
215837604 | Ground Loop | DAIKIN | WSCH048L3*G/J*T |  | 49200 | 17.36 | 37500 | 3.6 | 4.1
215837610 | Ground Loop | DAIKIN | WSCH048F3*G/J*C |  | 49200 | 17.36 | 37500 | 3.6 | 4.1
215837611 | Ground Loop | DAIKIN | WSCH048K3*G/J*C |  | 49200 | 17.36 | 37500 | 3.6 | 4.1
215837613 | Ground Loop | DAIKIN | WSCH048L3*G/J*C |  | 49200 | 17.36 | 37500 | 3.6 | 4.1
217897421 | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333
217897422 | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333
217897449 | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667
202146983 | Ground Loop | HYDRON MODULE | HZS030*2***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167
202146984 | Ground Loop | TETCO | TZS030 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475
202146985 | Ground Loop | TETCO | TZS030*2 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475
202146986 | Ground Loop | TETCO | TZS030*3 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475
202146987 | Ground Loop | TETCO | TZS030*4 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475
202146988 | Ground Loop | TETCO | TZS030*A |  | 29700 | 17.7 | 22900 | 3.6 | 2.475
202146989 | Ground Loop | TETCO | TZS030*****1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167
202146990 | Ground Loop | TETCO | TZS030*2***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167
202146991 | Ground Loop | GEOCOMFORT | GZS036 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05
202146992 | Ground Loop | GEOCOMFORT | GZS036*2 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05
202146993 | Ground Loop | GEOCOMFORT | GZS036*3 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05
202146994 | Ground Loop | GEOCOMFORT | GZS036*4 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05
202146995 | Ground Loop | GEOCOMFORT | GZS036*A |  | 36600 | 17.9 | 28300 | 3.7 | 3.05
202146996 | Ground Loop | GEOCOMFORT | GZS036*****1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1
202146997 | Ground Loop | GEOCOMFORT | GZS036*2***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1
202146998 | Ground Loop | GEOCOMFORT | GZS036*3***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1
202146999 | Ground Loop | GEOCOMFORT | GZS036*A***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1
202147000 | Ground Loop | HYDRON MODULE | HZS036 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05
202147001 | Ground Loop | HYDRON MODULE | HZS036*2 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05
202147002 | Ground Loop | HYDRON MODULE | HZS036*3 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05
202147003 | Ground Loop | HYDRON MODULE | HZS036*4 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05
202147004 | Ground Loop | HYDRON MODULE | HZS036*A |  | 36600 | 17.9 | 28300 | 3.7 | 3.05
202147005 | Ground Loop | HYDRON MODULE | HZS036*****1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1
202147006 | Ground Loop | HYDRON MODULE | HZS036*2***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1
202147007 | Ground Loop | HYDRON MODULE | HZS036*3***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1
202147008 | Ground Loop | HYDRON MODULE | HZS036*A***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1
202147009 | Ground Loop | TETCO | TZS036 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05
214823486 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048BD1**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
214823487 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060BD1**2 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
214823488 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072BD1**2 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
214837733 | Ground Loop | BOSCH | EC072-1VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167
214837734 | Ground Loop | BOSCH | EC072-3VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167
214837735 | Ground Loop | BOSCH | EC072-4VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167
214837736 | Ground Loop | BOSCH | EC096-1VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667
214837737 | Ground Loop | BOSCH | EC096-3VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667
214837738 | Ground Loop | BOSCH | EC096-4VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667
214837742 | Ground Loop | CARRIER | 50H/VQP072***3C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167
214837743 | Ground Loop | CARRIER | 50H/VQP072***5C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167
214837744 | Ground Loop | CARRIER | 50H/VQP072***6C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167
214837745 | Ground Loop | CARRIER | 50H/VQP096***3C |  | 104000 | 18.9 | 82000 | 4 | 8.6667
214837746 | Ground Loop | CARRIER | 50H/VQP096***5C |  | 104000 | 18.9 | 82000 | 4 | 8.6667
214837747 | Ground Loop | CARRIER | 50H/VQP096***6C |  | 104000 | 18.9 | 82000 | 4 | 8.6667
216621310 | Ground Loop | GEOSTAR | G5A(V/H)012*R0**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833
216621311 | Ground Loop | GEOSTAR | G5A(V/H)015*R0**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
216621312 | Ground Loop | GEOSTAR | G5A(V/H)018*R0**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
216621313 | Ground Loop | GEOSTAR | G5A(V/H)024*S0**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216621314 | Ground Loop | GEOSTAR | G5A(V/H)030*S0**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216621315 | Ground Loop | GEOSTAR | G5A(V/H)036*S0**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216621316 | Ground Loop | GEOSTAR | G5A(V/H)042*S0**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216621317 | Ground Loop | GEOSTAR | G5A(V/H)048*S0**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216621318 | Ground Loop | GEOSTAR | G5A(V/H)060*S0**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216621319 | Ground Loop | GEOSTAR | G5A(V/H)072*S0**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216621323 | Ground Loop | GEOSTAR | G5A(V/H)018*D0**1 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583
216621324 | Ground Loop | GEOSTAR | G5A(V/H)018*D0**4 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583
216621325 | Ground Loop | GEOSTAR | G5A(V/H)024*D0**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216621326 | Ground Loop | GEOSTAR | G5A(V/H)024*D2**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216621327 | Ground Loop | GEOSTAR | G5A(V/H)024*D3**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216621328 | Ground Loop | GEOSTAR | G5A(V/H)024*D4**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216621329 | Ground Loop | GEOSTAR | G5A(V/H)024*D0**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216621330 | Ground Loop | GEOSTAR | G5A(V/H)024*D2**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216621331 | Ground Loop | GEOSTAR | G5A(V/H)024*D3**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216621332 | Ground Loop | GEOSTAR | G5A(V/H)024*D4**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216621333 | Ground Loop | GEOSTAR | G5A(V/H)030*D0**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216621334 | Ground Loop | GEOSTAR | G5A(V/H)030*D3**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216621335 | Ground Loop | GEOSTAR | G5A(V/H)030*D0**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216621336 | Ground Loop | GEOSTAR | G5A(V/H)030*D3**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216621337 | Ground Loop | GEOSTAR | G5A(V/H)036*D0**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216621338 | Ground Loop | GEOSTAR | G5A(V/H)036*D3**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
217754426 | Ground Loop | DAIKIN | WSSV024F1*H*T |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167
217754427 | Ground Loop | DAIKIN | WSSV024K1*H*T |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167
217754429 | Ground Loop | DAIKIN | WSSV024F1*H*C |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167
217754430 | Ground Loop | DAIKIN | WSSV024K1*H*C |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167
217754432 | Ground Loop | DAIKIN | WSSV030F1*H*T |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167
217754433 | Ground Loop | DAIKIN | WSSV030K1*H*T |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167
217754435 | Ground Loop | DAIKIN | WSSV030F1*H*C |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167
217754436 | Ground Loop | DAIKIN | WSSV030K1*H*C |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167
217754438 | Ground Loop | DAIKIN | WSSV036F1*H*T |  | 40500 | 21.18 | 27600 | 3.83 | 3.375
217754439 | Ground Loop | DAIKIN | WSSV036K1*H*T |  | 40500 | 21.09 | 27600 | 3.83 | 3.375
217754441 | Ground Loop | DAIKIN | WSSV036F1*H*C |  | 40500 | 21.18 | 27600 | 3.83 | 3.375
217754442 | Ground Loop | DAIKIN | WSSV036K1*H*C |  | 40500 | 21.09 | 27600 | 3.83 | 3.375
217754444 | Ground Loop | DAIKIN | WSSV042F1*H*T |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587
217754445 | Ground Loop | DAIKIN | WSSV042K1*H*T |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587
217754447 | Ground Loop | DAIKIN | WSSV042F1*H*C |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587
217754448 | Ground Loop | DAIKIN | WSSV042K1*H*C |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587
9009366 | Ground Loop | FHP | ES025-2CF/HZ/VT*-*****A |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917
9011292 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**0*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
9032648 | Ground Loop | HYDROTECH | HRCX18*-6 |  | 18000 | 17.1 | 13000 | 3.6 | 1.5
9033424 | Ground Loop | HYDROTECH | HRCX09*-6 |  | 10000 | 19 | 6800 | 3.6 | 0.83333
9033758 | Ground Loop | HYDROTECH | HRCX24*-6 |  | 24000 | 19 | 17000 | 3.6 | 2
9033759 | Ground Loop | HYDROTECH | HRCX12*-6 |  | 11800 | 18 | 8000 | 3.6 | 0.98333
9035993 | Ground Loop | GEOCOMFORT | GZT024******B |  | 26800 | 19.8 | 18100 | 4 | 2.2333
9035994 | Ground Loop | HYDRON MODULE | HZT024******B |  | 26800 | 19.8 | 18100 | 4 | 2.2333
9035995 | Ground Loop | TETCO | TZT024******B |  | 26800 | 19.8 | 18100 | 4 | 2.2333
9035996 | Ground Loop | GEOCOMFORT | GZT024*2****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333
9035997 | Ground Loop | HYDRON MODULE | HZT024*2****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333
9035998 | Ground Loop | TETCO | TZT024*2****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333
9035999 | Ground Loop | GEOCOMFORT | GZT024*3****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333
9036000 | Ground Loop | HYDRON MODULE | HZT024*3****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333
9036001 | Ground Loop | TETCO | TZT024*3****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333
9036002 | Ground Loop | GEOCOMFORT | GZT024*A****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333
9036003 | Ground Loop | HYDRON MODULE | HZT024*A****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333
9036004 | Ground Loop | TETCO | TZT024*A****B |  | 26800 | 19.8 | 18100 | 4 | 2.2333
9036975 | Ground Loop | GEOCOMFORT | GZT036******B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833
9036998 | Ground Loop | HYDRON MODULE | HZT036******B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833
9037017 | Ground Loop | TETCO | TZT036******B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833
9037062 | Ground Loop | GEOCOMFORT | GZT036*2****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833
9037081 | Ground Loop | HYDRON MODULE | HZT036*2****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833
9037097 | Ground Loop | TETCO | TZT036*2****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833
9037137 | Ground Loop | GEOCOMFORT | GZT036*3****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833
9037158 | Ground Loop | HYDRON MODULE | HZT036*3****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833
9037175 | Ground Loop | TETCO | TZT036*3****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833
9037215 | Ground Loop | GEOCOMFORT | GZT036*A****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833
9037240 | Ground Loop | HYDRON MODULE | HZT036*A****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833
9037275 | Ground Loop | TETCO | TZT036*A****B |  | 38200 | 19.9 | 27600 | 4.1 | 3.1833
9038310 | Ground Loop | GEOCOMFORT | GZT048******B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15
9038311 | Ground Loop | HYDRON MODULE | HZT048******B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15
9038312 | Ground Loop | TETCO | TZT048******B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15
9038313 | Ground Loop | GEOCOMFORT | GZT048*2****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15
9038314 | Ground Loop | HYDRON MODULE | HZT048*2****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15
9038315 | Ground Loop | TETCO | TZT048*2****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15
208450079 | Ground Loop | AE Air | HRCX18*-6 |  | 18000 | 17.1 | 13000 | 3.6 | 1.5
208450080 | Ground Loop | AE Air | HRCX09*-6 |  | 10000 | 19 | 6800 | 3.6 | 0.83333
208450081 | Ground Loop | AE Air | HRCX24*-6 |  | 24000 | 19 | 17000 | 3.6 | 2
208450082 | Ground Loop | AE Air | HRCX12*-6 |  | 11800 | 18 | 8000 | 3.6 | 0.98333
208450083 | Ground Loop | AE Air | HRCX30*-6 |  | 28000 | 18 | 20000 | 3.6 | 2.3333
208450084 | Ground Loop | AE Air | HRCX36*-6 |  | 34100 | 17.1 | 25000 | 3.6 | 2.8417
208556796 | Ground Loop | GEOCOMFORT | GRT036 | EAD036 | 37500 | 18.5 | 28300 | 4.1 | 3.125
208556798 | Ground Loop | HYDRON MODULE | HRT036 | EAD036 | 37500 | 18.5 | 28300 | 4.1 | 3.125
208556799 | Ground Loop | TETCO | TRT036 | EAD036 | 37500 | 18.5 | 28300 | 4.1 | 3.125
208556801 | Ground Loop | GEOCOMFORT | GRT048 | EAD048 | 49800 | 17.9 | 38500 | 3.7 | 4.15
208556804 | Ground Loop | HYDRON MODULE | HRT048 | EAD048 | 49800 | 17.9 | 38500 | 3.7 | 4.15
208556806 | Ground Loop | TETCO | TRT048 | EAD048 | 49800 | 17.9 | 38500 | 3.7 | 4.15
208556808 | Ground Loop | GEOCOMFORT | GRT060 | EAD060 | 60500 | 17.4 | 46200 | 3.6 | 5.0417
208556810 | Ground Loop | HYDRON MODULE | HRT060 | EAD060 | 60500 | 17.4 | 46200 | 3.6 | 5.0417
208556812 | Ground Loop | TETCO | TRT060 | EAD060 | 60500 | 17.4 | 46200 | 3.6 | 5.0417
208556818 | Ground Loop | GEOCOMFORT | GRT036 | EED036 | 37700 | 17.9 | 28400 | 4.1 | 3.1417
215400210 | Ground Loop | DAIKIN | WSSV042E1*H*C |  | 44800 | 21.3 | 29000 | 3.92 | 3.7333
215400211 | Ground Loop | DAIKIN | WSSV042F3*H*C |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587
215400214 | Ground Loop | DAIKIN | WSSV048E1*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35
215400215 | Ground Loop | DAIKIN | WSSV048F3*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35
215400218 | Ground Loop | DAIKIN | WSSV048E1*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35
215400219 | Ground Loop | DAIKIN | WSSV048F3*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35
215402552 | Ground Loop | DAIKIN | WSSV024E1*H*T |  | 25400 | 21.11 | 15700 | 3.7 | 2.1167
215402553 | Ground Loop | DAIKIN | WSSV024F3*H*T |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167
215402556 | Ground Loop | DAIKIN | WSSV024E1*H*C |  | 25400 | 21.11 | 15700 | 3.7 | 2.1167
215402557 | Ground Loop | DAIKIN | WSSV024F3*H*C |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167
215402560 | Ground Loop | DAIKIN | WSSV030E1*H*T |  | 30200 | 21.8 | 20700 | 3.83 | 2.5167
215402561 | Ground Loop | DAIKIN | WSSV030F3*H*T |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167
215402564 | Ground Loop | DAIKIN | WSSV030E1*H*C |  | 30200 | 21.8 | 20700 | 3.83 | 2.5167
215402565 | Ground Loop | DAIKIN | WSSV030F3*H*C |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167
215402568 | Ground Loop | DAIKIN | WSSV036E1*H*T |  | 40500 | 21.9 | 27600 | 3.84 | 3.375
9910450 | Ground Loop | HYDRON MODULE | HZS018*****1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333
9910451 | Ground Loop | TETCO | TZS018*****1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333
9910452 | Ground Loop | GEOCOMFORT | GZS018*A***1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333
9910453 | Ground Loop | HYDRON MODULE | HZS018*A***1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333
9910454 | Ground Loop | TETCO | TZS018*A***1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333
9910540 | Ground Loop | GEOCOMFORT | GZS018******B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083
9910541 | Ground Loop | HYDRON MODULE | HZS018******B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083
9910542 | Ground Loop | TETCO | TZS018******B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083
9910543 | Ground Loop | GEOCOMFORT | GZS018*A****B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083
9910544 | Ground Loop | HYDRON MODULE | HZS018*A****B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083
9910545 | Ground Loop | TETCO | TZS018*A****B |  | 20500 | 18.2 | 14400 | 3.6 | 1.7083
9910548 | Ground Loop | GEOCOMFORT | GZS024*****1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175
9910549 | Ground Loop | HYDRON MODULE | HZS024*****1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175
9910550 | Ground Loop | TETCO | TZS024*****1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175
9910551 | Ground Loop | GEOCOMFORT | GZS024*2***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175
9910552 | Ground Loop | HYDRON MODULE | HZS024*2***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175
9910553 | Ground Loop | TETCO | TZS024*2***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175
9910554 | Ground Loop | GEOCOMFORT | GZS024*3***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175
9910555 | Ground Loop | HYDRON MODULE | HZS024*3***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175
9910556 | Ground Loop | TETCO | TZS024*3***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175
9910557 | Ground Loop | GEOCOMFORT | GZS024*A***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175
9910558 | Ground Loop | HYDRON MODULE | HZS024*A***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175
9910559 | Ground Loop | TETCO | TZS024*A***1B |  | 26100 | 21.5 | 18600 | 3.9 | 2.175
9910564 | Ground Loop | GEOCOMFORT | GZS024******B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1
9910565 | Ground Loop | HYDRON MODULE | HZS024******B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1
9910566 | Ground Loop | TETCO | TZS024******B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1
9910567 | Ground Loop | GEOCOMFORT | GZS024*2****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1
9910568 | Ground Loop | HYDRON MODULE | HZS024*2****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1
9910569 | Ground Loop | TETCO | TZS024*2****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1
9910570 | Ground Loop | GEOCOMFORT | GZS024*3****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1
9910571 | Ground Loop | HYDRON MODULE | HZS024*3****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1
9910572 | Ground Loop | TETCO | TZS024*3****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1
9910573 | Ground Loop | GEOCOMFORT | GZS024*4****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1
9910574 | Ground Loop | HYDRON MODULE | HZS024*4****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1
9910575 | Ground Loop | TETCO | TZS024*4****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1
9910576 | Ground Loop | GEOCOMFORT | GZS024*A****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1
9910577 | Ground Loop | HYDRON MODULE | HZS024*A****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1
9910578 | Ground Loop | TETCO | TZS024*A****B |  | 25200 | 18.7 | 18600 | 3.7 | 2.1
9910584 | Ground Loop | GEOCOMFORT | GZS030*****1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583
9910585 | Ground Loop | HYDRON MODULE | HZS030*****1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583
9910586 | Ground Loop | TETCO | TZS030*****1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583
9910587 | Ground Loop | GEOCOMFORT | GZS030*2***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583
9910588 | Ground Loop | HYDRON MODULE | HZS030*2***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583
9910589 | Ground Loop | TETCO | TZS030*2***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583
9910590 | Ground Loop | GEOCOMFORT | GZS030*3***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583
9910591 | Ground Loop | HYDRON MODULE | HZS030*3***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583
9910592 | Ground Loop | TETCO | TZS030*3***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583
9910593 | Ground Loop | GEOCOMFORT | GZS030*A***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583
9910594 | Ground Loop | HYDRON MODULE | HZS030*A***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583
9910595 | Ground Loop | TETCO | TZS030*A***1B |  | 30700 | 20.7 | 21500 | 4 | 2.5583
9910600 | Ground Loop | GEOCOMFORT | GZS030******B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525
9910601 | Ground Loop | HYDRON MODULE | HZS030******B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525
9910602 | Ground Loop | TETCO | TZS030******B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525
9910603 | Ground Loop | GEOCOMFORT | GZS030*2****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525
9910604 | Ground Loop | HYDRON MODULE | HZS030*2****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525
9910605 | Ground Loop | TETCO | TZS030*2****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525
215852876 | Ground Loop | DAIKIN | WSTV036E1*G/J*C |  | 39100 | 21.12 | 25600 | 3.68 | 3.2583
215852877 | Ground Loop | DAIKIN | WSTV036F3*G/J*C |  | 39100 | 20.7 | 25600 | 3.61 | 3.2583
215852880 | Ground Loop | DAIKIN | WSTV042E1*G/J*C |  | 44800 | 19.54 | 27600 | 3.74 | 3.7333
215852881 | Ground Loop | DAIKIN | WSTV042F3*G/J*C |  | 44800 | 19.15 | 27600 | 3.66 | 3.7333
215852886 | Ground Loop | DAIKIN | WSTV060E1*G/J*C |  | 63100 | 19.6 | 46800 | 4.1 | 5.2583
215852887 | Ground Loop | DAIKIN | WSTV060F3*G/J*C |  | 63100 | 19.21 | 46800 | 4.02 | 5.2583
215866226 | Ground Loop | ClimateMaster | SMS15A*L |  | 14800 | 17.5 | 11000 | 3.6 | 1.2333
217212057 | Ground Loop | FHP | CP024-4HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
217212059 | Ground Loop | FHP | CP024-4HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
217212060 | Ground Loop | FHP | CP024-4VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
217212061 | Ground Loop | FHP | CP024-4VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
217212062 | Ground Loop | FHP | CP036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25
217212064 | Ground Loop | FHP | CP036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083
217212065 | Ground Loop | FHP | CP036-2VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25
217212066 | Ground Loop | FHP | CP036-2VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083
217212067 | Ground Loop | FHP | CP036-3VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25
217212068 | Ground Loop | FHP | CP036-3VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083
217212070 | Ground Loop | FHP | CP036-4VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25
217212071 | Ground Loop | FHP | CP036-4VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083
217212072 | Ground Loop | FHP | CP048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25
217212073 | Ground Loop | FHP | CP048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083
217212074 | Ground Loop | FHP | CP048-3VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25
217212076 | Ground Loop | FHP | CP048-3VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083
217212077 | Ground Loop | FHP | CP048-4VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25
202667081 | Ground Loop | BOSCH-GEO | BP042-1VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
202679205 | Ground Loop | BOSCH-GEO | SM036-1CSC-*****B | SM036-1AH*-*****B | 37900 | 17.15 | 27400 | 3.8 | 3.1583
202679208 | Ground Loop | BOSCH | SM036-1CSC-*****B | SM036-1AH*-*****B | 37900 | 17.15 | 27400 | 3.8 | 3.1583
202729320 | Ground Loop | HEIL | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
202729321 | Ground Loop | ARCOAIRE | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
202729322 | Ground Loop | KEEPRITE | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
202729323 | Ground Loop | TEMPSTAR | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
202729324 | Ground Loop | COMFORTMAKER | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
202729325 | Ground Loop | DAY & NIGHT | HB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
202729332 | Ground Loop | HEIL | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
202729333 | Ground Loop | ARCOAIRE | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
202729334 | Ground Loop | KEEPRITE | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
202729335 | Ground Loop | TEMPSTAR | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
202729336 | Ground Loop | COMFORTMAKER | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
202729337 | Ground Loop | DAY & NIGHT | HB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
202732300 | Ground Loop | BOSCH | BP042-1VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
202732301 | Ground Loop | CARRIER | GB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
202732302 | Ground Loop | BRYANT | GB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
202732303 | Ground Loop | ARCOAIRE | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
202732304 | Ground Loop | HEIL | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
202732305 | Ground Loop | KEEPRITE | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
202732306 | Ground Loop | TEMPSTAR | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
202732307 | Ground Loop | COMFORTMAKER | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
202732308 | Ground Loop | DAY & NIGHT | HB042V******1**1 |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
202732914 | Ground Loop | BOSCH-GEO | BP018-1HZ*******C |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
202732916 | Ground Loop | BOSCH | BP018-1HZ*******C |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
202732917 | Ground Loop | CARRIER | GB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
202732918 | Ground Loop | BRYANT | GB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
202732919 | Ground Loop | HEIL | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
202732920 | Ground Loop | ARCOAIRE | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
202732921 | Ground Loop | KEEPRITE | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
202732922 | Ground Loop | TEMPSTAR | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
202732923 | Ground Loop | COMFORTMAKER | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
202732924 | Ground Loop | DAY & NIGHT | HB018H******1**2 |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
202732937 | Ground Loop | TRANE | GWSC048H3 |  | 55100 | 19.28 | 39000 | 3.77 | 4.5917
202732938 | Ground Loop | TRANE | GWSC048H4 |  | 55100 | 19.28 | 39000 | 3.77 | 4.5917
202732939 | Ground Loop | TRANE | GWSC048HW |  | 55100 | 19.28 | 39000 | 3.77 | 4.5917
207337469 | Ground Loop | GEOSTAR | 103H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207337470 | Ground Loop | GEOSTAR | 103H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207337471 | Ground Loop | GEOSTAR | 163H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207337472 | Ground Loop | GEOSTAR | 163H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207337473 | Ground Loop | GEOSTAR | 104H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207337474 | Ground Loop | GEOSTAR | 104H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207337475 | Ground Loop | GEOSTAR | 164H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207337476 | Ground Loop | GEOSTAR | 164H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207337477 | Ground Loop | GEOSTAR | 103J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3
207337478 | Ground Loop | GEOSTAR | 103J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3
207337479 | Ground Loop | GEOSTAR | 163J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3
207337480 | Ground Loop | GEOSTAR | 163J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3
207337481 | Ground Loop | GEOSTAR | 104J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3
207337482 | Ground Loop | GEOSTAR | 104J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3
207337483 | Ground Loop | GEOSTAR | 164J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3
207337484 | Ground Loop | GEOSTAR | 164J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3
207337485 | Ground Loop | GEOSTAR | 103J049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207337486 | Ground Loop | GEOSTAR | 103J049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207337487 | Ground Loop | GEOSTAR | 163J049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207337488 | Ground Loop | GEOSTAR | 163J049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207337489 | Ground Loop | GEOSTAR | 104H049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207337490 | Ground Loop | GEOSTAR | 104H049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207337491 | Ground Loop | GEOSTAR | 164H049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207337492 | Ground Loop | GEOSTAR | 164H049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207337493 | Ground Loop | GEOSTAR | 103J064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207337494 | Ground Loop | GEOSTAR | 103J064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207337495 | Ground Loop | GEOSTAR | 163J064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207337496 | Ground Loop | GEOSTAR | 163J064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207337497 | Ground Loop | GEOSTAR | 104H064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207337498 | Ground Loop | GEOSTAR | 104H064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207337499 | Ground Loop | GEOSTAR | 164H064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207337500 | Ground Loop | GEOSTAR | 164H064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207337509 | Ground Loop | GEOSTAR | 103H022**1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583
207337510 | Ground Loop | GEOSTAR | 103H022**1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583
207337511 | Ground Loop | GEOSTAR | 103H030**1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05
207337512 | Ground Loop | GEOSTAR | 103H030**1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05
207337513 | Ground Loop | GEOSTAR | 103J036**1 | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55
207337514 | Ground Loop | GEOSTAR | 103J036**1 | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55
207337515 | Ground Loop | GEOSTAR | 103J042**1 | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15
207337516 | Ground Loop | GEOSTAR | 103J042**1 | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15
207337517 | Ground Loop | GEOSTAR | 103H048**1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417
6501947 | Ground Loop | GEOSTAR | GBV/GBH038**3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
6501948 | Ground Loop | GEOSTAR | GBV/GBH038**4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
6501949 | Ground Loop | GEOSTAR | GBV/GBH038**4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
215224027 | Ground Loop | BOSCH | CF007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224028 | Ground Loop | BOSCH | CF007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224029 | Ground Loop | BOSCH | CF009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
215224030 | Ground Loop | BOSCH | CF009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
215224031 | Ground Loop | BOSCH | CF012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224032 | Ground Loop | BOSCH | CF012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224033 | Ground Loop | BOSCH | CF015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083
215224034 | Ground Loop | BOSCH | CF015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917
215224035 | Ground Loop | BOSCH | CF018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224036 | Ground Loop | BOSCH | CF018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224037 | Ground Loop | BOSCH | CF007-2VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224038 | Ground Loop | BOSCH | CF007-2VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224039 | Ground Loop | BOSCH | CF009-2VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
215224040 | Ground Loop | BOSCH | CF009-2VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
215224041 | Ground Loop | BOSCH | CF012-2VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224042 | Ground Loop | BOSCH | CF012-2VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224043 | Ground Loop | BOSCH | CF015-2VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083
215224044 | Ground Loop | BOSCH | CF015-2VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917
215224045 | Ground Loop | BOSCH | CF018-2VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224046 | Ground Loop | BOSCH | CF018-2VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224047 | Ground Loop | BOSCH | CF024-2VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224048 | Ground Loop | BOSCH | CF024-4VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224049 | Ground Loop | BOSCH | CF024-2VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224050 | Ground Loop | BOSCH | CF024-4VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
216743648 | Ground Loop | BOSCH | CP048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25
216743649 | Ground Loop | BOSCH | CP048-3VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25
216743650 | Ground Loop | BOSCH | CP048-4VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25
216743651 | Ground Loop | BOSCH-GEO | RP048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083
216743652 | Ground Loop | BOSCH | CP048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083
216743653 | Ground Loop | BOSCH | CP048-3VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083
216743654 | Ground Loop | BOSCH | CP048-4VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083
216743655 | Ground Loop | BOSCH-GEO | RP060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25
216743656 | Ground Loop | BOSCH | CP060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25
216743657 | Ground Loop | BOSCH | CP060-3VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25
216743658 | Ground Loop | BOSCH | CP060-4VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25
216743659 | Ground Loop | BOSCH-GEO | RP060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083
216743660 | Ground Loop | BOSCH | CP060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083
216743661 | Ground Loop | BOSCH | CP060-3VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083
216743662 | Ground Loop | BOSCH | CP060-4VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083
216743663 | Ground Loop | BOSCH-GEO | RP070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
216743664 | Ground Loop | BOSCH | CP070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
216743665 | Ground Loop | BOSCH | CP070-3VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
216743666 | Ground Loop | BOSCH | CP070-4VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
216743671 | Ground Loop | BOSCH-GEO | RP070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
216743672 | Ground Loop | BOSCH | CP070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
216743673 | Ground Loop | BOSCH | CP070-3HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
216743674 | Ground Loop | BOSCH | CP070-4HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
216759674 | Ground Loop | WaterFurnace | W7SZ042BV1**F | W7BM042BN1**2 | 41600 | 19.3 | 41400 | 3.8 | 3.4667
216759816 | Ground Loop | WaterFurnace | W5SS024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833
214067547 | Ground Loop | GeoSmart Energy | GBV/GBH024**3*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
214067548 | Ground Loop | GeoSmart Energy | GBV/GBH024**3*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
214067549 | Ground Loop | GeoSmart Energy | GBV/GBH024**3*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
214067550 | Ground Loop | GeoSmart Energy | GBV/GBH024**4*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
214067551 | Ground Loop | GeoSmart Energy | GBV/GBH024**4*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
214067552 | Ground Loop | GeoSmart Energy | GBV/GBH024**4*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
214067553 | Ground Loop | GeoSmart Energy | GBV/GBH026**3*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
214067554 | Ground Loop | GeoSmart Energy | GBV/GBH026**3*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
214067555 | Ground Loop | GeoSmart Energy | GBV/GBH026**4*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
214067556 | Ground Loop | GeoSmart Energy | GBV/GBH026**4*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
214067557 | Ground Loop | GeoSmart Energy | GBV/GBH030**3*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
214067558 | Ground Loop | GeoSmart Energy | GBV/GBH030**3*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
214067559 | Ground Loop | GeoSmart Energy | GBV/GBH030**3*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
214067560 | Ground Loop | GeoSmart Energy | GBV/GBH030**4*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
214067561 | Ground Loop | GeoSmart Energy | GBV/GBH030**4*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
214067562 | Ground Loop | GeoSmart Energy | GBV/GBH030**4*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
214067563 | Ground Loop | GeoSmart Energy | GBV/GBH036**3*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
214067564 | Ground Loop | GeoSmart Energy | GBV/GBH036**3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
214067565 | Ground Loop | GeoSmart Energy | GBV/GBH036**3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
214067566 | Ground Loop | GeoSmart Energy | GBV/GBH036**4*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
214067567 | Ground Loop | GeoSmart Energy | GBV/GBH036**4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
214067568 | Ground Loop | GeoSmart Energy | GBV/GBH036**4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
214067569 | Ground Loop | GeoSmart Energy | GBV/GBH038**3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
214067570 | Ground Loop | GeoSmart Energy | GBV/GBH038**3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
214067571 | Ground Loop | GeoSmart Energy | GBV/GBH038**4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
214067572 | Ground Loop | GeoSmart Energy | GBV/GBH038**4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
214067574 | Ground Loop | GeoSmart Energy | GBV/GBH042**3*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
214067575 | Ground Loop | GeoSmart Energy | GBV/GBH042**3*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
214067577 | Ground Loop | GeoSmart Energy | GBV/GBH042**4*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
214067578 | Ground Loop | GeoSmart Energy | GBV/GBH042**4*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
214067581 | Ground Loop | GeoSmart Energy | GBV/GBH048**4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
214067582 | Ground Loop | GeoSmart Energy | GBV/GBH048**4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
214067584 | Ground Loop | GeoSmart Energy | GBV/GBH049**3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
214067585 | Ground Loop | GeoSmart Energy | GBV/GBH049**3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
214067586 | Ground Loop | GeoSmart Energy | GBV/GBH049**4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
214067587 | Ground Loop | GeoSmart Energy | GBV/GBH049**4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
214067588 | Ground Loop | GeoSmart Energy | GBV/GBH060**3*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
214067589 | Ground Loop | GeoSmart Energy | GBV/GBH060**3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
214067590 | Ground Loop | GeoSmart Energy | GBV/GBH060**3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
214067591 | Ground Loop | GeoSmart Energy | GBV/GBH060**4*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
214067592 | Ground Loop | GeoSmart Energy | GBV/GBH060**4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
214067593 | Ground Loop | GeoSmart Energy | GBV/GBH060**4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
214067594 | Ground Loop | GeoSmart Energy | GBV/GBH060**5*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
214067595 | Ground Loop | GeoSmart Energy | GBV/GBH064**3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
214067596 | Ground Loop | GeoSmart Energy | GBV/GBH064**3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
214067597 | Ground Loop | GeoSmart Energy | GBV/GBH064**4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
214067598 | Ground Loop | GeoSmart Energy | GBV/GBH064**4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
214067600 | Ground Loop | GeoSmart Energy | GBV/GBH070**3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
214067601 | Ground Loop | GeoSmart Energy | GBV/GBH070**3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
215837814 | Ground Loop | DAIKIN | WSSH024F3*G/J*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417
215837815 | Ground Loop | DAIKIN | WSSH024J1*G/J*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417
215837817 | Ground Loop | DAIKIN | WSSH024K3*G/J*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417
215837822 | Ground Loop | DAIKIN | WSSH024F3*G/J*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417
7519567 | Ground Loop | GEOCOMFORT | GVS030*3 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083
7519568 | Ground Loop | HYDRON MODULE | HVS030*3 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083
7519569 | Ground Loop | TETCO | TVS030*3 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083
7519570 | Ground Loop | GEOCOMFORT | GVS030*4 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083
7519571 | Ground Loop | HYDRON MODULE | HVS030*4 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083
7519572 | Ground Loop | TETCO | TVS030*4 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083
7519573 | Ground Loop | GEOCOMFORT | GVS036*A |  | 37800 | 18 | 30200 | 3.9 | 3.15
7519574 | Ground Loop | HYDRON MODULE | HVS036*A |  | 37800 | 18 | 30200 | 3.9 | 3.15
7519575 | Ground Loop | TETCO | TVS036*A |  | 37800 | 18 | 30200 | 3.9 | 3.15
7519576 | Ground Loop | GEOCOMFORT | GVS036*2 |  | 37800 | 18 | 30200 | 3.9 | 3.15
7519577 | Ground Loop | HYDRON MODULE | HVS036*2 |  | 37800 | 18 | 30200 | 3.9 | 3.15
7519578 | Ground Loop | TETCO | TVS036*2 |  | 37800 | 18 | 30200 | 3.9 | 3.15
7519579 | Ground Loop | GEOCOMFORT | GVS036*3 |  | 37800 | 18 | 30200 | 3.9 | 3.15
7519580 | Ground Loop | HYDRON MODULE | HVS036*3 |  | 37800 | 18 | 30200 | 3.9 | 3.15
7519581 | Ground Loop | TETCO | TVS036*3 |  | 37800 | 18 | 30200 | 3.9 | 3.15
7519582 | Ground Loop | GEOCOMFORT | GVS036*4 |  | 37800 | 18 | 30200 | 3.9 | 3.15
7519583 | Ground Loop | HYDRON MODULE | HVS036*4 |  | 37800 | 18 | 30200 | 3.9 | 3.15
7519584 | Ground Loop | TETCO | TVS036*4 |  | 37800 | 18 | 30200 | 3.9 | 3.15
7519727 | Ground Loop | GEOCOMFORT | GVS024*****1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25
7519748 | Ground Loop | HYDRON MODULE | HVS024*****1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25
7519756 | Ground Loop | TETCO | TVS024*****1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25
7519769 | Ground Loop | GEOCOMFORT | GVS024*A***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25
7519770 | Ground Loop | HYDRON MODULE | HVS024*A***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25
7519771 | Ground Loop | TETCO | TVS024*A***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25
7519772 | Ground Loop | GEOCOMFORT | GVS024*2***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25
7519773 | Ground Loop | HYDRON MODULE | HVS024*2***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25
7519774 | Ground Loop | TETCO | TVS024*2***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25
7519775 | Ground Loop | GEOCOMFORT | GVS024*3***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25
7519776 | Ground Loop | HYDRON MODULE | HVS024*3***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25
7519777 | Ground Loop | TETCO | TVS024*3***1 |  | 27000 | 21.6 | 19300 | 4.2 | 2.25
7520238 | Ground Loop | GEOCOMFORT | GVS030*****1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167
7520239 | Ground Loop | HYDRON MODULE | HVS030*****1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167
7520240 | Ground Loop | TETCO | TVS030*****1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167
7520241 | Ground Loop | GEOCOMFORT | GVS030*2***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167
7520242 | Ground Loop | HYDRON MODULE | HVS030*2***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167
7520243 | Ground Loop | TETCO | TVS030*2***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167
7520244 | Ground Loop | TETCO | TVS030*3***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167
7520245 | Ground Loop | HYDRON MODULE | HVS030*3***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167
7520246 | Ground Loop | GEOCOMFORT | GVS030*A***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167
7520247 | Ground Loop | HYDRON MODULE | HVS030*A***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167
7520248 | Ground Loop | TETCO | TVS030*A***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167
7520249 | Ground Loop | GEOCOMFORT | GVS030*3***1 |  | 31400 | 20.4 | 23200 | 4.2 | 2.6167
7520250 | Ground Loop | GEOCOMFORT | GVS036*****1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333
7520251 | Ground Loop | HYDRON MODULE | HVS036*****1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333
7520252 | Ground Loop | TETCO | TVS036*****1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333
7520253 | Ground Loop | GEOCOMFORT | GVS036*2***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333
7520254 | Ground Loop | HYDRON MODULE | HVS036*2***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333
7520255 | Ground Loop | TETCO | TVS036*2***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333
7520256 | Ground Loop | GEOCOMFORT | GVS036*3***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333
7520257 | Ground Loop | HYDRON MODULE | HVS036*3***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333
7520258 | Ground Loop | TETCO | TVS036*3***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333
7520259 | Ground Loop | GEOCOMFORT | GVS036*A***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333
7520260 | Ground Loop | HYDRON MODULE | HVS036*A***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333
7520261 | Ground Loop | TETCO | TVS036*A***1 |  | 38800 | 19.2 | 29600 | 3.9 | 3.2333
7523956 | Ground Loop | GEOCOMFORT | GVS018*****1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083
7523957 | Ground Loop | HYDRON MODULE | HVS018*****1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083
203254607 | Ground Loop | BRYANT | GB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203254608 | Ground Loop | ARCOAIRE | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203254609 | Ground Loop | HEIL | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203254610 | Ground Loop | KEEPRITE | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203254611 | Ground Loop | TEMPSTAR | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203254612 | Ground Loop | COMFORTMAKER | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203254614 | Ground Loop | DAY & NIGHT | HB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203254620 | Ground Loop | BRYANT | GC024V/C**N***1*X1 |  | 26600 | 18.2 | 18000 | 3.7 | 2.2167
203254624 | Ground Loop | BRYANT | GC024H**C***1*X1 |  | 26600 | 19.9 | 18000 | 3.7 | 2.2167
203254626 | Ground Loop | BRYANT | GC024H**N***1*X1 |  | 26600 | 18.3 | 18000 | 3.7 | 2.2167
203254744 | Ground Loop | CARRIER | GC024V/C**N***1**1 |  | 26600 | 18.2 | 18000 | 3.7 | 2.2167
203254748 | Ground Loop | CARRIER | GC024H**C***1**1 |  | 26600 | 19.9 | 18000 | 3.7 | 2.2167
203254752 | Ground Loop | CARRIER | GC024H**N***1**1 |  | 26600 | 18.3 | 18000 | 3.7 | 2.2167
203260718 | Ground Loop | BOSCH-GEO | SM024-1VT/CFC******A |  | 26600 | 18.9 | 18000 | 3.7 | 2.2167
203260866 | Ground Loop | CARRIER | GC024V/C**C***1**1 + UI |  | 26600 | 18.9 | 18000 | 3.7 | 2.2167
203260867 | Ground Loop | BRYANT | GC024V/C**C***1*X1 + UI |  | 26600 | 18.9 | 18000 | 3.7 | 2.2167
215268677 | Ground Loop | WaterFurnace | V5A(V/H)015*R0**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
215268678 | Ground Loop | WaterFurnace | V5A(V/H)015*R2**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
215268679 | Ground Loop | WaterFurnace | V5A(V/H)018*R2**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
215268680 | Ground Loop | WaterFurnace | V5A(V/H)018*R0**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
215268681 | Ground Loop | WaterFurnace | V5A(V/H)018*R2**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
215268682 | Ground Loop | WaterFurnace | V5A(V/H)024*S2**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
215268683 | Ground Loop | WaterFurnace | V5A(V/H)024*S3**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
215268684 | Ground Loop | WaterFurnace | V5A(V/H)024*S4**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
215268685 | Ground Loop | WaterFurnace | V5A(V/H)024*S0**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
215268686 | Ground Loop | WaterFurnace | V5A(V/H)024*S2**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
215268687 | Ground Loop | WaterFurnace | V5A(V/H)024*S3**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
215268688 | Ground Loop | WaterFurnace | V5A(V/H)024*S4**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
215268689 | Ground Loop | WaterFurnace | V5A(V/H)030*S3**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
215268690 | Ground Loop | WaterFurnace | V5A(V/H)030*S0**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
215268691 | Ground Loop | WaterFurnace | V5A(V/H)030*S3**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
215268692 | Ground Loop | WaterFurnace | V5A(V/H)036*S3**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
215268693 | Ground Loop | WaterFurnace | V5A(V/H)036*S0**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
215268694 | Ground Loop | WaterFurnace | V5A(V/H)036*S3**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
215268695 | Ground Loop | WaterFurnace | V5A(V/H)036*S0**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
215268696 | Ground Loop | WaterFurnace | V5A(V/H)036*S3**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
215268697 | Ground Loop | WaterFurnace | V5A(V/H)042*S3**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
215268698 | Ground Loop | WaterFurnace | V5A(V/H)042*S0**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
215268699 | Ground Loop | WaterFurnace | V5A(V/H)042*S3**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
215268700 | Ground Loop | WaterFurnace | V5A(V/H)042*S0**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
215268701 | Ground Loop | WaterFurnace | V5A(V/H)042*S3**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
215268702 | Ground Loop | WaterFurnace | V5A(V/H)048*S3**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25
215268703 | Ground Loop | WaterFurnace | V5A(V/H)048*S0**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
215268704 | Ground Loop | WaterFurnace | V5A(V/H)048*S3**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
215268705 | Ground Loop | WaterFurnace | V5A(V/H)048*S0**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25
215268706 | Ground Loop | WaterFurnace | V5A(V/H)048*S3**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25
215268707 | Ground Loop | WaterFurnace | V5A(V/H)060*S3**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
215268708 | Ground Loop | WaterFurnace | V5A(V/H)060*S0**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
215268709 | Ground Loop | WaterFurnace | V5A(V/H)060*S3**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
215268710 | Ground Loop | WaterFurnace | V5A(V/H)072*S3**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
215268711 | Ground Loop | WaterFurnace | V5A(V/H)072*S0**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
215268712 | Ground Loop | WaterFurnace | V5A(V/H)072*S3**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
215268713 | Ground Loop | WaterFurnace | V5A(V/H)030*S2**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
215268714 | Ground Loop | WaterFurnace | V5A(V/H)030*S4**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
215268715 | Ground Loop | WaterFurnace | V5A(V/H)030*S2**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
215268716 | Ground Loop | WaterFurnace | V5A(V/H)030*S4**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
215268717 | Ground Loop | WaterFurnace | V5A(V/H)036*S4**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
215268718 | Ground Loop | WaterFurnace | V5A(V/H)036*S2**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
215268719 | Ground Loop | WaterFurnace | V5A(V/H)036*S4**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
215268720 | Ground Loop | WaterFurnace | V5A(V/H)036*S2**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
215268721 | Ground Loop | WaterFurnace | V5A(V/H)036*S4**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
215268722 | Ground Loop | WaterFurnace | V5A(V/H)042*S4**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
215268723 | Ground Loop | WaterFurnace | V5A(V/H)042*S2**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
215268724 | Ground Loop | WaterFurnace | V5A(V/H)042*S4**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
215268725 | Ground Loop | WaterFurnace | V5A(V/H)042*S4**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
215268726 | Ground Loop | WaterFurnace | V5A(V/H)048*S4**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25
215268727 | Ground Loop | WaterFurnace | V5A(V/H)048*S2**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
215268728 | Ground Loop | WaterFurnace | V5A(V/H)048*S4**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
215268729 | Ground Loop | WaterFurnace | V5A(V/H)048*S4**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25
215268730 | Ground Loop | WaterFurnace | V5A(V/H)060*S4**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
215268731 | Ground Loop | WaterFurnace | V5A(V/H)060*S4**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
215268732 | Ground Loop | WaterFurnace | V5A(V/H)072*S4**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
217351675 | Ground Loop | BOSCH | RP048-1CSC-*****A | BIVA-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167
217351676 | Ground Loop | BOSCH | RP048-1CSN-*****A | BIVA-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833
217351677 | Ground Loop | BOSCH | RP060-1CSC-*****A | BIVA-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667
217351678 | Ground Loop | BOSCH | RP060-1CSN-*****A | BIVA-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05
217351679 | Ground Loop | BOSCH | RP024-1CSC-*****A | BMAC2430BBTA | 25400 | 18.1 | 18800 | 4.1 | 2.1167
217351680 | Ground Loop | BOSCH | RP024-1CSN-*****A | BMAC2430BBTA | 26000 | 18.3 | 18800 | 4.3 | 2.1667
217351682 | Ground Loop | BOSCH | RP036-1CSN-*****A | BMAC3036BBTA | 38200 | 17.2 | 30800 | 4.2 | 3.1833
217351683 | Ground Loop | BOSCH | RP048-1CSC-*****A | BMAC4248CBTA | 50200 | 17.5 | 37200 | 3.9 | 4.1833
217351684 | Ground Loop | BOSCH | RP048-1CSN-*****A | BMAC4248CBTA | 51600 | 17.8 | 38200 | 4.1 | 4.3
217351692 | Ground Loop | FHP | CP024-1CSC-*****A | BIVA-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667
217351693 | Ground Loop | FHP | CP024-1CSN-*****A | BIVA-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667
217351694 | Ground Loop | FHP | CP036-1CSC-*****A | BIVA-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833
217351695 | Ground Loop | FHP | CP036-1CSN-*****A | BIVA-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667
214776193 | Ground Loop | TRANE | GETK0242-5 |  | 25200 | 18.5 | 20100 | 3.82 | 2.1
214776194 | Ground Loop | TRANE | GETK0247-5 |  | 25200 | 18.5 | 20100 | 3.82 | 2.1
214796343 | Ground Loop | WaterFurnace | W5A(V/H)024BD1**2 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
214796344 | Ground Loop | WaterFurnace | W5A(V/H)030BD1**2 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
214796345 | Ground Loop | WaterFurnace | W5A(V/H)036BD1**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
214796346 | Ground Loop | WaterFurnace | W5A(V/H)042BD1**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
214796347 | Ground Loop | WaterFurnace | W5A(V/H)048BD1**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
214796667 | Ground Loop | WaterFurnace | W5A(V/H)018BD1**2 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583
214796668 | Ground Loop | WaterFurnace | W5A(V/H)060BD1**2 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
214796669 | Ground Loop | WaterFurnace | W5A(V/H)072BD1**2 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
214810491 | Ground Loop | GEOSTAR | G5A(V/H)018BD1**2 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583
214810492 | Ground Loop | GEOSTAR | G5A(V/H)024BD1**2 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
214810493 | Ground Loop | GEOSTAR | G5A(V/H)030BD1**2 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
214810494 | Ground Loop | GEOSTAR | G5A(V/H)036BD1**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
214810495 | Ground Loop | GEOSTAR | G5A(V/H)042BD1**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
214810496 | Ground Loop | GEOSTAR | G5A(V/H)048BD1**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
214810497 | Ground Loop | GEOSTAR | G5A(V/H)060BD1**2 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
214810498 | Ground Loop | GEOSTAR | G5A(V/H)072BD1**2 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
214823444 | Ground Loop | GeoSmart Energy | S5A(V/H)018BD1**2 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583
214823445 | Ground Loop | GeoSmart Energy | S5A(V/H)024BD1**2 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
214823446 | Ground Loop | GeoSmart Energy | S5A(V/H)030BD1**2 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
214823447 | Ground Loop | GeoSmart Energy | S5A(V/H)036BD1**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
214823448 | Ground Loop | GeoSmart Energy | S5A(V/H)042BD1**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
214823449 | Ground Loop | GeoSmart Energy | S5A(V/H)048BD1**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
214823450 | Ground Loop | GeoSmart Energy | S5A(V/H)060BD1**2 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
214823451 | Ground Loop | GeoSmart Energy | S5A(V/H)072BD1**2 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
214823480 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)018BD1**2 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583
214823481 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024BD1**2 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
214823482 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030BD1**2 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
215685119 | Ground Loop | Dandelion Geo | DPG2048 |  | 50440 | 17.1 | 42300 | 4.7 | 4.2033
215685120 | Ground Loop | Dandelion Geo | DPG2060 |  | 63000 | 17.6 | 54570 | 4.6 | 5.25
216739885 | Ground Loop | DAIKIN | WSDV036E1*G/J*C |  | 37100 | 19 | 27300 | 3.8 | 3.0917
216739886 | Ground Loop | DAIKIN | WSDV036F3*G/J*C |  | 37100 | 18.6 | 27300 | 3.7 | 3.0917
216739887 | Ground Loop | DAIKIN | WSDV036J1*G/J*C |  | 37100 | 18.6 | 27300 | 3.7 | 3.0917
216739888 | Ground Loop | DAIKIN | WSDV036K3*G/J*C |  | 37100 | 18.4 | 27300 | 3.7 | 3.0917
216739901 | Ground Loop | DAIKIN | WSDV060E1*G/J*C |  | 62000 | 17.3 | 46100 | 3.7 | 5.1667
216739902 | Ground Loop | DAIKIN | WSDV060F3*G/J*C |  | 62000 | 17 | 46100 | 3.6 | 5.1667
216739903 | Ground Loop | DAIKIN | WSDV060K3*G/J*C |  | 62000 | 17 | 46100 | 3.6 | 5.1667
216739914 | Ground Loop | DAIKIN | WSNH024E1*G/J*C |  | 25300 | 18.5 | 17900 | 3.6 | 2.1083
215832292 | Ground Loop | AE Air | WSH6012D* |  | 12000 | 17.9 | 8500 | 3.8 | 1
215832293 | Ground Loop | AE Air | WSH6018D* |  | 19000 | 18 | 12000 | 3.6 | 1.5833
215832294 | Ground Loop | AE Air | WSH6024D* |  | 26000 | 18.4 | 17500 | 3.6 | 2.1667
215832295 | Ground Loop | AE Air | WSH6030D* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5
215832296 | Ground Loop | AE Air | WSH6036D* |  | 36400 | 18 | 28000 | 3.6 | 3.0333
215832297 | Ground Loop | AE Air | WSH6042D* |  | 43500 | 18.5 | 31000 | 3.8 | 3.625
215832298 | Ground Loop | AE Air | WSH6048D* |  | 49500 | 18 | 36000 | 3.6 | 4.125
215832299 | Ground Loop | AE Air | WSH6060D* |  | 60000 | 18.1 | 41000 | 3.6 | 5
215832300 | Ground Loop | AE Air | WSH6072D* |  | 73000 | 17.1 | 55000 | 3.6 | 6.0833
202921913 | Ground Loop | BOSCH | EP036-3HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202921914 | Ground Loop | BOSCH | EP036-4HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202921915 | Ground Loop | BOSCH-GEO | BP036-1HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202921952 | Ground Loop | FHP | EP036-1HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202921953 | Ground Loop | FHP | EP036-3HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202921954 | Ground Loop | FHP | EP036-4HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202921956 | Ground Loop | BOSCH | BP036-1HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202921957 | Ground Loop | FHP | EP036-1VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202921958 | Ground Loop | FHP | EP036-3VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202921959 | Ground Loop | FHP | EP036-4VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202921960 | Ground Loop | BOSCH | BP036-1VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202922686 | Ground Loop | CARRIER | 50PSH036***3/CA |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202922689 | Ground Loop | CARRIER | 50PSH036***5/EA |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202922692 | Ground Loop | CARRIER | 50PSH036***6/FA |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202922695 | Ground Loop | CARRIER | GB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202922697 | Ground Loop | BRYANT | GB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202922700 | Ground Loop | HEIL | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202922703 | Ground Loop | ARCOAIRE | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202922706 | Ground Loop | KEEPRITE | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202922708 | Ground Loop | TEMPSTAR | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202922711 | Ground Loop | COMFORTMAKER | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202922714 | Ground Loop | DAY & NIGHT | HB036H******1**1 |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202922716 | Ground Loop | CARRIER | 50PSV036***3/CA |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202922719 | Ground Loop | CARRIER | 50PSV036***5/EA |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202922722 | Ground Loop | CARRIER | 50PSV036***6/FA |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202922725 | Ground Loop | CARRIER | GB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202922728 | Ground Loop | BRYANT | GB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202922731 | Ground Loop | HEIL | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202922734 | Ground Loop | ARCOAIRE | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202922737 | Ground Loop | KEEPRITE | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202922740 | Ground Loop | TEMPSTAR | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202922742 | Ground Loop | COMFORTMAKER | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202922745 | Ground Loop | DAY & NIGHT | HB036V******1**1 |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
7418887 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
7418965 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**4*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
7419321 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
7419403 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
7419527 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
7419618 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
7419733 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
7419797 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH048**4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
7421327 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
7421397 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
7421438 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
7421969 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
7421970 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH049**4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
7421971 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
7421972 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
7421973 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
7421974 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
7421975 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
7421976 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
7421977 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
7421980 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
7421989 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
7421999 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH060**5*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
7422020 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
7422043 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
7422058 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
215399774 | Ground Loop | DAIKIN | WSMV015A1*G/J*T |  | 16300 | 21.12 | 11000 | 3.64 | 1.3583
215399775 | Ground Loop | DAIKIN | WSMV015J1*G/J*T |  | 16300 | 21.12 | 11100 | 3.64 | 1.3583
215399778 | Ground Loop | DAIKIN | WSMV015A1*G/J*C |  | 16300 | 21.12 | 11000 | 3.64 | 1.3583
215399779 | Ground Loop | DAIKIN | WSMV015J1*G/J*C |  | 16300 | 21.12 | 11100 | 3.64 | 1.3583
215399788 | Ground Loop | DAIKIN | WSMV024J1*G/J*P |  | 25500 | 19.07 | 18900 | 3.62 | 2.125
215399789 | Ground Loop | DAIKIN | WSMV024K3*G/J*P |  | 25500 | 19.07 | 18900 | 3.62 | 2.125
217531660 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)006A |  | 6700 | 20 | 4600 | 3.6 | 0.55833
217531661 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)009A |  | 9700 | 19 | 7000 | 3.7 | 0.80833
217531662 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)012A |  | 12400 | 19.5 | 9200 | 3.6 | 1.0333
217531663 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)018A |  | 20100 | 19.5 | 14500 | 4.1 | 1.675
216739978 | Ground Loop | DAIKIN | WSNV048E1*G/J*C |  | 51100 | 19.5 | 35000 | 3.8 | 4.2583
216739979 | Ground Loop | DAIKIN | WSNV048F3*G/J*C |  | 51100 | 19.1 | 35000 | 3.8 | 4.2583
216739980 | Ground Loop | DAIKIN | WSNV048K3*G/J*C |  | 51100 | 19.1 | 35000 | 3.8 | 4.2583
216739984 | Ground Loop | DAIKIN | WSNV060E1*G/J*C |  | 62200 | 17.8 | 46200 | 3.8 | 5.1833
216739985 | Ground Loop | DAIKIN | WSNV060F3*G/J*C |  | 62200 | 17.4 | 46200 | 3.7 | 5.1833
216739986 | Ground Loop | DAIKIN | WSNV060K3*G/J*C |  | 62200 | 17.4 | 46200 | 3.7 | 5.1833
216743538 | Ground Loop | DAIKIN | WSNH048E1*G/J*C |  | 49100 | 18.8 | 38500 | 3.6 | 4.0917
216743541 | Ground Loop | DAIKIN | WSNV024E1*G/J*C |  | 25100 | 18.8 | 18200 | 3.8 | 2.0917
216743542 | Ground Loop | DAIKIN | WSNV024F3*G/J*C |  | 25100 | 18.4 | 18200 | 3.8 | 2.0917
216743543 | Ground Loop | DAIKIN | WSNV024J1*G/J*C |  | 25100 | 18.4 | 18200 | 3.8 | 2.0917
216743544 | Ground Loop | DAIKIN | WSNV024K3*G/J*C |  | 25100 | 18.2 | 18200 | 3.7 | 2.0917
216743617 | Ground Loop | BOSCH-GEO | RP024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
216743618 | Ground Loop | BOSCH | CP024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
216743619 | Ground Loop | BOSCH | CP024-2VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
216743620 | Ground Loop | BOSCH | CP024-3VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
216743621 | Ground Loop | BOSCH | CP024-4VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
216743622 | Ground Loop | BOSCH-GEO | RP024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216743623 | Ground Loop | BOSCH | CP024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216743624 | Ground Loop | BOSCH | CP024-2VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216743625 | Ground Loop | BOSCH | CP024-3VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216743626 | Ground Loop | BOSCH | CP024-4VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216743627 | Ground Loop | BOSCH-GEO | RP024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
216743628 | Ground Loop | BOSCH | CP024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
216743629 | Ground Loop | BOSCH | CP024-2HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
216743630 | Ground Loop | BOSCH | CP024-3HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
216743631 | Ground Loop | BOSCH | CP024-4HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
216743632 | Ground Loop | BOSCH-GEO | RP024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216743633 | Ground Loop | BOSCH | CP024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216743634 | Ground Loop | BOSCH | CP024-2HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216743635 | Ground Loop | BOSCH | CP024-3HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216743636 | Ground Loop | BOSCH | CP024-4HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216743637 | Ground Loop | BOSCH-GEO | RP036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25
216743638 | Ground Loop | BOSCH | CP036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25
216743639 | Ground Loop | BOSCH | CP036-2VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25
216743640 | Ground Loop | BOSCH | CP036-3VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25
216743641 | Ground Loop | BOSCH | CP036-4VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25
216743642 | Ground Loop | BOSCH-GEO | RP036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216743643 | Ground Loop | BOSCH | CP036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216743644 | Ground Loop | BOSCH | CP036-2VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216743645 | Ground Loop | BOSCH | CP036-3VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216743646 | Ground Loop | BOSCH | CP036-4VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216743647 | Ground Loop | BOSCH-GEO | RP048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25
5295966 | Ground Loop | WaterFurnace | NBV/NBH018**2*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
5295968 | Ground Loop | WaterFurnace | NBV/NBH018**0*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
5295969 | Ground Loop | WaterFurnace | NBV/NBH018**0*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
5295980 | Ground Loop | WaterFurnace | NBV/NBH024**0*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
5295981 | Ground Loop | WaterFurnace | NBV/NBH024**3*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
5295982 | Ground Loop | WaterFurnace | NBV/NBH024**4*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
5295983 | Ground Loop | WaterFurnace | NBV/NBH024**2*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
5295984 | Ground Loop | WaterFurnace | NBV/NBH024**0*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
5295985 | Ground Loop | WaterFurnace | NBV/NBH024**3*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
5295986 | Ground Loop | WaterFurnace | NBV/NBH024**2*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
5295987 | Ground Loop | WaterFurnace | NBV/NBH024**4*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
5295988 | Ground Loop | WaterFurnace | NBV/NBH024**4*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
5295989 | Ground Loop | WaterFurnace | NBV/NBH024**3*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
5295990 | Ground Loop | WaterFurnace | NBV/NBH024**0*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
5295991 | Ground Loop | WaterFurnace | NBV/NBH024**2*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
5295992 | Ground Loop | WaterFurnace | NBV/NBH030**0*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
5295993 | Ground Loop | WaterFurnace | NBV/NBH030**3*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
5295994 | Ground Loop | WaterFurnace | NBV/NBH030**4*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
5295995 | Ground Loop | WaterFurnace | NBV/NBH030**2*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
5295996 | Ground Loop | WaterFurnace | NBV/NBH030**0*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
5295997 | Ground Loop | WaterFurnace | NBV/NBH030**2*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
207348682 | Ground Loop | WaterFurnace | URS060*0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
207348683 | Ground Loop | WaterFurnace | URS060*0*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
207348684 | Ground Loop | WaterFurnace | URS060*3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
207348685 | Ground Loop | WaterFurnace | URS060*3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
207348686 | Ground Loop | WaterFurnace | URS060*3*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
207348687 | Ground Loop | WaterFurnace | URS060*4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
207348688 | Ground Loop | WaterFurnace | URS060*4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
207348689 | Ground Loop | WaterFurnace | URS060*4*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
207348707 | Ground Loop | WaterFurnace | URD038*0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207348708 | Ground Loop | WaterFurnace | URD038*0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207348709 | Ground Loop | WaterFurnace | URD038*0*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207348710 | Ground Loop | WaterFurnace | URD038*3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207348711 | Ground Loop | WaterFurnace | URD038*3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207348712 | Ground Loop | WaterFurnace | URD038*3*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207348713 | Ground Loop | WaterFurnace | URD038*4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207348714 | Ground Loop | WaterFurnace | URD038*4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207348715 | Ground Loop | WaterFurnace | URD038*4*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207348716 | Ground Loop | WaterFurnace | URD049*0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207348717 | Ground Loop | WaterFurnace | URD049*0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207348718 | Ground Loop | WaterFurnace | URD049*0*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207348719 | Ground Loop | WaterFurnace | URD049*3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207348720 | Ground Loop | WaterFurnace | URD049*3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207348721 | Ground Loop | WaterFurnace | URD049*3*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207348722 | Ground Loop | WaterFurnace | URD049*4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207348723 | Ground Loop | WaterFurnace | URD049*4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207348724 | Ground Loop | WaterFurnace | URD049*4*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207348725 | Ground Loop | WaterFurnace | URD064*0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207348726 | Ground Loop | WaterFurnace | URD064*0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207348727 | Ground Loop | WaterFurnace | URD064*0*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207348728 | Ground Loop | WaterFurnace | URD064*3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207348729 | Ground Loop | WaterFurnace | URD064*3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207348730 | Ground Loop | WaterFurnace | URD064*3*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207348731 | Ground Loop | WaterFurnace | URD064*4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207348732 | Ground Loop | WaterFurnace | URD064*4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207348733 | Ground Loop | WaterFurnace | URD064*4*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207348734 | Ground Loop | WaterFurnace | URD072*0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207348735 | Ground Loop | WaterFurnace | URD072*0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207348736 | Ground Loop | WaterFurnace | URD072*0*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207348737 | Ground Loop | WaterFurnace | URD072*3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207348738 | Ground Loop | WaterFurnace | URD072*3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207348739 | Ground Loop | WaterFurnace | URD072*3*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207348740 | Ground Loop | WaterFurnace | URD072*4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207348741 | Ground Loop | WaterFurnace | URD072*4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207348742 | Ground Loop | WaterFurnace | URD072*4*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
215811946 | Ground Loop | HYDROTECH | WSV6009D* |  | 9800 | 19 | 6800 | 3.7 | 0.81667
215811947 | Ground Loop | AE Air | WSV6009D* |  | 9800 | 19 | 6800 | 3.7 | 0.81667
215811948 | Ground Loop | HYDROTECH | WSV6012D* |  | 12500 | 19 | 9000 | 3.6 | 1.0417
215811950 | Ground Loop | AE Air | WSV6012D* |  | 12500 | 19 | 9000 | 3.6 | 1.0417
215811951 | Ground Loop | HYDROTECH | WSV6018D* |  | 18000 | 17.2 | 13000 | 3.6 | 1.5
215811952 | Ground Loop | AE Air | WSV6018D* |  | 18000 | 17.2 | 13000 | 3.6 | 1.5
215811953 | Ground Loop | HYDROTECH | WSV6024D* |  | 23000 | 18 | 17500 | 3.6 | 1.9167
215811954 | Ground Loop | AE Air | WSV6024D* |  | 23000 | 18 | 17500 | 3.6 | 1.9167
215811955 | Ground Loop | HYDROTECH | WSV6030D* |  | 28000 | 17.5 | 19900 | 3.6 | 2.3333
215811957 | Ground Loop | AE Air | WSV6030D* |  | 28000 | 17.5 | 19900 | 3.6 | 2.3333
215811958 | Ground Loop | HYDROTECH | WSV6036D* |  | 37000 | 18 | 28000 | 3.6 | 3.0833
215811959 | Ground Loop | AE Air | WSV6036D* |  | 37000 | 18 | 28000 | 3.6 | 3.0833
215811960 | Ground Loop | HYDROTECH | WSV6042D* |  | 42000 | 18 | 30000 | 3.6 | 3.5
215811961 | Ground Loop | AE Air | WSV6042D* |  | 42000 | 18 | 30000 | 3.6 | 3.5
215815841 | Ground Loop | HYDROTECH | WSV6060D* |  | 63000 | 18 | 42500 | 3.6 | 5.25
215815842 | Ground Loop | AE Air | WSV6060D* |  | 63000 | 18 | 42500 | 3.6 | 5.25
215815843 | Ground Loop | HYDROTECH | WSV6072D* |  | 73000 | 17.9 | 52000 | 3.6 | 6.0833
215815844 | Ground Loop | AE Air | WSV6072D* |  | 73000 | 17.9 | 52000 | 3.6 | 6.0833
215415780 | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)024A*VB |  | 25800 | 18 | 19000 | 3.7 | 2.15
215415781 | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)024A*VC |  | 25800 | 18 | 19000 | 3.7 | 2.15
215415784 | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)030A*VB |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417
215415785 | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)030A*VC |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417
215415788 | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)036A*VB |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333
215415789 | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)036A*VC |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333
217754450 | Ground Loop | DAIKIN | WSSV048F1*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35
217754451 | Ground Loop | DAIKIN | WSSV048K1*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35
217754452 | Ground Loop | DAIKIN | WSSV048L1*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35
217754454 | Ground Loop | DAIKIN | WSSV048F1*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35
217754455 | Ground Loop | DAIKIN | WSSV048K1*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35
217754456 | Ground Loop | DAIKIN | WSSV048L1*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35
217754458 | Ground Loop | DAIKIN | WSSV060F1*H*T |  | 66300 | 19.8 | 48800 | 3.96 | 5.525
217754459 | Ground Loop | DAIKIN | WSSV060K1*H*T |  | 66300 | 19.8 | 48800 | 3.92 | 5.525
217754460 | Ground Loop | DAIKIN | WSSV060L1*H*T |  | 66300 | 19.4 | 48800 | 3.88 | 5.525
217754462 | Ground Loop | DAIKIN | WSSV060F1*H*C |  | 66300 | 19.8 | 48800 | 3.96 | 5.525
217754463 | Ground Loop | DAIKIN | WSSV060K1*H*C |  | 66300 | 19.8 | 48800 | 3.92 | 5.525
217754464 | Ground Loop | DAIKIN | WSSV060L1*H*C |  | 66300 | 19.4 | 48800 | 3.88 | 5.525
217754466 | Ground Loop | DAIKIN | WSSV070F1*H*T |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833
217754467 | Ground Loop | DAIKIN | WSSV070K1*H*T |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833
217754468 | Ground Loop | DAIKIN | WSSV070L1*H*T |  | 75400 | 18.82 | 54700 | 3.69 | 6.2833
217754470 | Ground Loop | DAIKIN | WSSV070F1*H*C |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833
217754471 | Ground Loop | DAIKIN | WSSV070K1*H*C |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833
217754472 | Ground Loop | DAIKIN | WSSV070L1*H*C |  | 75400 | 18.82 | 54700 | 3.69 | 6.2833
217754475 | Ground Loop | DAIKIN | WSTH024E1*H*C |  | 25100 | 19.92 | 17200 | 3.92 | 2.0917
217754476 | Ground Loop | DAIKIN | WSTH024F1*H*C |  | 25100 | 19.52 | 17200 | 3.84 | 2.0917
217754479 | Ground Loop | DAIKIN | WSTH030E1*H*C |  | 32700 | 19.69 | 20600 | 3.75 | 2.725
217754480 | Ground Loop | DAIKIN | WSTH030F1*H*C |  | 32700 | 19.29 | 20600 | 3.68 | 2.725
217754483 | Ground Loop | DAIKIN | WSTH036E1*H*C |  | 38700 | 20.64 | 25900 | 3.75 | 3.225
217754484 | Ground Loop | DAIKIN | WSTH036F1*H*C |  | 38700 | 20.23 | 25900 | 3.67 | 3.225
217754487 | Ground Loop | DAIKIN | WSTH042E1*H*C |  | 45900 | 20.06 | 28400 | 3.7 | 3.825
217754488 | Ground Loop | DAIKIN | WSTH042F1*H*C |  | 45900 | 19.66 | 28400 | 3.63 | 3.825
217754491 | Ground Loop | DAIKIN | WSTH048E1*H*C |  | 49300 | 19.59 | 36300 | 3.87 | 4.1083
217754492 | Ground Loop | DAIKIN | WSTH048F1*H*C |  | 49300 | 19.19 | 36300 | 3.79 | 4.1083
217754495 | Ground Loop | DAIKIN | WSTH060E1*H*C |  | 61600 | 19 | 44200 | 3.7 | 5.1333
217754496 | Ground Loop | DAIKIN | WSTH060F1*H*C |  | 61600 | 18.62 | 44200 | 3.63 | 5.1333
217754499 | Ground Loop | DAIKIN | WSTH070E1*H*C |  | 75600 | 19.03 | 52200 | 3.66 | 6.3
217754503 | Ground Loop | DAIKIN | WSTV024E1*H*C |  | 22400 | 17.99 | 17200 | 3.98 | 1.8667
217014544 | Ground Loop | HEIL | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217014545 | Ground Loop | ARCOAIRE | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217014546 | Ground Loop | KEEPRITE | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217014547 | Ground Loop | TEMPSTAR | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217014548 | Ground Loop | COMFORTMAKER | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217014549 | Ground Loop | DAY & NIGHT | HCR72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217037791 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS024BD1 | Y5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833
217037792 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS036BD1 | Y5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833
217037793 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS048BD1 | Y5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925
217037794 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS060BD1 | Y5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917
217037796 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ024BD1 | Y5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833
217037797 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ036BD1 | Y5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833
217037798 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ048BD1 | Y5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925
217037799 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ060BD1 | Y5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917
217037801 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833
217037802 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833
217037803 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925
217037804 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SS060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917
217037806 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833
217037807 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833
217037808 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925
217037809 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5SZ060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917
217037811 | Ground Loop | GeoSmart Energy | S5SS024BD1 | S5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833
217037812 | Ground Loop | GeoSmart Energy | S5SS036BD1 | S5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833
217037813 | Ground Loop | GeoSmart Energy | S5SS048BD1 | S5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925
217037814 | Ground Loop | GeoSmart Energy | S5SS060BD1 | S5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917
217037816 | Ground Loop | GeoSmart Energy | S5SZ024BD1 | S5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833
217037817 | Ground Loop | GeoSmart Energy | S5SZ036BD1 | S5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833
217037818 | Ground Loop | GeoSmart Energy | S5SZ048BD1 | S5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925
217037819 | Ground Loop | GeoSmart Energy | S5SZ060BD1 | S5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917
217037821 | Ground Loop | GeoSmart Energy | S5SS024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833
217037822 | Ground Loop | GeoSmart Energy | S5SS036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833
217037823 | Ground Loop | GeoSmart Energy | S5SS048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925
217037824 | Ground Loop | GeoSmart Energy | S5SS060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917
217037826 | Ground Loop | GeoSmart Energy | S5SZ024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833
216802011 | Ground Loop | CARRIER | 50WT*048***6*(A-H)** |  | 51000 | 18 | 38000 | 4 | 4.25
216802012 | Ground Loop | CARRIER | 50WT*048***6*(J-R)** |  | 50500 | 17.5 | 37500 | 4 | 4.2083
216802013 | Ground Loop | CARRIER | 50WT*060***3*(A-H)** |  | 63000 | 18 | 48000 | 4 | 5.25
216802014 | Ground Loop | CARRIER | 50WT*060***3*(J-R)** |  | 62500 | 18 | 47500 | 4 | 5.2083
216802015 | Ground Loop | CARRIER | 50WT*060***5*(A-H)** |  | 63000 | 18 | 48000 | 4 | 5.25
216802016 | Ground Loop | CARRIER | 50WT*060***5*(J-R)** |  | 62500 | 18 | 47500 | 4 | 5.2083
216802017 | Ground Loop | CARRIER | 50WT*060***6*(A-H)** |  | 63000 | 18 | 48000 | 4 | 5.25
216802018 | Ground Loop | CARRIER | 50WT*060***6*(J-R)** |  | 62500 | 18 | 47500 | 4 | 5.2083
216802019 | Ground Loop | CARRIER | 50WT*070(G-K;N-R)**3*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333
216802021 | Ground Loop | CARRIER | 50WT*070(L/M/S/T)**3*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333
216802023 | Ground Loop | CARRIER | 50WT*070(G-K;N-R)**5*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333
216802025 | Ground Loop | CARRIER | 50WT*070(L/M/S/T)**5*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333
216802027 | Ground Loop | CARRIER | 50WT*070(G-K;N-R)**6*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333
216802029 | Ground Loop | CARRIER | 50WT*070(L/M/S/T)**6*(A-H)** |  | 70000 | 17 | 55000 | 3.8 | 5.8333
216979809 | Ground Loop | CARRIER | GCA24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
216979810 | Ground Loop | BRYANT | GCA24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
216979811 | Ground Loop | CARRIER | GCA24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979812 | Ground Loop | BRYANT | GCA24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979813 | Ground Loop | CARRIER | GCA24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
216979814 | Ground Loop | BRYANT | GCA24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
216979815 | Ground Loop | CARRIER | GCA24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979816 | Ground Loop | BRYANT | GCA24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979817 | Ground Loop | CARRIER | GCA36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25
216979818 | Ground Loop | BRYANT | GCA36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25
216979819 | Ground Loop | CARRIER | GCA36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216979820 | Ground Loop | BRYANT | GCA36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216979821 | Ground Loop | CARRIER | GCA48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25
216979822 | Ground Loop | BRYANT | GCA48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25
216979823 | Ground Loop | CARRIER | GCA48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083
216979824 | Ground Loop | BRYANT | GCA48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083
216979825 | Ground Loop | CARRIER | GCA60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25
216979826 | Ground Loop | BRYANT | GCA60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25
216979827 | Ground Loop | CARRIER | GCA60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083
216979828 | Ground Loop | BRYANT | GCA60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083
216979837 | Ground Loop | HEIL | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
216979838 | Ground Loop | ARCOAIRE | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
216979839 | Ground Loop | KEEPRITE | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
216979840 | Ground Loop | TEMPSTAR | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
216979841 | Ground Loop | COMFORTMAKER | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
216979842 | Ground Loop | DAY & NIGHT | HCR24V**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
216979843 | Ground Loop | HEIL | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979844 | Ground Loop | ARCOAIRE | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979845 | Ground Loop | KEEPRITE | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979846 | Ground Loop | TEMPSTAR | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979847 | Ground Loop | COMFORTMAKER | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979848 | Ground Loop | DAY & NIGHT | HCR24V**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979849 | Ground Loop | HEIL | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
216979850 | Ground Loop | ARCOAIRE | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
216979851 | Ground Loop | KEEPRITE | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
216979852 | Ground Loop | TEMPSTAR | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
963507 | Ground Loop | WaterFurnace | NLV/NXV080T*3 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167
963508 | Ground Loop | WaterFurnace | NLV/NXV080T*4 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167
963509 | Ground Loop | WaterFurnace | NLV/NXV080T*5 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167
963510 | Ground Loop | WaterFurnace | NLV/NXV095T*3 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167
963511 | Ground Loop | WaterFurnace | NLV/NXV095T*4 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167
963512 | Ground Loop | WaterFurnace | NLV/NXV095T*5 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167
963513 | Ground Loop | WaterFurnace | NLV/NXV120T*3 |  | 122000 | 18 | 83000 | 3.6 | 10.1667
963514 | Ground Loop | WaterFurnace | NLV/NXV120T*4 |  | 122000 | 18 | 83000 | 3.6 | 10.1667
963515 | Ground Loop | WaterFurnace | NLV/NXV120T*5 |  | 122000 | 18 | 83000 | 3.6 | 10.1667
1483426 | Ground Loop | BOSCH | BP012-1HZ/VT |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
1483428 | Ground Loop | BOSCH | BP024-1HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
1483429 | Ground Loop | BOSCH | BP030-1HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
202147710 | Ground Loop | HYDRON MODULE | HZS042*3***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917
202147711 | Ground Loop | TETCO | TZS042*3***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917
202147712 | Ground Loop | GEOCOMFORT | GZS060*3***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75
202147713 | Ground Loop | HYDRON MODULE | HZS060*3***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75
202147714 | Ground Loop | TETCO | TZS060*3***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75
202211042 | Ground Loop | WaterFurnace | URD038*0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
202211043 | Ground Loop | WaterFurnace | URD038*0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
202211044 | Ground Loop | WaterFurnace | URD038*0*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
202211045 | Ground Loop | WaterFurnace | URD038*3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
202211046 | Ground Loop | WaterFurnace | URD038*3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
202211047 | Ground Loop | WaterFurnace | URD038*3*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
202211048 | Ground Loop | WaterFurnace | URD049*0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
202211049 | Ground Loop | WaterFurnace | URD049*0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
202211050 | Ground Loop | WaterFurnace | URD049*0*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
206726878 | Ground Loop | GEOCOMFORT | GBT060 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917
206726879 | Ground Loop | HYDRON MODULE | HBT060 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917
206726880 | Ground Loop | TETCO | TBT060 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917
206726881 | Ground Loop | GEOCOMFORT | GBT060*2 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917
206726882 | Ground Loop | HYDRON MODULE | HBT060*2 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917
206726883 | Ground Loop | TETCO | TBT060*2 | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917
206900466 | Ground Loop | WaterFurnace | UDV084**4 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5
206900467 | Ground Loop | WaterFurnace | UDV096**4 |  | 98000 | 17 | 76000 | 3.8 | 8.1667
206900469 | Ground Loop | WaterFurnace | UDV084**3 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5
206900470 | Ground Loop | WaterFurnace | UDV084**5 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5
206900471 | Ground Loop | WaterFurnace | UDH084**3 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333
206900472 | Ground Loop | WaterFurnace | UDH084**4 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333
206900473 | Ground Loop | WaterFurnace | UDH084**5 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333
206900474 | Ground Loop | WaterFurnace | UDV096**3 |  | 98000 | 17 | 76000 | 3.8 | 8.1667
206900475 | Ground Loop | WaterFurnace | UDV096**5 |  | 98000 | 17 | 76000 | 3.8 | 8.1667
206900553 | Ground Loop | GEOSTAR | GDV084**3 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5
206900554 | Ground Loop | GEOSTAR | GDV084**4 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5
206900555 | Ground Loop | GEOSTAR | GDV084**5 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5
206900556 | Ground Loop | GEOSTAR | GDH084**3 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333
206900557 | Ground Loop | GEOSTAR | GDH084**4 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333
206900558 | Ground Loop | GEOSTAR | GDH084**5 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333
206900559 | Ground Loop | GEOSTAR | GDV096**3 |  | 98000 | 17 | 76000 | 3.8 | 8.1667
206900560 | Ground Loop | GEOSTAR | GDV096**4 |  | 98000 | 17 | 76000 | 3.8 | 8.1667
206900561 | Ground Loop | GEOSTAR | GDV096**5 |  | 98000 | 17 | 76000 | 3.8 | 8.1667
206900571 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV084**3 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5
206900572 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV084**4 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5
217642990 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S0**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
217642991 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S3**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
217642992 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S3**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
217642993 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S4**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
217642994 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S4**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
202146871 | Ground Loop | TETCO | TZT030*3 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625
202146872 | Ground Loop | GEOCOMFORT | GZT036 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583
202146873 | Ground Loop | GEOCOMFORT | GZT036*2 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583
202146874 | Ground Loop | GEOCOMFORT | GZT036*3 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583
202146875 | Ground Loop | GEOCOMFORT | GZT036*A |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583
202146876 | Ground Loop | HYDRON MODULE | HZT036 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583
202146877 | Ground Loop | HYDRON MODULE | HZT036*2 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583
202146878 | Ground Loop | HYDRON MODULE | HZT036*3 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583
202146879 | Ground Loop | HYDRON MODULE | HZT036*A |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583
202146880 | Ground Loop | TETCO | TZT036 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583
202146881 | Ground Loop | TETCO | TZT036*2 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583
202146882 | Ground Loop | TETCO | TZT036*3 |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583
202146883 | Ground Loop | TETCO | TZT036*A |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583
202146884 | Ground Loop | GEOCOMFORT | GZT042 |  | 43000 | 18 | 32900 | 3.6 | 3.5833
202146885 | Ground Loop | GEOCOMFORT | GZT042*2 |  | 43000 | 18 | 32900 | 3.6 | 3.5833
202146886 | Ground Loop | GEOCOMFORT | GZT042*3 |  | 43000 | 18 | 32900 | 3.6 | 3.5833
202146887 | Ground Loop | HYDRON MODULE | HZT042 |  | 43000 | 18 | 32900 | 3.6 | 3.5833
202146888 | Ground Loop | HYDRON MODULE | HZT042*2 |  | 43000 | 18 | 32900 | 3.6 | 3.5833
202146889 | Ground Loop | HYDRON MODULE | HZT042*3 |  | 43000 | 18 | 32900 | 3.6 | 3.5833
202146890 | Ground Loop | TETCO | TZT042 |  | 43000 | 18 | 32900 | 3.6 | 3.5833
202146891 | Ground Loop | TETCO | TZT042*2 |  | 43000 | 18 | 32900 | 3.6 | 3.5833
202146892 | Ground Loop | TETCO | TZT042*3 |  | 43000 | 18 | 32900 | 3.6 | 3.5833
202146893 | Ground Loop | GEOCOMFORT | GZT048 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583
202146894 | Ground Loop | GEOCOMFORT | GZT048*2 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583
202146895 | Ground Loop | GEOCOMFORT | GZT048*3 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583
202146896 | Ground Loop | GEOCOMFORT | GZT048*A |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583
202146897 | Ground Loop | HYDRON MODULE | HZT048 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583
202146898 | Ground Loop | HYDRON MODULE | HZT048*2 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583
202146899 | Ground Loop | HYDRON MODULE | HZT048*3 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583
202146900 | Ground Loop | HYDRON MODULE | HZT048*A |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583
202146901 | Ground Loop | TETCO | TZT048 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583
202146902 | Ground Loop | TETCO | TZT048*2 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583
202146903 | Ground Loop | TETCO | TZT048*3 |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583
202146913 | Ground Loop | GEOCOMFORT | GZS015 |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083
202146914 | Ground Loop | GEOCOMFORT | GZS015*A |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083
202146915 | Ground Loop | GEOCOMFORT | GZS015*****1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833
202146916 | Ground Loop | HYDRON MODULE | HZS015 |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083
202146917 | Ground Loop | HYDRON MODULE | HZS015*A |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083
202146918 | Ground Loop | HYDRON MODULE | HZS015*****1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833
202146919 | Ground Loop | TETCO | TZS015 |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083
202146920 | Ground Loop | TETCO | TZS015*A |  | 14500 | 17.1 | 11300 | 3.9 | 1.2083
202146921 | Ground Loop | TETCO | TZS015*****1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833
202146922 | Ground Loop | GEOCOMFORT | GZS017 |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917
202146923 | Ground Loop | GEOCOMFORT | GZS017*A |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917
202146924 | Ground Loop | GEOCOMFORT | GZS017*****1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833
202146925 | Ground Loop | GEOCOMFORT | GZS017*A***1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833
202146926 | Ground Loop | HYDRON MODULE | HZS017 |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917
206438719 | Ground Loop | BOSCH | EP009-1HZ/VT*-*****B |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167
206438720 | Ground Loop | BOSCH | EP009-2HZ/VT*-*****B |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167
206438721 | Ground Loop | BOSCH | EP012-0HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438723 | Ground Loop | BOSCH | EP012-0VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
217351799 | Ground Loop | ARCOAIRE | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833
217351801 | Ground Loop | ARCOAIRE | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325
217351802 | Ground Loop | ARCOAIRE | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167
217351803 | Ground Loop | ARCOAIRE | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333
217351811 | Ground Loop | COMFORTMAKER | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667
217351812 | Ground Loop | COMFORTMAKER | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167
217351815 | Ground Loop | COMFORTMAKER | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25
217351816 | Ground Loop | COMFORTMAKER | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667
217351817 | Ground Loop | COMFORTMAKER | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417
217351819 | Ground Loop | COMFORTMAKER | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417
217351820 | Ground Loop | COMFORTMAKER | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583
217351822 | Ground Loop | COMFORTMAKER | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583
217351823 | Ground Loop | COMFORTMAKER | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167
217351824 | Ground Loop | COMFORTMAKER | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167
217351825 | Ground Loop | COMFORTMAKER | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05
217351826 | Ground Loop | COMFORTMAKER | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833
217351828 | Ground Loop | COMFORTMAKER | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325
217351829 | Ground Loop | COMFORTMAKER | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167
217351830 | Ground Loop | COMFORTMAKER | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333
217351838 | Ground Loop | DAY & NIGHT | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667
217351839 | Ground Loop | DAY & NIGHT | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167
217351842 | Ground Loop | DAY & NIGHT | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25
7523958 | Ground Loop | TETCO | TVS018*****1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083
7523959 | Ground Loop | GEOCOMFORT | GVS018*A***1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083
7523960 | Ground Loop | HYDRON MODULE | HVS018*A***1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083
7523961 | Ground Loop | TETCO | TVS018*A***1 |  | 21700 | 22.2 | 15400 | 4 | 1.8083
216714620 | Ground Loop | GEOSTAR | G3A(V/H)024*S0**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
216714621 | Ground Loop | GEOSTAR | G3A(V/H)024*S0**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
216714622 | Ground Loop | GEOSTAR | G3A(V/H)024*S2**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
216714623 | Ground Loop | GEOSTAR | G3A(V/H)024*S2**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
216714624 | Ground Loop | GEOSTAR | G3A(V/H)024*S3**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
216714625 | Ground Loop | GEOSTAR | G3A(V/H)024*S3**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
216714626 | Ground Loop | GEOSTAR | G3A(V/H)024*S4**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
216714627 | Ground Loop | GEOSTAR | G3A(V/H)024*S4**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
202434167 | Ground Loop | BOSCH | LV036-3VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434168 | Ground Loop | BOSCH | LV036-4VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434169 | Ground Loop | BOSCH | LV036-2VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434173 | Ground Loop | BOSCH | LV036-3HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434174 | Ground Loop | BOSCH | LV036-4HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434175 | Ground Loop | BOSCH | LV036-2HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
216625872 | Ground Loop | GeoSmart Energy | S5A(V/H)072*D3**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216625873 | Ground Loop | GeoSmart Energy | S5A(V/H)072*D3**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216625874 | Ground Loop | GeoSmart Energy | S5A(V/H)072*D4**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216625875 | Ground Loop | GeoSmart Energy | S5A(V/H)072*D4**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216625876 | Ground Loop | GeoSmart Energy | S5A(V/H)072*S0**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216625877 | Ground Loop | GeoSmart Energy | S5A(V/H)072*S0**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216625878 | Ground Loop | GeoSmart Energy | S5A(V/H)072*S3**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
202084059 | Ground Loop | GEOCOMFORT | GZT024*2 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2
202084060 | Ground Loop | HYDRON MODULE | HZT024 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2
202084061 | Ground Loop | HYDRON MODULE | HZT024*2 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2
202084062 | Ground Loop | TETCO | TZT024 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2
202084063 | Ground Loop | TETCO | TZT024*2 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2
202132024 | Ground Loop | NORTHERN HEAT PUMP | N-D/H/V-A-038-* |  | 38100 | 17.47 | 32700 | 3.66 | 3.175
202132025 | Ground Loop | NORTHERN HEAT PUMP | N-D/H/V-A-050-* |  | 52600 | 17.1 | 45200 | 3.6 | 4.3833
202132026 | Ground Loop | NORTHERN HEAT PUMP | N-D/H/V-A-060-* |  | 61800 | 17.1 | 50700 | 3.6 | 5.15
202146863 | Ground Loop | GEOCOMFORT | GZT030 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625
202146864 | Ground Loop | GEOCOMFORT | GZT030*2 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625
202146865 | Ground Loop | GEOCOMFORT | GZT030*3 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625
202146866 | Ground Loop | HYDRON MODULE | HZT030 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625
202146867 | Ground Loop | HYDRON MODULE | HZT030*2 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625
202146868 | Ground Loop | HYDRON MODULE | HZT030*3 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625
202146869 | Ground Loop | TETCO | TZT030 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625
202146870 | Ground Loop | TETCO | TZT030*2 |  | 31500 | 17.5 | 23300 | 3.7 | 2.625
206347002 | Ground Loop | DAIKIN | WCCW*030*E***14* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333
206347003 | Ground Loop | DAIKIN | WCCW*030*F***14* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333
206347004 | Ground Loop | DAIKIN | WCCW*030*J***14* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333
206347005 | Ground Loop | DAIKIN | WCCW*030*K***14* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333
206347006 | Ground Loop | DAIKIN | WCCW*036*E***14* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667
206347007 | Ground Loop | DAIKIN | WCCW*036*F***14* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667
206347008 | Ground Loop | DAIKIN | WCCW*036*J***14* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667
206347009 | Ground Loop | DAIKIN | WCCW*036*K***14* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667
206347010 | Ground Loop | DAIKIN | WCCW*042*E***14* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675
206347011 | Ground Loop | DAIKIN | WCCW*042*F***14* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675
206347012 | Ground Loop | DAIKIN | WCCW*042*K***14* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675
206347013 | Ground Loop | DAIKIN | WCCW*048*E***14* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167
206347014 | Ground Loop | DAIKIN | WCCW*048*F***14* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167
206347015 | Ground Loop | DAIKIN | WCCW*048*K***14* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167
206347016 | Ground Loop | DAIKIN | WCCW*060*E***14* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417
206347017 | Ground Loop | DAIKIN | WCCW*060*F***14* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417
206347018 | Ground Loop | DAIKIN | WCCW*060*K***14* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417
206347036 | Ground Loop | DAIKIN | WCCW*015*J***14* |  | 16800 | 20.8 | 11500 | 3.8 | 1.4
206347038 | Ground Loop | DAIKIN | WCCW*015*E***14* |  | 17200 | 20.8 | 11500 | 4 | 1.4333
206422417 | Ground Loop | CENTURY | HBH/V015*W/K |  | 14800 | 18 | 11000 | 3.6 | 1.2333
206422418 | Ground Loop | COMFORT-AIRE | HBH/V015*W/K |  | 14800 | 18 | 11000 | 3.6 | 1.2333
206422419 | Ground Loop | CENTURY | HBH/V018*W/K |  | 19500 | 17.1 | 14100 | 3.7 | 1.625
206185640 | Ground Loop | DAIKIN | WGCH048E1*G/J*T |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917
206185641 | Ground Loop | DAIKIN | WGCH048E1*G/J*C |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917
206185646 | Ground Loop | DAIKIN | WGCH048F1*G/J*T |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917
206185647 | Ground Loop | DAIKIN | WGCH048F1*G/J*C |  | 49100 | 17.1 | 38400 | 3.7 | 4.0917
206438725 | Ground Loop | BOSCH | EP012-1HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438727 | Ground Loop | BOSCH | EP012-1VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438729 | Ground Loop | BOSCH | EP012-2HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438731 | Ground Loop | BOSCH | EP012-2VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438733 | Ground Loop | BOSCH | EP015-2HZ/VT*-*****B |  | 16200 | 19.8 | 11000 | 3.63 | 1.35
206438734 | Ground Loop | BOSCH | EP030-1HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
206438735 | Ground Loop | BOSCH | EP030-2HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
206438736 | Ground Loop | BOSCH | EP030-3HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
206438737 | Ground Loop | BOSCH | EP030-4HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
206438738 | Ground Loop | BOSCH | EP060-3HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
206438739 | Ground Loop | BOSCH | EP060-4HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
206438740 | Ground Loop | BOSCH | EP070-3HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
206438741 | Ground Loop | BOSCH | EP070-4HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
206438761 | Ground Loop | BOSCH | EP012-1HZ/VT*-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438762 | Ground Loop | BOSCH | EP015-1HZ/VT*-*****B |  | 16200 | 19.8 | 11000 | 3.63 | 1.35
206438763 | Ground Loop | BOSCH | EP060-1HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
206438764 | Ground Loop | BOSCH | EP070-1HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
214772070 | Ground Loop | TRANE | GEVK048B |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417
214772071 | Ground Loop | TRANE | GEVK0484 |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417
214772072 | Ground Loop | TRANE | GEVK060B |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083
214772073 | Ground Loop | TRANE | GEVK0604 |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083
214772074 | Ground Loop | TRANE | EXVK0097 |  | 9000 | 21.2 | 6100 | 3.91 | 0.75
214772075 | Ground Loop | TRANE | EXVK0127 |  | 11900 | 19.8 | 8500 | 3.78 | 0.99167
214772076 | Ground Loop | TRANE | EXVK0157 |  | 16200 | 18.7 | 11800 | 3.73 | 1.35
214772077 | Ground Loop | TRANE | EXVK0187 |  | 19700 | 20.8 | 14400 | 3.93 | 1.6417
214772078 | Ground Loop | TRANE | EXVK024B |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833
214772079 | Ground Loop | TRANE | EXVK0244 |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833
214772080 | Ground Loop | TRANE | EXVK0247 |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833
214772081 | Ground Loop | TRANE | EXVK030B |  | 31800 | 21.3 | 22900 | 4.17 | 2.65
214772082 | Ground Loop | TRANE | EXVK0304 |  | 31800 | 21.3 | 22900 | 4.17 | 2.65
214772083 | Ground Loop | TRANE | EXVK0307 |  | 31800 | 21.3 | 22900 | 4.17 | 2.65
214772084 | Ground Loop | TRANE | EXVK036B |  | 36600 | 20.8 | 27200 | 4.11 | 3.05
214772085 | Ground Loop | TRANE | EXVK0364 |  | 36600 | 20.8 | 27200 | 4.11 | 3.05
214772086 | Ground Loop | TRANE | EXVK0367 |  | 36600 | 20.8 | 27200 | 4.11 | 3.05
216419921 | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667
216419924 | Ground Loop | Whalen | WR(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167
216419941 | Ground Loop | Whalen | WZ(L/R/B/P/T/K)024A |  | 25000 | 18 | 18400 | 3.9 | 2.0833
216419946 | Ground Loop | Whalen | WZ(L/R/B/P/T/K)048A |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833
216419947 | Ground Loop | Whalen | WZ(L/R/B/P/T/K)060A |  | 61500 | 17.8 | 44600 | 3.7 | 5.125
216439574 | Ground Loop | GeoSmart Energy | S5TV036BD1**2 |  | 38000 | 20.1 | 29300 | 4.3 | 3.1667
216439575 | Ground Loop | GeoSmart Energy | S5TV048BD1**2 |  | 49100 | 18.5 | 38400 | 4.1 | 4.0917
216439576 | Ground Loop | GeoSmart Energy | S5TV060BD1**2 |  | 63700 | 17.9 | 47300 | 4 | 5.3083
216439577 | Ground Loop | GeoSmart Energy | S5TV072BD1**2 |  | 71500 | 17.8 | 56100 | 3.9 | 5.9583
216508982 | Ground Loop | ClimateMaster | SJ/PN024A | SKN024A | 23700 | 17.8 | 18300 | 3.8 | 1.975
216508983 | Ground Loop | ClimateMaster | SJ/PN036A | SKN036A | 36800 | 18.2 | 27300 | 3.9 | 3.0667
202146927 | Ground Loop | HYDRON MODULE | HZS017*A |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917
202146928 | Ground Loop | HYDRON MODULE | HZS017*****1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833
202146929 | Ground Loop | HYDRON MODULE | HZS017*A***1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833
202146930 | Ground Loop | TETCO | TZS017 |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917
202146931 | Ground Loop | TETCO | TZS017*A |  | 17900 | 17.1 | 13700 | 3.7 | 1.4917
202146932 | Ground Loop | TETCO | TZS017*****1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833
202146933 | Ground Loop | TETCO | TZS017*A***1 |  | 17800 | 18.2 | 13500 | 3.9 | 1.4833
207323895 | Ground Loop | WaterFurnace | NDS064H1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207323900 | Ground Loop | WaterFurnace | NDS038J1 | SAH036* | 36000 | 19 | 27900 | 4 | 3
207323901 | Ground Loop | WaterFurnace | NSZ022H1* | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583
207323902 | Ground Loop | WaterFurnace | NSZ030H1* | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05
207323903 | Ground Loop | WaterFurnace | NSZ036J1* | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55
207323904 | Ground Loop | WaterFurnace | NSZ042J1* | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15
207323905 | Ground Loop | WaterFurnace | NSZ048J1* | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417
207323906 | Ground Loop | WaterFurnace | NSZ048J1* | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417
207323907 | Ground Loop | WaterFurnace | NSZ060J1* | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
207323908 | Ground Loop | WaterFurnace | NSZ060J1* | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
207323909 | Ground Loop | WaterFurnace | NSZ070H1* | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417
207323910 | Ground Loop | WaterFurnace | NSZ022H1* | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583
207323911 | Ground Loop | WaterFurnace | NSZ030H1* | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05
207323912 | Ground Loop | WaterFurnace | NSZ036J1* | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55
207323913 | Ground Loop | WaterFurnace | NSZ042J1* | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15
207323914 | Ground Loop | WaterFurnace | NSZ070H1* | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417
207335135 | Ground Loop | GEOSTAR | 101/102J018**1*(1,4)***** |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
207335136 | Ground Loop | GEOSTAR | 101/102J030**1*(1,4)***** |  | 28100 | 22 | 20500 | 3.9 | 2.3417
207335137 | Ground Loop | GEOSTAR | 101/102K036**1*(1,2,4)***** |  | 33700 | 22 | 24400 | 4.2 | 2.8083
207335138 | Ground Loop | GEOSTAR | 101/102K042**1*(1,2,4)***** |  | 40700 | 21.7 | 28900 | 4 | 3.3917
207335139 | Ground Loop | GEOSTAR | 101/102K048**1*(1,2,4) |  | 45900 | 18.8 | 36400 | 4 | 3.825
207335140 | Ground Loop | GEOSTAR | 101/102K060**1*(1,4)****** |  | 62200 | 18.4 | 47900 | 4 | 5.1833
207335141 | Ground Loop | GEOSTAR | 101/102J070**1*(1,4)***** |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
207335142 | Ground Loop | GEOSTAR | 101/102J026**1*(1,4)***** |  | 26400 | 19.6 | 19500 | 4 | 2.2
207335143 | Ground Loop | GEOSTAR | 101/102K038**1*(1,2,4)***** |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207335144 | Ground Loop | GEOSTAR | 101/102K049**1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207335145 | Ground Loop | GEOSTAR | 101/102K064**1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207335146 | Ground Loop | GEOSTAR | 101/102J072**1*(1,4)***** |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207335147 | Ground Loop | GEOSTAR | 161/162K064**1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207335247 | Ground Loop | GEOSTAR | 101/102J022**1*(1,4)***** |  | 19200 | 18.7 | 19200 | 4 | 1.6
207335249 | Ground Loop | GEOSTAR | 161/162J026**1*(1,4)***** |  | 26400 | 19.6 | 19500 | 4 | 2.2
207335251 | Ground Loop | GEOSTAR | 161/162K038**1*(1,2,4)***** |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
217754564 | Ground Loop | DAIKIN | WSMH036K1*G/J*T |  | 38000 | 19.16 | 30000 | 3.89 | 3.1667
215824878 | Ground Loop | ICE AIR LLC | 8VSHPGE09**C |  | 11000 | 21.3 | 6500 | 3.64 | 0.91667
215824879 | Ground Loop | ICE AIR LLC | 8VSHPGE12**C |  | 13800 | 20.1 | 9000 | 3.7 | 1.15
215824880 | Ground Loop | ICE AIR LLC | 8VSHPGE15**C |  | 15000 | 17.5 | 10500 | 3.7 | 1.25
215824881 | Ground Loop | ICE AIR LLC | 8VSHPGE18**C |  | 19500 | 18.7 | 13400 | 3.63 | 1.625
215824882 | Ground Loop | ICE AIR LLC | 8VSHPGE24**C |  | 24800 | 18.4 | 17000 | 3.66 | 2.0667
215824883 | Ground Loop | ICE AIR LLC | 8VSHPGE30**C |  | 30000 | 17.3 | 21900 | 3.6 | 2.5
215824884 | Ground Loop | ICE AIR LLC | 8VSHPGE06**C |  | 8800 | 19.6 | 5800 | 3.6 | 0.73333
215827077 | Ground Loop | DAIKIN | WSLH072F1*G/J |  | 73500 | 18 | 53600 | 3.6 | 6.125
215827078 | Ground Loop | DAIKIN | WSLH072K1*G/J |  | 73500 | 18 | 53600 | 3.6 | 6.125
215827083 | Ground Loop | DAIKIN | WSLH096F1*G/J |  | 98000 | 17.9 | 72000 | 3.6 | 8.1667
215827084 | Ground Loop | DAIKIN | WSLH096K1*G/J |  | 98000 | 17.9 | 72000 | 3.6 | 8.1667
215827089 | Ground Loop | DAIKIN | WSLH120F1*G/J |  | 123000 | 17.1 | 90000 | 3.7 | 10.25
215827090 | Ground Loop | DAIKIN | WSLH120K1*G/J |  | 123000 | 17.1 | 90000 | 3.6 | 10.25
215827091 | Ground Loop | DAIKIN | WSLH120L1*G/J |  | 123000 | 17.1 | 90000 | 3.6 | 10.25
215827092 | Ground Loop | DAIKIN | WSLV072F1*G/J |  | 77000 | 19 | 53000 | 3.7 | 6.4167
215827094 | Ground Loop | DAIKIN | WSLV072K1*G/J |  | 77000 | 19 | 53000 | 3.7 | 6.4167
215827096 | Ground Loop | DAIKIN | WSLV072L1*G/J |  | 77000 | 19 | 53000 | 3.6 | 6.4167
215827098 | Ground Loop | DAIKIN | WSLV096F1*G/J |  | 99500 | 19.4 | 74100 | 3.9 | 8.2917
215827100 | Ground Loop | DAIKIN | WSLV096K1*G/J |  | 99500 | 19.4 | 74100 | 3.9 | 8.2917
215827102 | Ground Loop | DAIKIN | WSLV096L1*G/J |  | 99500 | 18.7 | 74100 | 3.7 | 8.2917
215827106 | Ground Loop | DAIKIN | WSLV120K1*G/J |  | 124600 | 17 | 95600 | 3.6 | 10.3833
215832281 | Ground Loop | HYDROTECH | WSH6009D* |  | 9500 | 18.9 | 6500 | 3.6 | 0.79167
215832282 | Ground Loop | HYDROTECH | WSH6012D* |  | 12000 | 17.9 | 8500 | 3.8 | 1
215832283 | Ground Loop | HYDROTECH | WSH6018D* |  | 19000 | 18 | 12000 | 3.6 | 1.5833
215832284 | Ground Loop | HYDROTECH | WSH6024D* |  | 26000 | 18.4 | 17500 | 3.6 | 2.1667
216625656 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S3**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625657 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S3**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625658 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S4**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625659 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S4**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625660 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625661 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625662 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D0**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625663 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625664 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625665 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D2**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625666 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625667 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625668 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D3**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625669 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625670 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625671 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*D4**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625672 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625673 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625674 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S0**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625675 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625676 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625677 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S2**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625678 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625679 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625680 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S3**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625681 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625682 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625683 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036*S4**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625684 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D0**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625685 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D0**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625686 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D0**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625687 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D2**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625688 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D3**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625689 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D3**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625690 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D3**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625691 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D4**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625692 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D4**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625693 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*D4**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625694 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625695 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625696 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S0**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625697 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S2**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625698 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625699 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625700 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S3**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625701 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625702 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625703 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042*S4**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
202330518 | Ground Loop | AAON, Inc. | M2-003-2-H-BCBC-V0-10-000-A |  | 41900 | 18.4 | 28900 | 3.6 | 3.4917
202330522 | Ground Loop | AAON, Inc. | M2-003-3-H-BCBC-V0-10-000-A |  | 41900 | 18.4 | 28900 | 3.6 | 3.4917
202330526 | Ground Loop | AAON, Inc. | M2-003-4-H-BCBC-V0-10-000-A |  | 41900 | 18.4 | 28900 | 3.6 | 3.4917
202330529 | Ground Loop | AAON, Inc. | M2-004-1-H-BCAC-V0-10-000-A |  | 50000 | 18.3 | 35000 | 3.6 | 4.1667
202330530 | Ground Loop | AAON, Inc. | M2-004-1-H-BCBC-V0-10-000-A |  | 51900 | 18.8 | 35200 | 3.8 | 4.325
202330531 | Ground Loop | AAON, Inc. | M2-004-1-H-DCAC-S0-10-000-A |  | 49200 | 17.9 | 34800 | 3.6 | 4.1
202330532 | Ground Loop | AAON, Inc. | M2-004-1-H-DCBC-S0-10-000-A |  | 50900 | 18.2 | 35100 | 3.6 | 4.2417
202330533 | Ground Loop | AAON, Inc. | M2-004-2-H-BCAC-V0-10-000-A |  | 50000 | 18.3 | 35000 | 3.6 | 4.1667
202330534 | Ground Loop | AAON, Inc. | M2-004-2-H-BCBC-V0-10-000-A |  | 51900 | 18.8 | 35200 | 3.8 | 4.325
202330535 | Ground Loop | AAON, Inc. | M2-004-2-H-DCAC-S0-10-000-A |  | 49200 | 17.9 | 34800 | 3.6 | 4.1
202330536 | Ground Loop | AAON, Inc. | M2-004-2-H-DCBC-S0-10-000-A |  | 50900 | 18.2 | 35100 | 3.6 | 4.2417
202330537 | Ground Loop | AAON, Inc. | M2-004-3-H-BCAC-V0-10-000-A |  | 50000 | 18.3 | 35000 | 3.6 | 4.1667
202330538 | Ground Loop | AAON, Inc. | M2-004-3-H-BCBC-V0-10-000-A |  | 51900 | 18.8 | 35200 | 3.8 | 4.325
202330539 | Ground Loop | AAON, Inc. | M2-004-3-H-DCAC-S0-10-000-A |  | 49200 | 17.9 | 34800 | 3.6 | 4.1
202330540 | Ground Loop | AAON, Inc. | M2-004-3-H-DCBC-S0-10-000-A |  | 50900 | 18.2 | 35100 | 3.6 | 4.2417
202330541 | Ground Loop | AAON, Inc. | M2-004-4-H-BCAC-V0-10-000-A |  | 50000 | 18.3 | 35000 | 3.6 | 4.1667
215268741 | Ground Loop | WaterFurnace | V5A(V/H)024*D0**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
215268742 | Ground Loop | WaterFurnace | V5A(V/H)024*D2**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
215268743 | Ground Loop | WaterFurnace | V5A(V/H)024*D3**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
215268744 | Ground Loop | WaterFurnace | V5A(V/H)024*D4**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
215268745 | Ground Loop | WaterFurnace | V5A(V/H)030*D0**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
215268746 | Ground Loop | WaterFurnace | V5A(V/H)030*D3**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
215268747 | Ground Loop | WaterFurnace | V5A(V/H)030*D0**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
215268748 | Ground Loop | WaterFurnace | V5A(V/H)030*D3**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
215268749 | Ground Loop | WaterFurnace | V5A(V/H)036*D0**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
215268750 | Ground Loop | WaterFurnace | V5A(V/H)036*D3**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
215268751 | Ground Loop | WaterFurnace | V5A(V/H)036*D0**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
215268752 | Ground Loop | WaterFurnace | V5A(V/H)036*D3**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
215268753 | Ground Loop | WaterFurnace | V5A(V/H)036*D0**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
215268754 | Ground Loop | WaterFurnace | V5A(V/H)036*D3**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
215268755 | Ground Loop | WaterFurnace | V5A(V/H)042*D0**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
215268756 | Ground Loop | WaterFurnace | V5A(V/H)042*D3**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
215268757 | Ground Loop | WaterFurnace | V5A(V/H)042*D0**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
215268758 | Ground Loop | WaterFurnace | V5A(V/H)042*D3**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
215268759 | Ground Loop | WaterFurnace | V5A(V/H)042*D0**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
215268760 | Ground Loop | WaterFurnace | V5A(V/H)042*D3**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
215268761 | Ground Loop | WaterFurnace | V5A(V/H)048*D0**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
215268762 | Ground Loop | WaterFurnace | V5A(V/H)048*D3**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
215268763 | Ground Loop | WaterFurnace | V5A(V/H)048*D0**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
215268764 | Ground Loop | WaterFurnace | V5A(V/H)048*D3**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
215268765 | Ground Loop | WaterFurnace | V5A(V/H)048*D0**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
215268766 | Ground Loop | WaterFurnace | V5A(V/H)048*D3**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
215268767 | Ground Loop | WaterFurnace | V5A(V/H)060*D0**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
215268768 | Ground Loop | WaterFurnace | V5A(V/H)060*D3**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
215268769 | Ground Loop | WaterFurnace | V5A(V/H)060*D0**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
215268770 | Ground Loop | WaterFurnace | V5A(V/H)060*D3**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
215268771 | Ground Loop | WaterFurnace | V5A(V/H)072*D0**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
215268772 | Ground Loop | WaterFurnace | V5A(V/H)072*D3**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
215268773 | Ground Loop | WaterFurnace | V5A(V/H)072*D0**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
215268774 | Ground Loop | WaterFurnace | V5A(V/H)072*D3**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
215268775 | Ground Loop | WaterFurnace | V5A(V/H)030*D2**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
215268776 | Ground Loop | WaterFurnace | V5A(V/H)030*D4**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
215268777 | Ground Loop | WaterFurnace | V5A(V/H)030*D2**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
215268778 | Ground Loop | WaterFurnace | V5A(V/H)030*D4**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
215268779 | Ground Loop | WaterFurnace | V5A(V/H)036*D2**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
215268780 | Ground Loop | WaterFurnace | V5A(V/H)036*D4**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
215268781 | Ground Loop | WaterFurnace | V5A(V/H)036*D2**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
215268782 | Ground Loop | WaterFurnace | V5A(V/H)036*D4**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
215268783 | Ground Loop | WaterFurnace | V5A(V/H)036*D2**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
215268784 | Ground Loop | WaterFurnace | V5A(V/H)036*D4**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
215268785 | Ground Loop | WaterFurnace | V5A(V/H)042*D4**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
215268786 | Ground Loop | WaterFurnace | V5A(V/H)042*D2**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
215268787 | Ground Loop | WaterFurnace | V5A(V/H)042*D4**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
215268788 | Ground Loop | WaterFurnace | V5A(V/H)042*D4**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
217351731 | Ground Loop | CARRIER | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 25400 | 18.1 | 18400 | 4 | 2.1167
217351734 | Ground Loop | CARRIER | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 39000 | 18.5 | 27400 | 3.7 | 3.25
217351735 | Ground Loop | CARRIER | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 38000 | 18.1 | 26800 | 3.7 | 3.1667
217351736 | Ground Loop | CARRIER | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 48500 | 17.1 | 37800 | 4 | 4.0417
217351738 | Ground Loop | CARRIER | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 60500 | 17.6 | 47000 | 3.7 | 5.0417
217351739 | Ground Loop | CARRIER | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 59500 | 17.3 | 46000 | 3.7 | 4.9583
217351741 | Ground Loop | CARRIER | GZ024SA*C******1 | CAAMP2***AMA | 25900 | 17.5 | 18900 | 3.8 | 2.1583
217351742 | Ground Loop | CARRIER | GZ024SA*N******1 | CAAMP2***AMA | 25400 | 17.1 | 18500 | 3.7 | 2.1167
217351743 | Ground Loop | CARRIER | GZ036SA*C******1 | CAAMP3***AMA | 37400 | 17.7 | 27600 | 3.6 | 3.1167
217351744 | Ground Loop | CARRIER | GZ036SA*N******1 | CAAMP3***AMA | 36600 | 17.4 | 27100 | 3.6 | 3.05
217351745 | Ground Loop | CARRIER | GZ048SA*C******1 | CAAMP4***AMA | 49000 | 17.1 | 37900 | 3.9 | 4.0833
217351747 | Ground Loop | CARRIER | GZ060SA*C******1 | CAAMP6***AMA | 63900 | 17.7 | 48300 | 3.8 | 5.325
217351748 | Ground Loop | CARRIER | GZ060SA*N******1 | CAAMP6***AMA | 62600 | 17.3 | 47300 | 3.7 | 5.2167
217351749 | Ground Loop | CARRIER | GZ072SA*C******1 | CAAMP6***AMA | 70000 | 17.5 | 55200 | 3.6 | 5.8333
215310991 | Ground Loop | GeoSmart Energy | S7A(V/H)036BV1**2 |  | 35800 | 18.1 | 32900 | 3.8 | 2.9833
215310992 | Ground Loop | GeoSmart Energy | S7A(V/H)048BV1**2 |  | 45000 | 18.9 | 42000 | 3.6 | 3.75
217351843 | Ground Loop | DAY & NIGHT | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667
217351844 | Ground Loop | DAY & NIGHT | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417
217351846 | Ground Loop | DAY & NIGHT | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417
217351847 | Ground Loop | DAY & NIGHT | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583
217351849 | Ground Loop | DAY & NIGHT | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583
217351850 | Ground Loop | DAY & NIGHT | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167
217351851 | Ground Loop | DAY & NIGHT | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167
217351852 | Ground Loop | DAY & NIGHT | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05
217351853 | Ground Loop | DAY & NIGHT | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833
217351855 | Ground Loop | DAY & NIGHT | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325
217351856 | Ground Loop | DAY & NIGHT | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167
217351857 | Ground Loop | DAY & NIGHT | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333
217351865 | Ground Loop | HEIL | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667
217351866 | Ground Loop | HEIL | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167
217351869 | Ground Loop | HEIL | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25
217351870 | Ground Loop | HEIL | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667
217351871 | Ground Loop | HEIL | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417
217351873 | Ground Loop | HEIL | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417
217351874 | Ground Loop | HEIL | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583
217351876 | Ground Loop | HEIL | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583
217351877 | Ground Loop | HEIL | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167
217351878 | Ground Loop | HEIL | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167
217351879 | Ground Loop | HEIL | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05
217351880 | Ground Loop | HEIL | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833
215224495 | Ground Loop | FHP | CF018-2VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224496 | Ground Loop | FHP | CF018-2VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224497 | Ground Loop | FHP | CF024-2VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224498 | Ground Loop | FHP | CF024-4VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224499 | Ground Loop | FHP | CF024-2VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224500 | Ground Loop | FHP | CF024-4VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
216801983 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**3*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125
216801984 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**3*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216801985 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**3*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125
216801986 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**3*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216801987 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**4*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125
216801988 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**4*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216801989 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**4*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125
216801990 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**4*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216801991 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**5*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125
216801992 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**5*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216801993 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**5*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125
216801994 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**5*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216801995 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**6*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125
216801996 | Ground Loop | CARRIER | 50WT*024(G-K;N-R)**6*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216801997 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**6*(A-H)** |  | 25500 | 18.5 | 18000 | 4 | 2.125
216801998 | Ground Loop | CARRIER | 50WT*024(L/M/S/T)**6*(J-R)** |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216801999 | Ground Loop | CARRIER | 50WT*036***3*(A-H)** |  | 39000 | 18.5 | 28000 | 4 | 3.25
216802000 | Ground Loop | CARRIER | 50WT*036***3*(J-R)** |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216802001 | Ground Loop | CARRIER | 50WT*036***4*(A-H)** |  | 39000 | 18.5 | 28000 | 4 | 3.25
216802002 | Ground Loop | CARRIER | 50WT*036***4*(J-R)** |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216802003 | Ground Loop | CARRIER | 50WT*036***5*(A-H)** |  | 39000 | 18.5 | 28000 | 4 | 3.25
216802004 | Ground Loop | CARRIER | 50WT*036***5*(J-R)** |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216802005 | Ground Loop | CARRIER | 50WT*036***6*(A-H)** |  | 39000 | 18.5 | 28000 | 4 | 3.25
216802006 | Ground Loop | CARRIER | 50WT*036***6*(J-R)** |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216802007 | Ground Loop | CARRIER | 50WT*048***3*(A-H)** |  | 51000 | 18 | 38000 | 4 | 4.25
216802008 | Ground Loop | CARRIER | 50WT*048***3*(J-R)** |  | 50500 | 17.5 | 37500 | 4 | 4.2083
216802009 | Ground Loop | CARRIER | 50WT*048***5*(A-H)** |  | 51000 | 18 | 38000 | 4 | 4.25
216802010 | Ground Loop | CARRIER | 50WT*048***5*(J-R)** |  | 50500 | 17.5 | 37500 | 4 | 4.2083
209180331 | Ground Loop | HYDROTECH | WSV6036B* |  | 37000 | 18 | 28000 | 3.6 | 3.0833
209180332 | Ground Loop | HYDROTECH | WSV6042B* |  | 42000 | 18.5 | 30000 | 3.6 | 3.5
209180334 | Ground Loop | HYDROTECH | WSV6048B* |  | 51000 | 17.7 | 37000 | 3.6 | 4.25
212509301 | Ground Loop | AE Air | WSH6060AN* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083
215746915 | Ground Loop | TRANE | GSK036A3 |  | 41280 | 22.1 | 29804 | 4.28 | 3.44
215746916 | Ground Loop | TRANE | GSK048A3 |  | 55159 | 20.4 | 39719 | 4.14 | 4.5966
215746918 | Ground Loop | TRANE | GSK060A3 |  | 66724 | 20.1 | 47737 | 3.95 | 5.5603
215746919 | Ground Loop | TRANE | GSK072A3 |  | 86809 | 21.4 | 59774 | 4.1 | 7.2341
215746920 | Ground Loop | TRANE | GSK090A3 |  | 102892 | 20.6 | 67696 | 3.86 | 8.5743
213154446 | Ground Loop | GeoSmart Energy | GTS064*1******K | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
213154447 | Ground Loop | GeoSmart Energy | GTS038*1******K | SAH036* | 36000 | 19 | 27900 | 4 | 3
213154448 | Ground Loop | GeoSmart Energy | GTS038*1******K | SRAA036* | 36000 | 19 | 27900 | 4 | 3
213154454 | Ground Loop | GeoSmart Energy | GTZ026*1******K | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
213154455 | Ground Loop | GeoSmart Energy | GTZ026*1******K | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
213154456 | Ground Loop | GeoSmart Energy | GTZ038*1******K | SAH036* | 36000 | 19 | 27900 | 4 | 3
213154457 | Ground Loop | GeoSmart Energy | GTZ038*1******K | SRAA036* | 36000 | 19 | 27900 | 4 | 3
213154458 | Ground Loop | GeoSmart Energy | GTZ049*1******K | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
213154459 | Ground Loop | GeoSmart Energy | GTZ049*1******K | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
213154460 | Ground Loop | GeoSmart Energy | GTZ064*1******K | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
213154461 | Ground Loop | GeoSmart Energy | GTZ064*1******K | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
213154465 | Ground Loop | GeoSmart Energy | GS018**1*1********L |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
213154466 | Ground Loop | GeoSmart Energy | GS022**1*1********L |  | 19200 | 18.7 | 15000 | 4 | 1.6
213154467 | Ground Loop | GeoSmart Energy | GS030**1*1********L |  | 28100 | 22 | 20500 | 3.9 | 2.3417
213154468 | Ground Loop | GeoSmart Energy | GS036**1*1********L |  | 33700 | 22 | 24400 | 4.2 | 2.8083
213154469 | Ground Loop | GeoSmart Energy | GS042**1*1********L |  | 40700 | 21.7 | 28900 | 4 | 3.3917
213154470 | Ground Loop | GeoSmart Energy | GS048**1*1********L |  | 45900 | 18.8 | 36400 | 4 | 3.825
213154471 | Ground Loop | GeoSmart Energy | GS060**1*1********L |  | 62200 | 18.4 | 47900 | 4 | 5.1833
213154472 | Ground Loop | GeoSmart Energy | GS070**1*1********L |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
213154473 | Ground Loop | GeoSmart Energy | GT026**1*1********L |  | 26400 | 19.6 | 19500 | 4 | 2.2
213154474 | Ground Loop | GeoSmart Energy | GT038**1*1********L |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
213154475 | Ground Loop | GeoSmart Energy | GT049**1*1********L |  | 50800 | 19.3 | 38200 | 4 | 4.2333
213154476 | Ground Loop | GeoSmart Energy | GT064**1*1********L |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
213154477 | Ground Loop | GeoSmart Energy | GT072**1*1********L |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
216726191 | Ground Loop | DAIKIN | WSRC009*E*G/J |  | 9100 | 18.1 | 6500 | 3.6 | 0.75833
216726195 | Ground Loop | DAIKIN | WSRC015*E*G/J |  | 15400 | 18.9 | 11200 | 3.6 | 1.2833
202434436 | Ground Loop | FHP | LV036-1VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434437 | Ground Loop | FHP | LV036-3VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434438 | Ground Loop | FHP | LV036-4VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
8560948 | Ground Loop | TETCO | TVS015*****1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333
8560949 | Ground Loop | GEOCOMFORT | GVS015*A***1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333
8560950 | Ground Loop | HYDRON MODULE | HVS015*A***1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333
8560951 | Ground Loop | TETCO | TVS015*A***1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333
211594119 | Ground Loop | TRANE | GEHG009A |  | 8900 | 17.8 | 6700 | 3.7 | 0.74167
211594120 | Ground Loop | TRANE | GEHG012A |  | 12100 | 17.6 | 9400 | 3.7 | 1.0083
211594121 | Ground Loop | TRANE | GEHG015A |  | 15500 | 17.4 | 12300 | 3.6 | 1.2917
211594122 | Ground Loop | TRANE | GEHG018A |  | 18100 | 17.7 | 14300 | 3.6 | 1.5083
216772574 | Ground Loop | Enertech | EYT024* |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583
216772575 | Ground Loop | Enertech | EYT036* |  | 39700 | 21 | 27900 | 4.3 | 3.3083
216772576 | Ground Loop | Enertech | EYT048* |  | 51900 | 19.2 | 36700 | 4.1 | 4.325
216772579 | Ground Loop | Enertech | EZT024* |  | 26400 | 18.8 | 18400 | 3.9 | 2.2
216772580 | Ground Loop | Enertech | EZT030* |  | 32625 | 17.6 | 24400 | 3.7 | 2.7188
216772581 | Ground Loop | Enertech | EZT036* |  | 36725 | 18.9 | 28375 | 3.84 | 3.0604
216772582 | Ground Loop | Enertech | EZT042* |  | 44750 | 18.8 | 32900 | 3.67 | 3.7292
216772583 | Ground Loop | Enertech | EZT048* |  | 48700 | 17.3 | 36900 | 3.7 | 4.0583
216772584 | Ground Loop | Enertech | EZT060* |  | 58875 | 17.4 | 44550 | 3.6 | 4.9062
216772586 | Ground Loop | Enertech | EVS015* |  | 16725 | 24.1 | 11500 | 4.3 | 1.3938
216772588 | Ground Loop | Enertech | EBT060* | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917
216772590 | Ground Loop | Enertech | EVT060* |  | 60900 | 17.6 | 46700 | 3.8 | 5.075
216772591 | Ground Loop | Enertech | EYT060* |  | 63100 | 18.7 | 49100 | 4 | 5.2583
216772592 | Ground Loop | Enertech | EZS015* |  | 14525 | 18.6 | 11200 | 3.9 | 1.2104
216772593 | Ground Loop | Enertech | EZS017* |  | 17300 | 17 | 12825 | 3.61 | 1.4417
216772594 | Ground Loop | Enertech | EZS018* |  | 20400 | 21.5 | 14100 | 3.86 | 1.7
216772596 | Ground Loop | Enertech | EYT072* |  | 70300 | 17.1 | 57800 | 3.8 | 5.8583
214772106 | Ground Loop | TRANE | GEHK0244 |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167
214772107 | Ground Loop | TRANE | GEHK0247 |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167
214772108 | Ground Loop | TRANE | GEHK030B |  | 30000 | 18.2 | 23700 | 3.66 | 2.5
214772109 | Ground Loop | TRANE | GEHK0304 |  | 30000 | 18.2 | 23700 | 3.66 | 2.5
214772110 | Ground Loop | TRANE | GEHK0307 |  | 30000 | 18.2 | 23700 | 3.66 | 2.5
214772116 | Ground Loop | TRANE | GEHK048B |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417
214772117 | Ground Loop | TRANE | GEHK0484 |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417
214772118 | Ground Loop | TRANE | GEHK060B |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083
214772119 | Ground Loop | TRANE | GEHK0604 |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083
214772120 | Ground Loop | TRANE | EXHK0097 |  | 9000 | 21.2 | 6100 | 3.91 | 0.75
214772121 | Ground Loop | TRANE | EXHK0127 |  | 11900 | 19.8 | 8500 | 3.78 | 0.99167
214772122 | Ground Loop | TRANE | EXHK0157 |  | 16200 | 18.7 | 11800 | 3.73 | 1.35
214772123 | Ground Loop | TRANE | EXHK0187 |  | 19700 | 20.8 | 14400 | 3.93 | 1.6417
214772124 | Ground Loop | TRANE | EXHK024B |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833
214772125 | Ground Loop | TRANE | EXHK0244 |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833
214772126 | Ground Loop | TRANE | EXHK0247 |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833
214772127 | Ground Loop | TRANE | EXHK030B |  | 31800 | 21.3 | 22900 | 4.17 | 2.65
214772128 | Ground Loop | TRANE | EXHK0304 |  | 31800 | 21.3 | 22900 | 4.17 | 2.65
214772129 | Ground Loop | TRANE | EXHK0307 |  | 31800 | 21.3 | 22900 | 4.17 | 2.65
214772130 | Ground Loop | TRANE | EXHK036B |  | 36600 | 20.8 | 27200 | 4.11 | 3.05
214772131 | Ground Loop | TRANE | EXHK0364 |  | 36600 | 20.8 | 27200 | 4.11 | 3.05
214772132 | Ground Loop | TRANE | EXHK0367 |  | 36600 | 20.8 | 27200 | 4.11 | 3.05
214772133 | Ground Loop | TRANE | EXHK042B |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083
214772134 | Ground Loop | TRANE | EXHK0424 |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083
214772135 | Ground Loop | TRANE | EXHK048B |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083
214772136 | Ground Loop | TRANE | EXHK0484 |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083
214772137 | Ground Loop | TRANE | EXHK060B |  | 62700 | 19.7 | 45200 | 3.82 | 5.225
214772138 | Ground Loop | TRANE | EXHK0604 |  | 62700 | 19.7 | 45200 | 3.82 | 5.225
214772139 | Ground Loop | TRANE | EXHK070B |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917
214772140 | Ground Loop | TRANE | EXHK0704 |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917
214772141 | Ground Loop | TRANE | DXHK024A |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417
214772142 | Ground Loop | TRANE | DXHK036A |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167
202330572 | Ground Loop | AAON, Inc. | M2-006-4-H-BCBC-V0-10-000-A |  | 68700 | 17.3 | 43100 | 3.6 | 5.725
202350417 | Ground Loop | AAON, Inc. | RN-009-2-0-BCAY-V0-10-000-A |  | 101100 | 19.1 | 69000 | 3.9 | 8.425
202350418 | Ground Loop | AAON, Inc. | RN-009-3-0-BCAY-V0-10-000-A |  | 101100 | 19.1 | 69000 | 3.9 | 8.425
202350419 | Ground Loop | AAON, Inc. | RN-009-4-0-BCAY-V0-10-000-A |  | 101100 | 19.1 | 69000 | 3.9 | 8.425
202350429 | Ground Loop | AAON, Inc. | RN-011-2-0-BCAY-V0-10-000-A |  | 125300 | 17.2 | 89400 | 3.6 | 10.4417
202350430 | Ground Loop | AAON, Inc. | RN-011-3-0-BCAY-V0-10-000-A |  | 125300 | 17.2 | 89400 | 3.6 | 10.4417
202350431 | Ground Loop | AAON, Inc. | RN-011-4-0-BCAY-V0-10-000-A |  | 125300 | 17.2 | 89400 | 3.6 | 10.4417
202350444 | Ground Loop | AAON, Inc. | M2-007-2-H-ACAC-C0-10-000-A |  | 80400 | 17.4 | 52600 | 3.6 | 6.7
202350445 | Ground Loop | AAON, Inc. | M2-007-2-H-ACBC-C0-10-000-A |  | 83500 | 17.7 | 52900 | 3.7 | 6.9583
202350446 | Ground Loop | AAON, Inc. | M2-007-2-H-BCAC-V0-10-000-A |  | 73700 | 17.3 | 54800 | 3.7 | 6.1417
202350447 | Ground Loop | AAON, Inc. | M2-007-2-H-BCBC-V0-10-000-A |  | 78000 | 18.2 | 53800 | 3.7 | 6.5
202350448 | Ground Loop | AAON, Inc. | M2-007-3-H-ACAC-C0-10-000-A |  | 80400 | 17.4 | 52600 | 3.6 | 6.7
202350449 | Ground Loop | AAON, Inc. | M2-007-3-H-ACBC-C0-10-000-A |  | 83500 | 17.7 | 52900 | 3.7 | 6.9583
202350450 | Ground Loop | AAON, Inc. | M2-007-3-H-BCAC-V0-10-000-A |  | 73700 | 17.3 | 54800 | 3.7 | 6.1417
202350451 | Ground Loop | AAON, Inc. | M2-007-3-H-BCBC-V0-10-000-A |  | 78000 | 18.2 | 53800 | 3.7 | 6.5
202350452 | Ground Loop | AAON, Inc. | M2-007-4-H-ACAC-C0-10-000-A |  | 80400 | 17.4 | 52600 | 3.6 | 6.7
202350453 | Ground Loop | AAON, Inc. | M2-007-4-H-ACBC-C0-10-000-A |  | 83500 | 17.7 | 52900 | 3.7 | 6.9583
202350454 | Ground Loop | AAON, Inc. | M2-007-4-H-BCAC-V0-10-000-A |  | 73700 | 17.3 | 54800 | 3.7 | 6.1417
202350455 | Ground Loop | AAON, Inc. | M2-007-4-H-BCBC-V0-10-000-A |  | 78000 | 18.2 | 53800 | 3.7 | 6.5
215224293 | Ground Loop | BOSCH-GEO | RF007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224294 | Ground Loop | BOSCH-GEO | RF007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224295 | Ground Loop | BOSCH-GEO | RF009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
215224296 | Ground Loop | BOSCH-GEO | RF009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
215224297 | Ground Loop | BOSCH-GEO | RF012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224298 | Ground Loop | BOSCH-GEO | RF012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224299 | Ground Loop | BOSCH-GEO | RF015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083
215224300 | Ground Loop | BOSCH-GEO | RF015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917
215224301 | Ground Loop | BOSCH-GEO | RF018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224302 | Ground Loop | BOSCH-GEO | RF018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224305 | Ground Loop | BOSCH-GEO | RF024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224306 | Ground Loop | BOSCH-GEO | RF024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215399792 | Ground Loop | DAIKIN | WSMV024J1*G/J*T |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333
215399793 | Ground Loop | DAIKIN | WSMV024K3*G/J*T |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333
215399796 | Ground Loop | DAIKIN | WSMV024J1*G/J*C |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333
215399797 | Ground Loop | DAIKIN | WSMV024K3*G/J*C |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333
215399812 | Ground Loop | DAIKIN | WSMV036J1*G/J*P |  | 37600 | 18.26 | 28000 | 3.6 | 3.1333
215399816 | Ground Loop | DAIKIN | WSMV036J1*G/J*T |  | 37500 | 18.76 | 28000 | 3.72 | 3.125
215399817 | Ground Loop | DAIKIN | WSMV036K3*G/J*T |  | 37100 | 19.16 | 27700 | 3.72 | 3.0917
215399820 | Ground Loop | DAIKIN | WSMV036J1*G/J*C |  | 37500 | 18.76 | 28000 | 3.72 | 3.125
215399821 | Ground Loop | DAIKIN | WSMV036K3*G/J*C |  | 37100 | 19.16 | 27700 | 3.72 | 3.0917
215399825 | Ground Loop | DAIKIN | WSMV042K3*G/J*T |  | 42600 | 19.67 | 29700 | 3.63 | 3.55
215399827 | Ground Loop | DAIKIN | WSMV042K3*G/J*C |  | 42600 | 19.67 | 29700 | 3.63 | 3.55
215399830 | Ground Loop | DAIKIN | WSMV048K3*G/J*P |  | 50200 | 18.61 | 37100 | 3.64 | 4.1833
215399831 | Ground Loop | DAIKIN | WSMV048L3*G/J*P |  | 49700 | 18.61 | 36700 | 3.64 | 4.1417
215399834 | Ground Loop | DAIKIN | WSMV048K3*G/J*T |  | 49800 | 19.09 | 36400 | 3.75 | 4.15
215399835 | Ground Loop | DAIKIN | WSMV048L3*G/J*T |  | 49300 | 19.09 | 36000 | 3.75 | 4.1083
215399838 | Ground Loop | DAIKIN | WSMV048K3*G/J*C |  | 49800 | 19.09 | 36400 | 3.75 | 4.15
215399839 | Ground Loop | DAIKIN | WSMV048L3*G/J*C |  | 49300 | 19.09 | 36000 | 3.75 | 4.1083
215837669 | Ground Loop | DAIKIN | WSMH024F3*G/J*P |  | 25600 | 18.72 | 18400 | 3.8 | 2.1333
215837671 | Ground Loop | DAIKIN | WSMH024J1*G/J*P |  | 25600 | 18.72 | 18400 | 3.8 | 2.1333
215837672 | Ground Loop | DAIKIN | WSMH024K3*G/J*P |  | 25600 | 18.72 | 18400 | 3.8 | 2.1333
215837677 | Ground Loop | DAIKIN | WSMH024F3*G/J*T |  | 25800 | 19.99 | 18200 | 3.8 | 2.15
215837679 | Ground Loop | DAIKIN | WSMH024J1*G/J*T |  | 25800 | 19.99 | 18200 | 3.8 | 2.15
215837680 | Ground Loop | DAIKIN | WSMH024K3*G/J*T |  | 25800 | 19.99 | 18200 | 3.8 | 2.15
215837686 | Ground Loop | DAIKIN | WSMH024F3*G/J*C |  | 25800 | 19.99 | 18200 | 3.8 | 2.15
215837687 | Ground Loop | DAIKIN | WSMH024J1*G/J*C |  | 25800 | 19.99 | 18200 | 3.8 | 2.15
215837689 | Ground Loop | DAIKIN | WSMH024K3*G/J*C |  | 25800 | 19.99 | 18200 | 3.8 | 2.15
215837694 | Ground Loop | DAIKIN | WSMH030F3*G/J*P |  | 29200 | 18.62 | 22200 | 3.72 | 2.4333
215837697 | Ground Loop | DAIKIN | WSMH030K3*G/J*P |  | 29200 | 18.62 | 22200 | 3.72 | 2.4333
215837703 | Ground Loop | DAIKIN | WSMH030F3*G/J*T |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583
215837704 | Ground Loop | DAIKIN | WSMH030J1*G/J*T |  | 29500 | 19.36 | 21900 | 3.76 | 2.4583
215837705 | Ground Loop | DAIKIN | WSMH030K3*G/J*T |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583
217903418 | Ground Loop | WaterFurnace | V5R036*S0**1* |  | 36000 | 20.6 | 25000 | 4 | 3
217903419 | Ground Loop | WaterFurnace | V5R036*S0**4* |  | 36000 | 20.6 | 25000 | 4 | 3
217903420 | Ground Loop | WaterFurnace | V5R036*S0**5* |  | 36000 | 20.6 | 25000 | 4 | 3
217903421 | Ground Loop | WaterFurnace | V5R048*S0**1* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833
217903422 | Ground Loop | WaterFurnace | V5R048*S0**4* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833
217903423 | Ground Loop | WaterFurnace | V5R048*S0**5* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833
217903424 | Ground Loop | WaterFurnace | V5R060*S0**1* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417
217903425 | Ground Loop | WaterFurnace | V5R060*S0**4* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417
217903426 | Ground Loop | WaterFurnace | V5R060*S0**5* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417
217903427 | Ground Loop | WaterFurnace | V5R072*S0**1* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6
217903428 | Ground Loop | WaterFurnace | V5R072*S0**4* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6
217903429 | Ground Loop | WaterFurnace | V5R072*S0**5* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6
217903430 | Ground Loop | WaterFurnace | V5R036*S3**1* |  | 36000 | 20.6 | 25000 | 4 | 3
217903431 | Ground Loop | WaterFurnace | V5R036*S3**4* |  | 36000 | 20.6 | 25000 | 4 | 3
217903432 | Ground Loop | WaterFurnace | V5R036*S3**5* |  | 36000 | 20.6 | 25000 | 4 | 3
217903433 | Ground Loop | WaterFurnace | V5R036*S4**1* |  | 36000 | 20.6 | 25000 | 4 | 3
217903434 | Ground Loop | WaterFurnace | V5R036*S4**4* |  | 36000 | 20.6 | 25000 | 4 | 3
217903435 | Ground Loop | WaterFurnace | V5R036*S4**5* |  | 36000 | 20.6 | 25000 | 4 | 3
217903436 | Ground Loop | WaterFurnace | V5R048*S3**1* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833
217903437 | Ground Loop | WaterFurnace | V5R048*S3**4* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833
217903438 | Ground Loop | WaterFurnace | V5R048*S3**5* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833
217903439 | Ground Loop | WaterFurnace | V5R048*S4**1* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833
217903440 | Ground Loop | WaterFurnace | V5R048*S4**4* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833
217903441 | Ground Loop | WaterFurnace | V5R048*S4**5* |  | 49000 | 18.2 | 37000 | 3.8 | 4.0833
217903442 | Ground Loop | WaterFurnace | V5R060*S3**1* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417
217903443 | Ground Loop | WaterFurnace | V5R060*S3**4* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417
217903444 | Ground Loop | WaterFurnace | V5R060*S3**5* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417
217903445 | Ground Loop | WaterFurnace | V5R060*S4**1* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417
217903446 | Ground Loop | WaterFurnace | V5R060*S4**4* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417
217903447 | Ground Loop | WaterFurnace | V5R060*S4**5* |  | 60500 | 18.4 | 46000 | 3.8 | 5.0417
217903448 | Ground Loop | WaterFurnace | V5R072*S3**1* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6
217903449 | Ground Loop | WaterFurnace | V5R072*S3**4* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6
217903450 | Ground Loop | WaterFurnace | V5R072*S3**5* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6
217903451 | Ground Loop | WaterFurnace | V5R072*S4**1* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6
217903452 | Ground Loop | WaterFurnace | V5R072*S4**4* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6
217903453 | Ground Loop | WaterFurnace | V5R072*S4**5* |  | 67200 | 17.1 | 51800 | 3.6 | 5.6
217903454 | Ground Loop | WaterFurnace | V5R036*D4**1* |  | 37000 | 20 | 28400 | 4 | 3.0833
217903455 | Ground Loop | WaterFurnace | V5R036*D4**4* |  | 37000 | 20 | 28400 | 4 | 3.0833
217903456 | Ground Loop | WaterFurnace | V5R036*D4**5* |  | 37000 | 20 | 28400 | 4 | 3.0833
217903457 | Ground Loop | WaterFurnace | V5R048*D4**1* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417
217903458 | Ground Loop | WaterFurnace | V5R048*D4**4* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417
217903459 | Ground Loop | WaterFurnace | V5R048*D4**5* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417
217903460 | Ground Loop | WaterFurnace | V5R060*D4**1* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833
9910606 | Ground Loop | GEOCOMFORT | GZS030*3****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525
9910607 | Ground Loop | HYDRON MODULE | HZS030*3****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525
9910608 | Ground Loop | TETCO | TZS030*3****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525
9910609 | Ground Loop | GEOCOMFORT | GZS030*4****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525
9910610 | Ground Loop | HYDRON MODULE | HZS030*4****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525
9910611 | Ground Loop | TETCO | TZS030*4****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525
9910612 | Ground Loop | GEOCOMFORT | GZS030*A****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525
9910613 | Ground Loop | HYDRON MODULE | HZS030*A****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525
9910614 | Ground Loop | TETCO | TZS030*A****B |  | 30300 | 19.1 | 21900 | 3.7 | 2.525
9910620 | Ground Loop | GEOCOMFORT | GZS036*****1B |  | 38400 | 19.5 | 27600 | 4 | 3.2
9910621 | Ground Loop | HYDRON MODULE | HZS036*****1B |  | 38400 | 19.5 | 27600 | 4 | 3.2
9910622 | Ground Loop | TETCO | TZS036*****1B |  | 38400 | 19.5 | 27600 | 4 | 3.2
9910623 | Ground Loop | GEOCOMFORT | GZS036*2***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2
9910624 | Ground Loop | HYDRON MODULE | HZS036*2***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2
9910625 | Ground Loop | TETCO | TZS036*2***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2
9910626 | Ground Loop | GEOCOMFORT | GZS036*3***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2
9910627 | Ground Loop | HYDRON MODULE | HZS036*3***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2
9910628 | Ground Loop | TETCO | TZS036*3***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2
9910629 | Ground Loop | GEOCOMFORT | GZS036*A***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2
9910630 | Ground Loop | HYDRON MODULE | HZS036*A***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2
9910631 | Ground Loop | TETCO | TZS036*A***1B |  | 38400 | 19.5 | 27600 | 4 | 3.2
9910636 | Ground Loop | GEOCOMFORT | GZS036******B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333
9910637 | Ground Loop | HYDRON MODULE | HZS036******B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333
9910638 | Ground Loop | TETCO | TZS036******B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333
9910639 | Ground Loop | GEOCOMFORT | GZS036*2****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333
9910640 | Ground Loop | HYDRON MODULE | HZS036*2****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333
9910641 | Ground Loop | TETCO | TZS036*2****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333
9910642 | Ground Loop | GEOCOMFORT | GZS036*3****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333
9910643 | Ground Loop | HYDRON MODULE | HZS036*3****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333
9910644 | Ground Loop | TETCO | TZS036*3****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333
9910645 | Ground Loop | GEOCOMFORT | GZS036*4****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333
9910646 | Ground Loop | HYDRON MODULE | HZS036*4****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333
9910647 | Ground Loop | TETCO | TZS036*4****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333
9910648 | Ground Loop | GEOCOMFORT | GZS036*A****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333
9910649 | Ground Loop | HYDRON MODULE | HZS036*A****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333
9910650 | Ground Loop | TETCO | TZS036*A****B |  | 37600 | 18.1 | 27800 | 3.7 | 3.1333
9910660 | Ground Loop | GEOCOMFORT | GZS042*****1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675
9910661 | Ground Loop | HYDRON MODULE | HZS042*****1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675
9910662 | Ground Loop | TETCO | TZS042*****1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675
9910663 | Ground Loop | GEOCOMFORT | GZS042*2***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675
9910664 | Ground Loop | HYDRON MODULE | HZS042*2***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675
9910665 | Ground Loop | TETCO | TZS042*2***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675
9910666 | Ground Loop | GEOCOMFORT | GZS042*3***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675
9910667 | Ground Loop | HYDRON MODULE | HZS042*3***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675
9910668 | Ground Loop | TETCO | TZS042*3***1B |  | 44100 | 21.1 | 32200 | 4.1 | 3.675
9910672 | Ground Loop | GEOCOMFORT | GZS042******B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167
9910673 | Ground Loop | HYDRON MODULE | HZS042******B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167
9910674 | Ground Loop | TETCO | TZS042******B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167
9910675 | Ground Loop | GEOCOMFORT | GZS042*2****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167
9910676 | Ground Loop | HYDRON MODULE | HZS042*2****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167
9910677 | Ground Loop | TETCO | TZS042*2****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167
9910678 | Ground Loop | GEOCOMFORT | GZS042*3****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167
9910679 | Ground Loop | HYDRON MODULE | HZS042*3****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167
9910680 | Ground Loop | TETCO | TZS042*3****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167
9910681 | Ground Loop | GEOCOMFORT | GZS042*4****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167
9910682 | Ground Loop | HYDRON MODULE | HZS042*4****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167
205767473 | Ground Loop | ClimateMaster | TEV/H/D026B |  | 26000 | 19.9 | 20200 | 4.1 | 2.1667
205767474 | Ground Loop | ClimateMaster | TEV/H/D038B |  | 39000 | 20.3 | 29700 | 4.4 | 3.25
205767475 | Ground Loop | ClimateMaster | TEV/H/D049B |  | 49600 | 19.3 | 36400 | 4 | 4.1333
205767476 | Ground Loop | ClimateMaster | TEV/H/D064B |  | 66200 | 18.8 | 48700 | 3.9 | 5.5167
207200586 | Ground Loop | GeoSmart Energy | GSZ022*1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583
207200587 | Ground Loop | GeoSmart Energy | GSZ022*1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583
207200588 | Ground Loop | GeoSmart Energy | GSZ030*1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05
207200589 | Ground Loop | GeoSmart Energy | GSZ030*1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05
207200590 | Ground Loop | GeoSmart Energy | GSZ048*1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417
207200591 | Ground Loop | GeoSmart Energy | GSZ048*1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417
207200592 | Ground Loop | GeoSmart Energy | GSZ060*1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
207200593 | Ground Loop | GeoSmart Energy | GSZ060*1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
207200594 | Ground Loop | GeoSmart Energy | GSZ070*1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417
207200596 | Ground Loop | GeoSmart Energy | GSZ070*1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417
207200598 | Ground Loop | GeoSmart Energy | GSZ036*1*J | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55
207200599 | Ground Loop | GeoSmart Energy | GSZ042*1*J | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15
207200600 | Ground Loop | GeoSmart Energy | GTZ038*1*J | SAH038* | 36000 | 19 | 27900 | 4 | 3
207200601 | Ground Loop | GeoSmart Energy | GTZ049*1*J | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207200602 | Ground Loop | GeoSmart Energy | GTZ049*1*J | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207200603 | Ground Loop | GeoSmart Energy | GTS064*1*J | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207200604 | Ground Loop | GeoSmart Energy | GTS064*1*J | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207200605 | Ground Loop | GeoSmart Energy | GSZ036*1*J | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55
207200606 | Ground Loop | GeoSmart Energy | GSZ042*1*J | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15
207200607 | Ground Loop | GeoSmart Energy | GTZ038*1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3
207200608 | Ground Loop | GeoSmart Energy | GTS038*1*J | SAH036* | 36000 | 19 | 27900 | 4 | 3
207200609 | Ground Loop | GeoSmart Energy | GTS038*1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3
207200613 | Ground Loop | GeoSmart Energy | QT038**1*(1,2)* |  | 36000 | 18.7 | 27400 | 3.9 | 3
207216511 | Ground Loop | GEOSTAR | GDV084**3 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5
207216512 | Ground Loop | GEOSTAR | GDV084**4 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5
207216513 | Ground Loop | GEOSTAR | GDV084**5 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5
207216514 | Ground Loop | GEOSTAR | GDH084**3 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333
207216515 | Ground Loop | GEOSTAR | GDH084**4 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333
207216516 | Ground Loop | GEOSTAR | GDH084**5 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333
207216517 | Ground Loop | GEOSTAR | GDV096**3 |  | 98000 | 17 | 76000 | 3.8 | 8.1667
207216518 | Ground Loop | GEOSTAR | GDV096**4 |  | 98000 | 17 | 76000 | 3.8 | 8.1667
207216519 | Ground Loop | GEOSTAR | GDV096**5 |  | 98000 | 17 | 76000 | 3.8 | 8.1667
213502579 | Ground Loop | DAIKIN | WSCH048E1*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075
213502580 | Ground Loop | DAIKIN | WSCH048E1*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075
213502581 | Ground Loop | DAIKIN | WSCH048E1*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075
213614501 | Ground Loop | DAIKIN | WSCH015A1*G/J*T |  | 15600 | 19 | 11900 | 3.6 | 1.3
213614502 | Ground Loop | DAIKIN | WSCH015A1*G/J*C |  | 15600 | 19 | 11900 | 3.6 | 1.3
213614506 | Ground Loop | DAIKIN | WSCH015J1*G/J*P |  | 15500 | 18 | 11900 | 3.6 | 1.2917
213614507 | Ground Loop | DAIKIN | WSCH015J1*G/J*T |  | 15500 | 18.7 | 12000 | 3.8 | 1.2917
213614508 | Ground Loop | DAIKIN | WSCH015J1*G/J*C |  | 15500 | 18.7 | 12000 | 3.8 | 1.2917
215832285 | Ground Loop | HYDROTECH | WSH6030D* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5
215832286 | Ground Loop | HYDROTECH | WSH6036D* |  | 36400 | 18 | 28000 | 3.6 | 3.0333
215832287 | Ground Loop | HYDROTECH | WSH6042D* |  | 43500 | 18.5 | 31000 | 3.8 | 3.625
215832288 | Ground Loop | HYDROTECH | WSH6048D* |  | 49500 | 18 | 36000 | 3.6 | 4.125
215832289 | Ground Loop | HYDROTECH | WSH6060D* |  | 60000 | 18.1 | 41000 | 3.6 | 5
215832290 | Ground Loop | HYDROTECH | WSH6072D* |  | 73000 | 17.1 | 55000 | 3.6 | 6.0833
215832291 | Ground Loop | AE Air | WSH6009D* |  | 9500 | 18.9 | 6500 | 3.6 | 0.79167
216714636 | Ground Loop | GEOSTAR | G3A(V/H)036*S0**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
216714637 | Ground Loop | GEOSTAR | G3A(V/H)036*S0**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
216714638 | Ground Loop | GEOSTAR | G3A(V/H)036*S2**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
216714639 | Ground Loop | GEOSTAR | G3A(V/H)036*S2**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
216714640 | Ground Loop | GEOSTAR | G3A(V/H)036*S3**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
216714641 | Ground Loop | GEOSTAR | G3A(V/H)036*S3**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
216714642 | Ground Loop | GEOSTAR | G3A(V/H)036*S4**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
216714643 | Ground Loop | GEOSTAR | G3A(V/H)036*S4**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
216714644 | Ground Loop | GEOSTAR | G3A(V/H)042*S0**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
216714645 | Ground Loop | GEOSTAR | G3A(V/H)042*S0**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
216714646 | Ground Loop | GEOSTAR | G3A(V/H)042*S3**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
216714647 | Ground Loop | GEOSTAR | G3A(V/H)042*S3**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
216714648 | Ground Loop | GEOSTAR | G3A(V/H)042*S4**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
216714649 | Ground Loop | GEOSTAR | G3A(V/H)042*S4**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
216714656 | Ground Loop | GEOSTAR | G3A(V/H)060*S0**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
216714657 | Ground Loop | GEOSTAR | G3A(V/H)060*S0**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
216714658 | Ground Loop | GEOSTAR | G3A(V/H)060*S3**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
216714659 | Ground Loop | GEOSTAR | G3A(V/H)060*S3**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
216714660 | Ground Loop | GEOSTAR | G3A(V/H)060*S4**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
216714661 | Ground Loop | GEOSTAR | G3A(V/H)060*S4**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
216726174 | Ground Loop | DAIKIN | WSRC007*A*G/J |  | 7400 | 19.4 | 4800 | 3.6 | 0.61667
216726178 | Ground Loop | DAIKIN | WSRC009*A*G/J |  | 9100 | 18.9 | 6500 | 3.6 | 0.75833
216569713 | Ground Loop | GeoCool | GCHPV/H/D024BT**A*** |  | 26400 | 17.95 | 19000 | 4.2 | 2.2
216569714 | Ground Loop | GeoCool | GCHPV/H/D036BT**A*** |  | 39000 | 17.86 | 28500 | 4.2 | 3.25
202147040 | Ground Loop | GEOCOMFORT | GZS048*****1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083
202147041 | Ground Loop | GEOCOMFORT | GZS048*2***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083
202147042 | Ground Loop | GEOCOMFORT | GZS048*3***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083
202147047 | Ground Loop | HYDRON MODULE | HZS048*****1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083
202147048 | Ground Loop | HYDRON MODULE | HZS048*2***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083
202147049 | Ground Loop | HYDRON MODULE | HZS048*3***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083
202147054 | Ground Loop | TETCO | TZS048*****1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083
202147055 | Ground Loop | TETCO | TZS048*2***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083
202147056 | Ground Loop | TETCO | TZS048*3***1 |  | 49300 | 17.4 | 36200 | 3.6 | 4.1083
202147061 | Ground Loop | GEOCOMFORT | GZS060*****1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75
202147062 | Ground Loop | GEOCOMFORT | GZS060*2***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75
202147067 | Ground Loop | HYDRON MODULE | HZS060*****1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75
202147068 | Ground Loop | HYDRON MODULE | HZS060*2***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75
217754591 | Ground Loop | DAIKIN | WSMH048E1*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075
217754592 | Ground Loop | DAIKIN | WSMH048F1*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075
217754593 | Ground Loop | DAIKIN | WSMH048K1*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075
217754594 | Ground Loop | DAIKIN | WSMH048L1*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075
217754598 | Ground Loop | DAIKIN | WSMH048E1*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075
217754599 | Ground Loop | DAIKIN | WSMH048F1*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075
217754600 | Ground Loop | DAIKIN | WSMH048K1*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075
217754604 | Ground Loop | DAIKIN | WSMH048E1*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075
217754605 | Ground Loop | DAIKIN | WSMH048F1*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075
217754606 | Ground Loop | DAIKIN | WSMH048K1*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075
9105364 | Ground Loop | GEOCOMFORT | GVS006 |  | 7200 | 18.6 | 5600 | 3.7 | 0.6
9105366 | Ground Loop | HYDRON MODULE | HVS006 |  | 7200 | 18.6 | 5600 | 3.7 | 0.6
9105367 | Ground Loop | TETCO | TVS006 |  | 7200 | 18.6 | 5600 | 3.7 | 0.6
9111997 | Ground Loop | BOSCH | SM024-1VT/CF*-*****B |  | 26900 | 18.9 | 18700 | 4.1 | 2.2417
9111998 | Ground Loop | BOSCH | SM036-1VT/CF*-*****B |  | 40200 | 21 | 28200 | 4.3 | 3.35
9113111 | Ground Loop | BOSCH | SM048-1VT/CF*-*****B* |  | 51800 | 18.6 | 38200 | 4.2 | 4.3167
9113180 | Ground Loop | BOSCH | SM060-1VT/CF*-*****B |  | 63900 | 18.6 | 48600 | 4 | 5.325
9113181 | Ground Loop | BOSCH | SM070-1VT/CF*-*****B |  | 71500 | 17.3 | 56000 | 3.8 | 5.9583
9113182 | Ground Loop | BOSCH | SM024-1VT/CF*-*****B |  | 26900 | 18.9 | 18700 | 4.1 | 2.2417
9113183 | Ground Loop | BOSCH | SM036-1VT/CF*-*****B |  | 40200 | 21 | 28200 | 4.3 | 3.35
9113184 | Ground Loop | BOSCH | SM048-1VT/CF*-*****B* |  | 51800 | 18.6 | 38200 | 4.2 | 4.3167
9113185 | Ground Loop | BOSCH | SM060-1VT/CF*-*****B |  | 63900 | 18.6 | 48600 | 4 | 5.325
9113186 | Ground Loop | BOSCH | SM070-1VT/CF*-*****B |  | 71500 | 17.3 | 56000 | 3.8 | 5.9583
9114306 | Ground Loop | GEOCOMFORT | GZT060******B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1
9114307 | Ground Loop | HYDRON MODULE | HZT060******B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1
9114308 | Ground Loop | TETCO | TZT060******B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1
9114309 | Ground Loop | GEOCOMFORT | GZT060*2****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1
9114310 | Ground Loop | HYDRON MODULE | HZT060*2****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1
9114311 | Ground Loop | TETCO | TZT060*2****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1
9114312 | Ground Loop | GEOCOMFORT | GZT060*3****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1
9114313 | Ground Loop | HYDRON MODULE | HZT060*3****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1
9114314 | Ground Loop | TETCO | TZT060*3****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1
9114315 | Ground Loop | GEOCOMFORT | GZT060*A****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1
9114316 | Ground Loop | HYDRON MODULE | HZT060*A****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1
9114317 | Ground Loop | TETCO | TZT060*A****B |  | 61200 | 18.7 | 48100 | 3.9 | 5.1
9114322 | Ground Loop | GEOCOMFORT | GZT072******B |  | 70400 | 18 | 57900 | 3.8 | 5.8667
9114323 | Ground Loop | HYDRON MODULE | HZT072******B |  | 70400 | 18 | 57900 | 3.8 | 5.8667
9114324 | Ground Loop | TETCO | TZT072******B |  | 70400 | 18 | 57900 | 3.8 | 5.8667
9114325 | Ground Loop | GEOCOMFORT | GZT072*2****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667
9114326 | Ground Loop | HYDRON MODULE | HZT072*2****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667
9114327 | Ground Loop | TETCO | TZT072*2****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667
9114328 | Ground Loop | GEOCOMFORT | GZT072*3****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667
9114329 | Ground Loop | HYDRON MODULE | HZT072*3****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667
9114330 | Ground Loop | TETCO | TZT072*3****B |  | 70400 | 18 | 57900 | 3.8 | 5.8667
207178495 | Ground Loop | GEOSTAR | 163J049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207178496 | Ground Loop | GEOSTAR | 163J049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207178497 | Ground Loop | GEOSTAR | 163J064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207178498 | Ground Loop | GEOSTAR | 163J064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207178499 | Ground Loop | GEOSTAR | 164J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3
207178500 | Ground Loop | GEOSTAR | 163J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3
207178519 | Ground Loop | GEOSTAR | 164H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207178520 | Ground Loop | GEOSTAR | 164H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207178521 | Ground Loop | GEOSTAR | 164H064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207178522 | Ground Loop | GEOSTAR | 164H064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207178525 | Ground Loop | GEOSTAR | 161/162J064**1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207178536 | Ground Loop | GEOSTAR | 163H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207198394 | Ground Loop | BOSCH | QV024-1HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083
207198395 | Ground Loop | BOSCH | QV024-1HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083
207198401 | Ground Loop | BOSCH | QV024-2HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083
207198402 | Ground Loop | BOSCH | QV024-2HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083
207198406 | Ground Loop | BOSCH | QV024-3HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083
207198407 | Ground Loop | BOSCH | QV024-3HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083
207198410 | Ground Loop | BOSCH | QV024-4HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083
207198411 | Ground Loop | BOSCH | QV024-4HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083
207198416 | Ground Loop | BOSCH | QV030-1HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958
207198417 | Ground Loop | BOSCH | QV030-1HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708
207198419 | Ground Loop | BOSCH | QV030-1VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958
207198420 | Ground Loop | BOSCH | QV030-1VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708
207198421 | Ground Loop | BOSCH | QV030-2HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958
207198422 | Ground Loop | BOSCH | QV030-2HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708
207198424 | Ground Loop | BOSCH | QV030-2VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958
207198425 | Ground Loop | BOSCH | QV030-2VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708
207198426 | Ground Loop | BOSCH | QV030-3HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958
207198428 | Ground Loop | BOSCH | QV030-3HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708
207198429 | Ground Loop | BOSCH | QV030-3VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958
207198430 | Ground Loop | BOSCH | QV030-3VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708
207198432 | Ground Loop | BOSCH | QV030-4HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958
207198433 | Ground Loop | BOSCH | QV030-4HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708
207198434 | Ground Loop | BOSCH | QV030-4VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958
207198436 | Ground Loop | BOSCH | QV030-4VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708
207198437 | Ground Loop | BOSCH | QV036-1HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667
207198440 | Ground Loop | BOSCH | QV036-1VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625
207198441 | Ground Loop | BOSCH | QV036-1VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583
215224089 | Ground Loop | BOSCH | CF024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224090 | Ground Loop | BOSCH | CF024-3VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224091 | Ground Loop | BOSCH | CF024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224092 | Ground Loop | BOSCH | CF024-3VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
216759832 | Ground Loop | GEOSTAR | G5SZ036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833
216759833 | Ground Loop | GEOSTAR | G5SZ048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925
216759834 | Ground Loop | GEOSTAR | G5SZ060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917
216767321 | Ground Loop | TETCO | TVT024* |  | 25800 | 18.6 | 19400 | 4 | 2.15
216767322 | Ground Loop | TETCO | TVT030* |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833
216767323 | Ground Loop | TETCO | TVT036* |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167
216767324 | Ground Loop | TETCO | TVT042* |  | 45900 | 18.5 | 32400 | 3.9 | 3.825
216767325 | Ground Loop | TETCO | TVT048* |  | 50300 | 18.8 | 38500 | 4 | 4.1917
216767326 | Ground Loop | TETCO | TYT024* |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583
216767327 | Ground Loop | TETCO | TYT036* |  | 39700 | 21 | 27900 | 4.3 | 3.3083
216767328 | Ground Loop | TETCO | TYT048* |  | 51900 | 19.2 | 36700 | 4.1 | 4.325
216767329 | Ground Loop | TETCO | TVT060* |  | 60900 | 17.6 | 46300 | 3.8 | 5.075
216767330 | Ground Loop | TETCO | TYT060* |  | 63100 | 18.7 | 49100 | 4 | 5.2583
217752687 | Ground Loop | DAIKIN | WSSH036J1*H*C |  | 40300 | 20.75 | 27600 | 3.61 | 3.3583
217752689 | Ground Loop | DAIKIN | WSSH042J1*H*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667
217752691 | Ground Loop | DAIKIN | WSSH042J1*H*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667
215400096 | Ground Loop | DAIKIN | WSMV024E1*G/J*T |  | 25600 | 20.91 | 18600 | 3.87 | 2.1333
215400097 | Ground Loop | DAIKIN | WSMV024F3*G/J*T |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333
215400100 | Ground Loop | DAIKIN | WSMV024E1*G/J*C |  | 25600 | 20.91 | 18600 | 3.87 | 2.1333
215400101 | Ground Loop | DAIKIN | WSMV024F3*G/J*C |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333
215400104 | Ground Loop | DAIKIN | WSMV030E1*G/J*P |  | 29500 | 19.36 | 21300 | 3.62 | 2.4583
215400108 | Ground Loop | DAIKIN | WSMV030E1*G/J*T |  | 29800 | 19.77 | 21500 | 3.65 | 2.4833
215400112 | Ground Loop | DAIKIN | WSMV030E1*G/J*C |  | 29800 | 19.77 | 21500 | 3.65 | 2.4833
215400116 | Ground Loop | DAIKIN | WSMV036E1*G/J*P |  | 37600 | 19.36 | 28000 | 3.69 | 3.1333
215400120 | Ground Loop | DAIKIN | WSMV036E1*G/J*T |  | 37500 | 19.9 | 28000 | 3.82 | 3.125
215400121 | Ground Loop | DAIKIN | WSMV036F3*G/J*T |  | 37100 | 19.24 | 27700 | 3.72 | 3.0917
215400124 | Ground Loop | DAIKIN | WSMV036E1*G/J*C |  | 37500 | 19.9 | 28000 | 3.82 | 3.125
215400125 | Ground Loop | DAIKIN | WSMV036F3*G/J*C |  | 37100 | 19.24 | 27700 | 3.72 | 3.0917
215400132 | Ground Loop | DAIKIN | WSMV042E1*G/J*T |  | 43000 | 19.86 | 30000 | 3.66 | 3.5833
215400136 | Ground Loop | DAIKIN | WSMV042E1*G/J*C |  | 43000 | 19.86 | 30000 | 3.66 | 3.5833
215400140 | Ground Loop | DAIKIN | WSMV048E1*G/J*P |  | 50200 | 18.61 | 37100 | 3.64 | 4.1833
215400141 | Ground Loop | DAIKIN | WSMV048F3*G/J*P |  | 50200 | 18.61 | 37100 | 3.64 | 4.1833
215400144 | Ground Loop | DAIKIN | WSMV048E1*G/J*T |  | 49800 | 19.09 | 36400 | 3.75 | 4.15
215400145 | Ground Loop | DAIKIN | WSMV048F3*G/J*T |  | 49800 | 19.09 | 36400 | 3.75 | 4.15
207337518 | Ground Loop | GEOSTAR | 103H048**1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417
207337521 | Ground Loop | GEOSTAR | 103H070**1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417
207337522 | Ground Loop | GEOSTAR | 103H070**1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417
207348654 | Ground Loop | WaterFurnace | URS036*0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
207348655 | Ground Loop | WaterFurnace | URS036*0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
207348656 | Ground Loop | WaterFurnace | URS036*0*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
207348657 | Ground Loop | WaterFurnace | URS036*3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
207348658 | Ground Loop | WaterFurnace | URS036*3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
207348659 | Ground Loop | WaterFurnace | URS036*3*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
207348660 | Ground Loop | WaterFurnace | URS036*4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
207348661 | Ground Loop | WaterFurnace | URS036*4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
207348662 | Ground Loop | WaterFurnace | URS036*4*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
207348663 | Ground Loop | WaterFurnace | URS048*0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
207348664 | Ground Loop | WaterFurnace | URS048*0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
207348665 | Ground Loop | WaterFurnace | URS048*0*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825
207348666 | Ground Loop | WaterFurnace | URS048*3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
207348667 | Ground Loop | WaterFurnace | URS048*3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
207348668 | Ground Loop | WaterFurnace | URS048*3*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825
207348669 | Ground Loop | WaterFurnace | URS048*4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
207348670 | Ground Loop | WaterFurnace | URS048*4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
207348671 | Ground Loop | WaterFurnace | URS048*4*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825
207348672 | Ground Loop | WaterFurnace | URS070*0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
207348673 | Ground Loop | WaterFurnace | URS070*0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
207348674 | Ground Loop | WaterFurnace | URS070*0*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
207348675 | Ground Loop | WaterFurnace | URS070*3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
207348676 | Ground Loop | WaterFurnace | URS070*3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
207348677 | Ground Loop | WaterFurnace | URS070*3*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
207348678 | Ground Loop | WaterFurnace | URS070*4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
201907620 | Ground Loop | WaterFurnace | URS048*0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
201907621 | Ground Loop | WaterFurnace | URS048*0*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825
201907622 | Ground Loop | WaterFurnace | URS048*3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
201907623 | Ground Loop | WaterFurnace | URS048*3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
201907624 | Ground Loop | WaterFurnace | URS048*3*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825
201907625 | Ground Loop | WaterFurnace | URS048*4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
201907626 | Ground Loop | WaterFurnace | URS048*4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
201907627 | Ground Loop | WaterFurnace | URS048*4*5 |  | 45900 | 18.8 | 36400 | 4 | 3.825
201907628 | Ground Loop | WaterFurnace | URD038*4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
201907629 | Ground Loop | WaterFurnace | URD038*4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
201907630 | Ground Loop | WaterFurnace | URD038*4*5 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
201907631 | Ground Loop | WaterFurnace | URD049*4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
201907632 | Ground Loop | WaterFurnace | URD049*4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
201907633 | Ground Loop | WaterFurnace | URD049*4*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
201926691 | Ground Loop | WaterFurnace | URS060*0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
201926694 | Ground Loop | WaterFurnace | URS060*0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
201926696 | Ground Loop | WaterFurnace | URS060*0*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
201926699 | Ground Loop | WaterFurnace | URS060*3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
201926702 | Ground Loop | WaterFurnace | URS060*3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
201926705 | Ground Loop | WaterFurnace | URS060*3*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
201926708 | Ground Loop | WaterFurnace | URS060*4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
201926711 | Ground Loop | WaterFurnace | URS060*4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
201926714 | Ground Loop | WaterFurnace | URS060*4*5 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
201926717 | Ground Loop | WaterFurnace | URS070*0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
201926719 | Ground Loop | WaterFurnace | URS070*0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
201926724 | Ground Loop | WaterFurnace | URS070*0*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
201926727 | Ground Loop | WaterFurnace | URS070*3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
201926730 | Ground Loop | WaterFurnace | URS070*3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
201926733 | Ground Loop | WaterFurnace | URS070*3*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
201926736 | Ground Loop | WaterFurnace | URS070*4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
206346938 | Ground Loop | DAIKIN | WCCW*019*J***14* |  | 20600 | 19 | 14000 | 3.7 | 1.7167
206346939 | Ground Loop | DAIKIN | WCCW*024*E***14* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417
206346940 | Ground Loop | DAIKIN | WCCW*024*F***14* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417
206346941 | Ground Loop | DAIKIN | WCCW*024*J***14* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417
206346942 | Ground Loop | DAIKIN | WCCW*024*K***14* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417
206346943 | Ground Loop | DAIKIN | WVFW*019*E***14 |  | 19700 | 19 | 13400 | 3.7 | 1.6417
206346944 | Ground Loop | DAIKIN | WVFW*019*J***14 |  | 19700 | 19 | 13400 | 3.7 | 1.6417
206346948 | Ground Loop | DAIKIN | WVFW*024*E***14 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917
206346949 | Ground Loop | DAIKIN | WVFW*024*F***14 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917
206346950 | Ground Loop | DAIKIN | WVFW*024*J***14 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917
206346954 | Ground Loop | DAIKIN | WVFW*030*E***14 |  | 30600 | 19.3 | 22300 | 4 | 2.55
206346955 | Ground Loop | DAIKIN | WVFW*030*F***14 |  | 30600 | 19.3 | 22300 | 4 | 2.55
206346956 | Ground Loop | DAIKIN | WVFW*030*J***14 |  | 30600 | 19.3 | 22300 | 4 | 2.55
206346966 | Ground Loop | DAIKIN | WVFW*042*E***14 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417
206346967 | Ground Loop | DAIKIN | WVFW*042*F***14 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417
206346968 | Ground Loop | DAIKIN | WVFW*042*K***14 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417
206346972 | Ground Loop | DAIKIN | WVFW*048*E***14 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833
206346973 | Ground Loop | DAIKIN | WVFW*048*F***14 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833
206346974 | Ground Loop | DAIKIN | WVFW*048*K***14 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833
206346978 | Ground Loop | DAIKIN | WVFW*060*E***14 |  | 66000 | 18 | 46000 | 3.8 | 5.5
206346979 | Ground Loop | DAIKIN | WVFW*060*F***14 |  | 66000 | 18 | 46000 | 3.8 | 5.5
206346980 | Ground Loop | DAIKIN | WVFW*060*K***14 |  | 66000 | 18 | 46000 | 3.8 | 5.5
216739946 | Ground Loop | DAIKIN | WSNH060E1*G/J*C |  | 61200 | 17.3 | 49000 | 3.9 | 5.1
216739947 | Ground Loop | DAIKIN | WSNH060F3*G/J*C |  | 61200 | 17 | 49000 | 3.9 | 5.1
216739948 | Ground Loop | DAIKIN | WSNH060K3*G/J*C |  | 61200 | 17 | 49000 | 3.9 | 5.1
216739957 | Ground Loop | DAIKIN | WSNV030E1*G/J*C |  | 31900 | 18.9 | 20500 | 3.6 | 2.6583
216739965 | Ground Loop | DAIKIN | WSNV036E1*G/J*C |  | 37300 | 20.3 | 26100 | 3.8 | 3.1083
216739966 | Ground Loop | DAIKIN | WSNV036F3*G/J*C |  | 37300 | 19.9 | 26100 | 3.8 | 3.1083
216739967 | Ground Loop | DAIKIN | WSNV036J1*G/J*C |  | 37300 | 19.9 | 26100 | 3.8 | 3.1083
216739968 | Ground Loop | DAIKIN | WSNV036K3*G/J*C |  | 37300 | 19.7 | 26100 | 3.7 | 3.1083
216739972 | Ground Loop | DAIKIN | WSNV042E1*G/J*C |  | 44700 | 19.3 | 29000 | 3.6 | 3.725
202434548 | Ground Loop | BOSCH | SV036-1VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434549 | Ground Loop | BOSCH | SV036-3VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434550 | Ground Loop | BOSCH | SV036-4VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434551 | Ground Loop | BOSCH | SV036-2VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434556 | Ground Loop | BOSCH | SV036-1HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434557 | Ground Loop | BOSCH | SV036-3HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434558 | Ground Loop | BOSCH | SV036-4HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434559 | Ground Loop | BOSCH | SV036-2HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
215852852 | Ground Loop | DAIKIN | WSTH030E1*G/J*C |  | 32700 | 19.69 | 20600 | 3.75 | 2.725
215852853 | Ground Loop | DAIKIN | WSTH030F3*G/J*C |  | 32700 | 19.29 | 20600 | 3.68 | 2.725
215852856 | Ground Loop | DAIKIN | WSTH036E1*G/J*C |  | 38700 | 20.64 | 25900 | 3.75 | 3.225
215852857 | Ground Loop | DAIKIN | WSTH036F3*G/J*C |  | 38700 | 20.23 | 25900 | 3.67 | 3.225
215852860 | Ground Loop | DAIKIN | WSTH042E1*G/J*C |  | 45900 | 20.06 | 28400 | 3.7 | 3.825
215852861 | Ground Loop | DAIKIN | WSTH042F3*G/J*C |  | 45900 | 19.66 | 28400 | 3.63 | 3.825
215852864 | Ground Loop | DAIKIN | WSTH060E1*G/J*C |  | 61600 | 19 | 44200 | 3.7 | 5.1333
215852865 | Ground Loop | DAIKIN | WSTH060F3*G/J*C |  | 61600 | 18.62 | 44200 | 3.63 | 5.1333
215852872 | Ground Loop | DAIKIN | WSTV030E1*G/J*C |  | 32200 | 19.48 | 20800 | 3.78 | 2.6833
215852873 | Ground Loop | DAIKIN | WSTV030F3*G/J*C |  | 32200 | 19.09 | 20800 | 3.7 | 2.6833
206194171 | Ground Loop | Johnson Controls | JSH/V/D030C*K B |  | 29200 | 19.4 | 22000 | 4.1 | 2.4333
206194172 | Ground Loop | SKYMARK | JSH/V/D030C*K C |  | 29200 | 19.4 | 22000 | 4.1 | 2.4333
206194173 | Ground Loop | Johnson Controls | JSH/V/D048C*K B |  | 50600 | 18.8 | 36100 | 3.7 | 4.2167
206194174 | Ground Loop | SKYMARK | JSH/V/D048C*K C |  | 50600 | 18.8 | 36100 | 3.7 | 4.2167
206194175 | Ground Loop | Johnson Controls | JSH/V/D060C*K B |  | 64400 | 18.4 | 46400 | 3.9 | 5.3667
206194176 | Ground Loop | SKYMARK | JSH/V/D060C*K C |  | 64400 | 18.4 | 46400 | 3.9 | 5.3667
206194177 | Ground Loop | Johnson Controls | JSH/V/D070C*K B |  | 73000 | 17.2 | 53000 | 3.6 | 6.0833
206194178 | Ground Loop | SKYMARK | JSH/V/D070C*K C |  | 73000 | 17.2 | 53000 | 3.6 | 6.0833
202835053 | Ground Loop | BOSCH | SM036-1HZ*-*****C |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
202835056 | Ground Loop | BOSCH | SM024-1VT*-*****C |  | 26900 | 18.9 | 18700 | 4.1 | 2.2417
202835057 | Ground Loop | BOSCH | SM060-1VT*-*****C |  | 63900 | 18.6 | 48600 | 4 | 5.325
202836307 | Ground Loop | BOSCH | SM036-1VT*-*****C |  | 40200 | 21 | 28200 | 4.3 | 3.35
202836309 | Ground Loop | BOSCH | SM048-1VT*-*****C |  | 51800 | 18.6 | 38200 | 4.2 | 4.3167
7411100 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
7411231 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
7411301 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
7411380 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
7411778 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**2*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
7411875 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
7411949 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
7412057 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**3*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
7412158 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
7412253 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
7412381 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**4*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
7412626 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**0*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
7412712 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**0*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
7412777 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**2*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
7412856 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**2*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
7412926 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**3*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
7413034 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**3*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
7413487 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**4*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
7414142 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
7414232 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
7414335 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**0*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
7414470 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
7414553 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
7414651 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**2*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
7414828 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
7414896 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
7415098 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**3*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
7415209 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
7415301 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
7415373 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH030**4*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
7415455 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
216979875 | Ground Loop | KEEPRITE | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25
216979876 | Ground Loop | TEMPSTAR | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25
216979877 | Ground Loop | COMFORTMAKER | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25
216979878 | Ground Loop | DAY & NIGHT | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25
216979879 | Ground Loop | HEIL | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083
216979880 | Ground Loop | ARCOAIRE | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083
216979881 | Ground Loop | KEEPRITE | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083
216979882 | Ground Loop | TEMPSTAR | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083
216979883 | Ground Loop | COMFORTMAKER | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083
216979884 | Ground Loop | DAY & NIGHT | HCR48V/H**N******1 |  | 50500 | 17.5 | 37500 | 4 | 4.2083
216979885 | Ground Loop | HEIL | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25
216979886 | Ground Loop | ARCOAIRE | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25
216979887 | Ground Loop | KEEPRITE | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25
216979888 | Ground Loop | TEMPSTAR | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25
216979889 | Ground Loop | COMFORTMAKER | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25
216979890 | Ground Loop | DAY & NIGHT | HCR60V/H**C******1 |  | 63000 | 18 | 48000 | 4 | 5.25
216979891 | Ground Loop | HEIL | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083
216979892 | Ground Loop | ARCOAIRE | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083
216979893 | Ground Loop | KEEPRITE | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083
216979894 | Ground Loop | TEMPSTAR | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083
216979895 | Ground Loop | COMFORTMAKER | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083
216979896 | Ground Loop | DAY & NIGHT | HCR60V/H**N******1 |  | 62500 | 18 | 47500 | 4 | 5.2083
217014524 | Ground Loop | CARRIER | GCA72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217014525 | Ground Loop | BRYANT | GCA72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217014528 | Ground Loop | CARRIER | GCA72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217014529 | Ground Loop | BRYANT | GCA72H**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217014532 | Ground Loop | HEIL | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217014533 | Ground Loop | ARCOAIRE | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217014534 | Ground Loop | KEEPRITE | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217014535 | Ground Loop | TEMPSTAR | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
202541572 | Ground Loop | BOSCH-GEO | BP048-1VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
202541573 | Ground Loop | BOSCH | BP048-1VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
202541574 | Ground Loop | CARRIER | GB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
202541575 | Ground Loop | BRYANT | GB048V******1**1 |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
202543170 | Ground Loop | CARRIER | GB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
202543171 | Ground Loop | BRYANT | GB018V******1**2 |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
216625646 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D2**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625647 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D2**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
3628355 | Ground Loop | WaterFurnace | USV/USH070**0*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
3628356 | Ground Loop | WaterFurnace | USV/USH070**3*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
3628357 | Ground Loop | WaterFurnace | USV/USH070**4*1 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
3628359 | Ground Loop | WaterFurnace | USV/USH060**0*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
3628360 | Ground Loop | WaterFurnace | USV/USH060**3*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
3628361 | Ground Loop | WaterFurnace | USV/USH060**4*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
3628363 | Ground Loop | WaterFurnace | USV/USH048**0*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
3628364 | Ground Loop | WaterFurnace | USV/USH048**3*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
3628365 | Ground Loop | WaterFurnace | USV/USH048**4*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
3628367 | Ground Loop | WaterFurnace | USV/USH042**0*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
3628368 | Ground Loop | WaterFurnace | USV/USH042**3*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
3628369 | Ground Loop | WaterFurnace | USV/USH042**4*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
3628403 | Ground Loop | WaterFurnace | USV/USH030**0*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
3628404 | Ground Loop | WaterFurnace | USV/USH030**2*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
3628405 | Ground Loop | WaterFurnace | USV/USH030**3*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
3628406 | Ground Loop | WaterFurnace | USV/USH030**4*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
215223494 | Ground Loop | WaterFurnace | V5AV084*D4**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5
215223500 | Ground Loop | WaterFurnace | V5AV084*D3**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5
215223501 | Ground Loop | WaterFurnace | V5AV084*D5**5 |  | 90000 | 17 | 69000 | 3.8 | 7.5
215837917 | Ground Loop | DAIKIN | WSSH070F3*G/J*T |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083
215837919 | Ground Loop | DAIKIN | WSSH070K3*G/J*T |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083
215837926 | Ground Loop | DAIKIN | WSSH070F3*G/J*C |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083
215837927 | Ground Loop | DAIKIN | WSSH070K3*G/J*C |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083
215851758 | Ground Loop | DAIKIN | WSTH024J1*G/J*C |  | 25100 | 19.52 | 17200 | 3.84 | 2.0917
215851759 | Ground Loop | DAIKIN | WSTH024K3*G/J*C |  | 25100 | 19.32 | 17200 | 3.8 | 2.0917
215851764 | Ground Loop | DAIKIN | WSTH030J1*G/J*C |  | 32700 | 19.29 | 20600 | 3.68 | 2.725
215851765 | Ground Loop | DAIKIN | WSTH030K3*G/J*C |  | 32700 | 19.1 | 20600 | 3.64 | 2.725
215851770 | Ground Loop | DAIKIN | WSTH036J1*G/J*C |  | 38700 | 20.23 | 25900 | 3.67 | 3.225
215851772 | Ground Loop | DAIKIN | WSTH036K3*G/J*C |  | 38700 | 20.02 | 25900 | 3.64 | 3.225
10259035 | Ground Loop | GEOCOMFORT | GZS015*****1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667
10259036 | Ground Loop | HYDRON MODULE | HZS015*****1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667
10259037 | Ground Loop | TETCO | TZS015*****1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667
10259038 | Ground Loop | GEOCOMFORT | GZS015*A***1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667
10259039 | Ground Loop | HYDRON MODULE | HZS015*A***1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667
10259040 | Ground Loop | TETCO | TZS015*A***1B |  | 15200 | 20.3 | 10900 | 3.9 | 1.2667
10259044 | Ground Loop | GEOCOMFORT | GZS015******B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275
10259045 | Ground Loop | HYDRON MODULE | HZS015******B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275
10259046 | Ground Loop | TETCO | TZS015******B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275
10259047 | Ground Loop | GEOCOMFORT | GZS015*A****B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275
10259048 | Ground Loop | HYDRON MODULE | HZS015*A****B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275
10259049 | Ground Loop | TETCO | TZS015*A****B |  | 15300 | 19.2 | 11100 | 3.8 | 1.275
10259054 | Ground Loop | GEOCOMFORT | GZS017*****1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083
10259055 | Ground Loop | HYDRON MODULE | HZS017*****1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083
10259056 | Ground Loop | TETCO | TZS017*****1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083
10259057 | Ground Loop | GEOCOMFORT | GZS017*A***1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083
10259058 | Ground Loop | HYDRON MODULE | HZS017*A***1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083
10259059 | Ground Loop | TETCO | TZS017*A***1B |  | 18100 | 20.5 | 13000 | 3.8 | 1.5083
10259062 | Ground Loop | GEOCOMFORT | GZS017******B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525
10259063 | Ground Loop | HYDRON MODULE | HZS017******B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525
10259064 | Ground Loop | TETCO | TZS017******B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525
10259065 | Ground Loop | GEOCOMFORT | GZS017*A****B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525
10259066 | Ground Loop | HYDRON MODULE | HZS017*A****B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525
10259067 | Ground Loop | TETCO | TZS017*A****B |  | 18300 | 18.6 | 13400 | 3.7 | 1.525
10271778 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ026H1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10271930 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ026H1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10271959 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ022H1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583
10271961 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ022H1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583
10271981 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ030H1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05
10271985 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ030H1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05
10272006 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ048H1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417
10272008 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ048H1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417
10272012 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ060H1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
10272014 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ060H1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
10272021 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ070H1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417
10272215 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS026H1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10272216 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS026H1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10272219 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS049H1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
10272220 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS049H1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
10272221 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS064H1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
10272222 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS064H1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
10298936 | Ground Loop | WaterFurnace | UVV/UVH036**0*1 |  | 39000 | 21 | 29000 | 3.8 | 3.25
10298937 | Ground Loop | WaterFurnace | UVV/UVH036**3*1 |  | 39000 | 21 | 29000 | 3.8 | 3.25
10298938 | Ground Loop | WaterFurnace | UVV/UVH036**4*1 |  | 39000 | 21 | 29000 | 3.8 | 3.25
205767566 | Ground Loop | ClimateMaster | TSL15 A |  | 15400 | 17.7 | 11500 | 3.6 | 1.2833
205767567 | Ground Loop | ClimateMaster | TSL15 B |  | 15400 | 19.2 | 11000 | 3.7 | 1.2833
205767571 | Ground Loop | ClimateMaster | TSL24 B |  | 26500 | 19.4 | 18500 | 3.6 | 2.2083
205767573 | Ground Loop | ClimateMaster | TSL30 B |  | 29500 | 18.4 | 21000 | 3.7 | 2.4583
205996643 | Ground Loop | Johnson Controls | JEV/H/D026B B |  | 26000 | 19.9 | 20200 | 4.1 | 2.1667
205996644 | Ground Loop | Johnson Controls | JEV/H/D038B B |  | 39000 | 20.3 | 29700 | 4.4 | 3.25
205996645 | Ground Loop | Johnson Controls | JEV/H/D049B B |  | 49600 | 19.3 | 36400 | 4 | 4.1333
205996646 | Ground Loop | Johnson Controls | JEV/H/D064B B |  | 66200 | 18.8 | 48700 | 3.9 | 5.5167
206185518 | Ground Loop | DAIKIN | WGCH015A1*G/J*T |  | 15300 | 18 | 10700 | 3.6 | 1.275
206185519 | Ground Loop | DAIKIN | WGCH015A1*G/J*C |  | 15300 | 18 | 10700 | 3.6 | 1.275
206185527 | Ground Loop | DAIKIN | WGCH015J1*G/J*T |  | 14800 | 18 | 10500 | 3.6 | 1.2333
206185528 | Ground Loop | DAIKIN | WGCH015J1*G/J*C |  | 14800 | 18 | 10500 | 3.6 | 1.2333
206185532 | Ground Loop | DAIKIN | WGCH019E1*G/J*P |  | 18000 | 17.9 | 13600 | 3.8 | 1.5
206185533 | Ground Loop | DAIKIN | WGCH019E1*G/J*T |  | 18300 | 19 | 13200 | 3.9 | 1.525
214776169 | Ground Loop | TRANE | GETK0151-5 |  | 15800 | 17.1 | 12500 | 3.93 | 1.3167
214776171 | Ground Loop | TRANE | GETK0241-5 |  | 25200 | 18.5 | 20100 | 3.82 | 2.1
214776189 | Ground Loop | TRANE | GETK0152-5 |  | 15800 | 17.1 | 12500 | 3.93 | 1.3167
214776190 | Ground Loop | TRANE | GETK0157-5 |  | 15800 | 17.1 | 12500 | 3.93 | 1.3167
215268669 | Ground Loop | WaterFurnace | V5A(V/H)036*S0**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
215268670 | Ground Loop | WaterFurnace | V5A(V/H)042*S0**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
215268671 | Ground Loop | WaterFurnace | V5A(V/H)048*S0**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25
215268672 | Ground Loop | WaterFurnace | V5A(V/H)060*S0**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
215268673 | Ground Loop | WaterFurnace | V5A(V/H)072*S0**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
215268675 | Ground Loop | WaterFurnace | V5A(V/H)012*R2**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833
215268676 | Ground Loop | WaterFurnace | V5A(V/H)015*R2**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
217351073 | Ground Loop | BOSCH | CP036-1CSC-*****A | BIVA-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833
217351074 | Ground Loop | BOSCH | CP036-1CSN-*****A | BIVA-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667
217351075 | Ground Loop | BOSCH | CP048-1CSC-*****A | BIVA-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167
217351076 | Ground Loop | BOSCH | CP048-1CSN-*****A | BIVA-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833
217351077 | Ground Loop | BOSCH | CP060-1CSC-*****A | BIVA-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667
217351078 | Ground Loop | BOSCH | CP060-1CSN-*****A | BIVA-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05
217351079 | Ground Loop | BOSCH | CP024-1CSC-*****A | BMAC2430BBTA | 25400 | 18.1 | 18800 | 4.1 | 2.1167
217351080 | Ground Loop | BOSCH | CP024-1CSN-*****A | BMAC2430BBTA | 26000 | 18.3 | 18800 | 4.3 | 2.1667
217351082 | Ground Loop | BOSCH | CP036-1CSN-*****A | BMAC3036BBTA | 38200 | 17.2 | 30800 | 4.2 | 3.1833
217351083 | Ground Loop | BOSCH | CP048-1CSC-*****A | BMAC4248CBTA | 50200 | 17.5 | 37200 | 3.9 | 4.1833
217351084 | Ground Loop | BOSCH | CP048-1CSN-*****A | BMAC4248CBTA | 51600 | 17.8 | 38200 | 4.1 | 4.3
217351087 | Ground Loop | BOSCH-GEO | RP024-1CSC-*****A | BIVA-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667
217351088 | Ground Loop | BOSCH-GEO | RP024-1CSN-*****A | BIVA-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667
217351089 | Ground Loop | BOSCH-GEO | RP036-1CSC-*****A | BIVA-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833
217351090 | Ground Loop | BOSCH-GEO | RP036-1CSN-*****A | BIVA-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667
217351091 | Ground Loop | BOSCH-GEO | RP048-1CSC-*****A | BIVA-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167
217351092 | Ground Loop | BOSCH-GEO | RP048-1CSN-*****A | BIVA-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833
217351093 | Ground Loop | BOSCH-GEO | RP060-1CSC-*****A | BIVA-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667
217351094 | Ground Loop | BOSCH-GEO | RP060-1CSN-*****A | BIVA-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05
217351095 | Ground Loop | BOSCH-GEO | RP024-1CSC-*****A | BMAC2430BBTA | 25400 | 18.1 | 18800 | 4.1 | 2.1167
217351096 | Ground Loop | BOSCH-GEO | RP024-1CSN-*****A | BMAC2430BBTA | 26000 | 18.3 | 18800 | 4.3 | 2.1667
217351098 | Ground Loop | BOSCH-GEO | RP036-1CSN-*****A | BMAC3036BBTA | 38200 | 17.2 | 30800 | 4.2 | 3.1833
217351099 | Ground Loop | BOSCH-GEO | RP048-1CSC-*****A | BMAC4248CBTA | 50200 | 17.5 | 37200 | 3.9 | 4.1833
217351100 | Ground Loop | BOSCH-GEO | RP048-1CSN-*****A | BMAC4248CBTA | 51600 | 17.8 | 38200 | 4.1 | 4.3
217351103 | Ground Loop | GEO-THERMAL SPLIT | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 26000 | 18.5 | 18800 | 4.1 | 2.1667
217351104 | Ground Loop | GEO-THERMAL SPLIT | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 25400 | 18.1 | 18400 | 4 | 2.1167
217351107 | Ground Loop | GEO-THERMAL SPLIT | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 39000 | 18.5 | 27400 | 3.7 | 3.25
217351108 | Ground Loop | GEO-THERMAL SPLIT | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 38000 | 18.1 | 26800 | 3.7 | 3.1667
217351109 | Ground Loop | GEO-THERMAL SPLIT | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 48500 | 17.1 | 37800 | 4 | 4.0417
217351111 | Ground Loop | GEO-THERMAL SPLIT | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 60500 | 17.6 | 47000 | 3.7 | 5.0417
217351112 | Ground Loop | GEO-THERMAL SPLIT | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 59500 | 17.3 | 46000 | 3.7 | 4.9583
217351114 | Ground Loop | GEO-THERMAL SPLIT | GZ024SA*C******1 | CAAMP2***AMA | 25900 | 17.5 | 18900 | 3.8 | 2.1583
217351115 | Ground Loop | GEO-THERMAL SPLIT | GZ024SA*N******1 | CAAMP2***AMA | 25400 | 17.1 | 18500 | 3.7 | 2.1167
217351116 | Ground Loop | GEO-THERMAL SPLIT | GZ036SA*C******1 | CAAMP3***AMA | 37400 | 17.7 | 27600 | 3.6 | 3.1167
217351117 | Ground Loop | GEO-THERMAL SPLIT | GZ036SA*N******1 | CAAMP3***AMA | 36600 | 17.4 | 27100 | 3.6 | 3.05
217351118 | Ground Loop | GEO-THERMAL SPLIT | GZ048SA*C******1 | CAAMP4***AMA | 49000 | 17.1 | 37900 | 3.9 | 4.0833
217351120 | Ground Loop | GEO-THERMAL SPLIT | GZ060SA*C******1 | CAAMP6***AMA | 63900 | 17.7 | 48300 | 3.8 | 5.325
217351121 | Ground Loop | GEO-THERMAL SPLIT | GZ060SA*N******1 | CAAMP6***AMA | 62600 | 17.3 | 47300 | 3.7 | 5.2167
217351122 | Ground Loop | GEO-THERMAL SPLIT | GZ072SA*C******1 | CAAMP6***AMA | 70000 | 17.5 | 55200 | 3.6 | 5.8333
217351671 | Ground Loop | BOSCH | RP024-1CSC-*****A | BIVA-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667
217351672 | Ground Loop | BOSCH | RP024-1CSN-*****A | BIVA-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667
217351673 | Ground Loop | BOSCH | RP036-1CSC-*****A | BIVA-36RCB-M20X | 38200 | 17.6 | 29200 | 4 | 3.1833
217351674 | Ground Loop | BOSCH | RP036-1CSN-*****A | BIVA-36RCB-M20X | 39200 | 18.6 | 29800 | 4.1 | 3.2667
202921908 | Ground Loop | BOSCH | EP036-1VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202921909 | Ground Loop | BOSCH | EP036-3VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202921910 | Ground Loop | BOSCH | EP036-4VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202921911 | Ground Loop | BOSCH-GEO | BP036-1VT*-*****B |  | 37500 | 19.7 | 26000 | 3.9 | 3.125
202921912 | Ground Loop | BOSCH | EP036-1HZ*-*****B |  | 37500 | 18.7 | 26000 | 3.9 | 3.125
202434117 | Ground Loop | BOSCH | LV024-1VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434119 | Ground Loop | BOSCH | LV024-1HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434121 | Ground Loop | BOSCH | LV024-1VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434123 | Ground Loop | BOSCH | LV024-1HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434125 | Ground Loop | BOSCH | LV036-1VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434127 | Ground Loop | BOSCH | LV036-1HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434143 | Ground Loop | BOSCH | LV024-3VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434144 | Ground Loop | BOSCH | LV024-4VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434145 | Ground Loop | BOSCH | LV024-2VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434149 | Ground Loop | BOSCH | LV024-3HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434150 | Ground Loop | BOSCH | LV024-4HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434151 | Ground Loop | BOSCH | LV024-2HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434155 | Ground Loop | BOSCH | LV024-3VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434156 | Ground Loop | BOSCH | LV024-4VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434157 | Ground Loop | BOSCH | LV024-2VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434161 | Ground Loop | BOSCH | LV024-3HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434162 | Ground Loop | BOSCH | LV024-4HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434163 | Ground Loop | BOSCH | LV024-2HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
207083977 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C/A5/EE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
207083981 | Ground Loop | CARRIER | 50PCV036J/K*C/A5/EE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
207083985 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C/A6/FE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
207083989 | Ground Loop | CARRIER | 50PCV036J/K*C/A6/FE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
214063756 | Ground Loop | GeoSmart Energy | GBV/GBH024**2*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
214063757 | Ground Loop | GeoSmart Energy | GBV/GBH024**2*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
214063758 | Ground Loop | GeoSmart Energy | GBV/GBH026**0*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
214063759 | Ground Loop | GeoSmart Energy | GBV/GBH026**0*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
214063760 | Ground Loop | GeoSmart Energy | GBV/GBH026**2*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
214063761 | Ground Loop | GeoSmart Energy | GBV/GBH026**2*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
214063762 | Ground Loop | GeoSmart Energy | GBV/GBH030**0*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
214063763 | Ground Loop | GeoSmart Energy | GBV/GBH030**0*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
214063764 | Ground Loop | GeoSmart Energy | GBV/GBH030**0*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
214063765 | Ground Loop | GeoSmart Energy | GBV/GBH030**2*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
214063766 | Ground Loop | GeoSmart Energy | GBV/GBH030**2*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
214063767 | Ground Loop | GeoSmart Energy | GBV/GBH030**2*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
214063768 | Ground Loop | GeoSmart Energy | GBV/GBH036**0*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
214063769 | Ground Loop | GeoSmart Energy | GBV/GBH036**0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
214063770 | Ground Loop | GeoSmart Energy | GBV/GBH036**0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
214063771 | Ground Loop | GeoSmart Energy | GBV/GBH036**2*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
214063772 | Ground Loop | GeoSmart Energy | GBV/GBH036**2*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
214063773 | Ground Loop | GeoSmart Energy | GBV/GBH036**2*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
214063774 | Ground Loop | GeoSmart Energy | GBV/GBH038**0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
214063775 | Ground Loop | GeoSmart Energy | GBV/GBH038**0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
214063776 | Ground Loop | GeoSmart Energy | GBV/GBH038**2*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
214063777 | Ground Loop | GeoSmart Energy | GBV/GBH038**2*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
214063778 | Ground Loop | GeoSmart Energy | GBV/GBH042**0*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
214063779 | Ground Loop | GeoSmart Energy | GBV/GBH042**0*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
214063780 | Ground Loop | GeoSmart Energy | GBV/GBH049**0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
214063781 | Ground Loop | GeoSmart Energy | GBV/GBH049**0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
214063782 | Ground Loop | GeoSmart Energy | GBV/GBH060**0*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
214063783 | Ground Loop | GeoSmart Energy | GBV/GBH060**0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
214063784 | Ground Loop | GeoSmart Energy | GBV/GBH060**0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
214063785 | Ground Loop | GeoSmart Energy | GBV/GBH064**0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
214063786 | Ground Loop | GeoSmart Energy | GBV/GBH064**0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
214063788 | Ground Loop | GeoSmart Energy | GBV/GBH070**0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
214063789 | Ground Loop | GeoSmart Energy | GBV/GBH070**0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
214063790 | Ground Loop | GeoSmart Energy | GBV/GBH072**0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
214063791 | Ground Loop | GeoSmart Energy | GBV/GBH072**0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
9008839 | Ground Loop | BOSCH | ES025-1CF/HZ/VT*-*****A |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917
9008840 | Ground Loop | BOSCH | ES025-2CF/HZ/VT*-*****A |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917
9009353 | Ground Loop | FHP | ES025-1CF/HZ/VT*-*****A |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917
216625704 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D0**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625705 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D0**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625706 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D0**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625707 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D2**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625708 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D3**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625709 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D3**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625710 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D3**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625711 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D4**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625712 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D4**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625713 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*D4**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625714 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S0**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625715 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S0**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625716 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S0**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625717 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S2**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625718 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S3**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625719 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S3**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625720 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S3**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625721 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S4**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625722 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S4**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625723 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)048*S4**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625724 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D0**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216625725 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D0**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216625726 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D3**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216625727 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D3**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216625728 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D4**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216625729 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*D4**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216625730 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S0**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625731 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S0**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625732 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S3**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625733 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S3**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625734 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S4**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625735 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)060*S4**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625736 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D0**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216625737 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D0**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216625738 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D3**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216625739 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D3**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216625740 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D4**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216625741 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*D4**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216625742 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S0**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216625743 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S0**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216625744 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S3**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216625745 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S3**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216625746 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S4**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216625747 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)072*S4**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216625750 | Ground Loop | GeoSmart Energy | S5A(V/H)012*R0**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833
216625751 | Ground Loop | GeoSmart Energy | S5A(V/H)012*R2**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833
216625752 | Ground Loop | GeoSmart Energy | S5A(V/H)015*R0**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
216625753 | Ground Loop | GeoSmart Energy | S5A(V/H)015*R0**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
216625754 | Ground Loop | GeoSmart Energy | S5A(V/H)015*R2**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
216625755 | Ground Loop | GeoSmart Energy | S5A(V/H)015*R2**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
216625756 | Ground Loop | GeoSmart Energy | S5A(V/H)018*D0**1 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583
216625757 | Ground Loop | GeoSmart Energy | S5A(V/H)018*D0**4 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583
216625758 | Ground Loop | GeoSmart Energy | S5A(V/H)018*R0**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
216625759 | Ground Loop | GeoSmart Energy | S5A(V/H)018*R0**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
7410095 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25
7410164 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25
7410223 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**0*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25
7410291 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25
7410355 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25
7410435 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH015**2*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25
7410657 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**0*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
7410825 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**2*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
7410908 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH018**2*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
7411002 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH024**0*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
215400079 | Ground Loop | DAIKIN | WSMV015E1*G/J*P |  | 16100 | 20.21 | 11200 | 3.65 | 1.3417
215400081 | Ground Loop | DAIKIN | WSMV015E1*G/J*T |  | 16300 | 21.12 | 11100 | 3.74 | 1.3583
215400083 | Ground Loop | DAIKIN | WSMV015E1*G/J*C |  | 16300 | 21.12 | 11100 | 3.74 | 1.3583
215400087 | Ground Loop | DAIKIN | WSMV019E1*G/J*T |  | 20600 | 20.26 | 15100 | 3.69 | 1.7167
215400089 | Ground Loop | DAIKIN | WSMV019E1*G/J*C |  | 20600 | 20.26 | 15100 | 3.69 | 1.7167
215400092 | Ground Loop | DAIKIN | WSMV024E1*G/J*P |  | 25500 | 19.55 | 18900 | 3.72 | 2.125
215400093 | Ground Loop | DAIKIN | WSMV024F3*G/J*P |  | 25500 | 19.07 | 18900 | 3.62 | 2.125
217642983 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S4**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
217642984 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S4**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
202434372 | Ground Loop | FHP | LV024-1VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434373 | Ground Loop | FHP | LV024-3VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434374 | Ground Loop | FHP | LV024-4VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434375 | Ground Loop | FHP | LV024-2VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434380 | Ground Loop | FHP | LV024-1HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434381 | Ground Loop | FHP | LV024-3HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434382 | Ground Loop | FHP | LV024-4HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434383 | Ground Loop | FHP | LV024-2HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434388 | Ground Loop | FHP | LV024-1VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434389 | Ground Loop | FHP | LV024-3VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434390 | Ground Loop | FHP | LV024-4VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434391 | Ground Loop | FHP | LV024-2VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434396 | Ground Loop | FHP | LV024-1HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434397 | Ground Loop | FHP | LV024-3HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434398 | Ground Loop | FHP | LV024-4HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434399 | Ground Loop | FHP | LV024-2HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
207177431 | Ground Loop | TRANE | GEVG009A |  | 8900 | 17.8 | 6700 | 3.7 | 0.74167
207177432 | Ground Loop | TRANE | GEVG0097 |  | 8900 | 17.8 | 6700 | 3.7 | 0.74167
207177433 | Ground Loop | TRANE | GEVG012A |  | 12100 | 17.6 | 9400 | 3.7 | 1.0083
207177434 | Ground Loop | TRANE | GEVG0127 |  | 12100 | 17.6 | 9400 | 3.7 | 1.0083
207177435 | Ground Loop | TRANE | GEVG015A |  | 15500 | 17.4 | 12300 | 3.6 | 1.2917
207177436 | Ground Loop | TRANE | GEVG0157 |  | 15500 | 17.4 | 12300 | 3.6 | 1.2917
207177437 | Ground Loop | TRANE | GEVG018A |  | 18100 | 17.7 | 14300 | 3.6 | 1.5083
207177438 | Ground Loop | TRANE | GEVG0187 |  | 18100 | 17.7 | 14300 | 3.6 | 1.5083
207177439 | Ground Loop | TRANE | GEVG024A |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667
207177440 | Ground Loop | TRANE | GEVG024B |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667
213614585 | Ground Loop | DAIKIN | WSCH015E1*G/J*T |  | 15600 | 19 | 11900 | 3.6 | 1.3
213614586 | Ground Loop | DAIKIN | WSCH015E1*G/J*C |  | 15600 | 19 | 11900 | 3.6 | 1.3
213710596 | Ground Loop | DAIKIN | WSSH007A1*H*T |  | 7500 | 22.3 | 5200 | 3.7 | 0.625
213710598 | Ground Loop | DAIKIN | WSSH007E1*H*T |  | 7500 | 22.3 | 5200 | 3.7 | 0.625
213710600 | Ground Loop | DAIKIN | WSSH007J1*H*T |  | 7500 | 22.3 | 5200 | 3.7 | 0.625
213710604 | Ground Loop | DAIKIN | WSSH009A1*H*T |  | 9500 | 21 | 7000 | 3.91 | 0.79167
213710605 | Ground Loop | DAIKIN | WSSH009E1*H*T |  | 9500 | 21 | 7000 | 3.91 | 0.79167
213710611 | Ground Loop | DAIKIN | WSSH012A1*H*T |  | 12200 | 20.1 | 9100 | 3.9 | 1.0167
213710613 | Ground Loop | DAIKIN | WSSH012E1*H*T |  | 12000 | 20.3 | 9100 | 3.9 | 1
205973168 | Ground Loop | Enertech | ERE060D |  | 62100 | 17.6 | 45600 | 3.6 | 5.175
205973779 | Ground Loop | COMFORT-AIRE | HEV/H060D |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667
205973780 | Ground Loop | CENTURY | HEV/H060D |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667
214772143 | Ground Loop | TRANE | DXHK048A |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583
214772144 | Ground Loop | TRANE | DXHK060A |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083
214772145 | Ground Loop | TRANE | DXHK070A |  | 65100 | 18.9 | 51700 | 4.1 | 5.425
214772146 | Ground Loop | TRANE | DXVK024B |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417
214772147 | Ground Loop | TRANE | DXVK0244 |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417
214772148 | Ground Loop | TRANE | DXVK036B |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167
214772149 | Ground Loop | TRANE | DXVK0364 |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167
214772150 | Ground Loop | TRANE | DXVK048B |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583
214772151 | Ground Loop | TRANE | DXVK0484 |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583
214772152 | Ground Loop | TRANE | DXVK060B |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083
214772153 | Ground Loop | TRANE | DXVK0604 |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083
214772154 | Ground Loop | TRANE | DXVK070B |  | 65100 | 18.9 | 51700 | 4.1 | 5.425
214772155 | Ground Loop | TRANE | DXVK0704 |  | 65100 | 18.9 | 51700 | 4.1 | 5.425
214772156 | Ground Loop | TRANE | DXHK024B |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417
214772157 | Ground Loop | TRANE | DXHK0244 |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417
214772158 | Ground Loop | TRANE | DXHK036B |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167
214772159 | Ground Loop | TRANE | DXHK0364 |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167
214772160 | Ground Loop | TRANE | DXHK048B |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583
214772161 | Ground Loop | TRANE | DXHK0484 |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583
214772162 | Ground Loop | TRANE | DXHK060B |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083
214772163 | Ground Loop | TRANE | DXHK0604 |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083
214772164 | Ground Loop | TRANE | DXHK070B |  | 65100 | 18.9 | 51700 | 4.1 | 5.425
214772165 | Ground Loop | TRANE | DXHK0704 |  | 65100 | 18.9 | 51700 | 4.1 | 5.425
214772166 | Ground Loop | TRANE | DXVK0247 |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417
214772167 | Ground Loop | TRANE | DXVK0367 |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167
214772168 | Ground Loop | TRANE | DXHK0247 |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417
214772169 | Ground Loop | TRANE | DXHK0367 |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167
214773312 | Ground Loop | TRANE | GEVK090 |  | 95600 | 18.9 | 70700 | 3.69 | 7.9667
214776121 | Ground Loop | TRANE | GEVK120 |  | 130200 | 19.1 | 97100 | 3.67 | 10.85
214776125 | Ground Loop | TRANE | GEVK0904 |  | 95600 | 18.9 | 70700 | 3.69 | 7.9667
214776126 | Ground Loop | TRANE | GEVK0908 |  | 95600 | 18.9 | 70700 | 3.69 | 7.9667
214776135 | Ground Loop | TRANE | GEVK1203 |  | 130200 | 19.1 | 97100 | 3.67 | 10.85
214776136 | Ground Loop | TRANE | GEVK1208 |  | 130200 | 19.1 | 97100 | 3.67 | 10.85
200083647 | Ground Loop | CENTURY | HZV/H/D048B |  | 49600 | 19.3 | 36400 | 4 | 4.1333
200083648 | Ground Loop | COMFORT-AIRE | HZV/H/D060B |  | 66200 | 18.8 | 48700 | 3.9 | 5.5167
200083649 | Ground Loop | CENTURY | HZV/H/D060B |  | 66200 | 18.8 | 48700 | 3.9 | 5.5167
200083684 | Ground Loop | COMFORT-AIRE | HZS024B | WDG024**A-*B | 24700 | 17.7 | 18800 | 3.6 | 2.0583
200083685 | Ground Loop | CENTURY | HZS024B | WDG024**A-*B | 24700 | 17.7 | 18800 | 3.6 | 2.0583
200083686 | Ground Loop | COMFORT-AIRE | HZS024B | WDG024**B-*B | 25800 | 18.3 | 18700 | 3.8 | 2.15
200083687 | Ground Loop | CENTURY | HZS024B | WDG024**B-*B | 25800 | 18.3 | 18700 | 3.8 | 2.15
200083688 | Ground Loop | COMFORT-AIRE | HZS024B | MWG24*A-B | 24000 | 17.4 | 18800 | 3.9 | 2
200083689 | Ground Loop | CENTURY | HZS024B | MWG24*A-B | 24000 | 17.4 | 18800 | 3.9 | 2
200083690 | Ground Loop | COMFORT-AIRE | HZS024B | MWG24*C-B | 26000 | 18 | 18600 | 3.8 | 2.1667
200083691 | Ground Loop | CENTURY | HZS024B | MWG24*C-B | 26000 | 18 | 18600 | 3.8 | 2.1667
200083692 | Ground Loop | COMFORT-AIRE | HZS024B | MWG24*B-B | 24000 | 17.4 | 18800 | 3.9 | 2
200083693 | Ground Loop | CENTURY | HZS024B | MWG24*B-B | 24000 | 17.4 | 18800 | 3.9 | 2
200083694 | Ground Loop | COMFORT-AIRE | HZS036B | MWG36**-B | 38000 | 17.3 | 26600 | 3.7 | 3.1667
200083695 | Ground Loop | CENTURY | HZS036B | MWG36**-B | 38000 | 17.3 | 26600 | 3.7 | 3.1667
200083696 | Ground Loop | COMFORT-AIRE | HZS036B | WDG036***-*B | 37700 | 17.8 | 26200 | 3.8 | 3.1417
200083697 | Ground Loop | CENTURY | HZS036B | WDG036***-*B | 37700 | 17.8 | 26200 | 3.8 | 3.1417
206185538 | Ground Loop | DAIKIN | WGCH019J1*G/J*T |  | 18300 | 17.6 | 13200 | 3.8 | 1.525
206185539 | Ground Loop | DAIKIN | WGCH019J1*G/J*C |  | 18300 | 17.6 | 13200 | 3.8 | 1.525
214823484 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)036BD1**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
214823485 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)042BD1**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
215405064 | Ground Loop | DAIKIN | WSSV060E1*H*T |  | 66300 | 20 | 48800 | 4 | 5.525
215405065 | Ground Loop | DAIKIN | WSSV060F3*H*T |  | 66300 | 19.8 | 48800 | 3.96 | 5.525
215405066 | Ground Loop | DAIKIN | WSSV060K3*H*T |  | 66300 | 19.8 | 48800 | 3.92 | 5.525
215405067 | Ground Loop | DAIKIN | WSSV060L3*H*T |  | 66300 | 19.4 | 48800 | 3.88 | 5.525
215405068 | Ground Loop | DAIKIN | WSSV060E1*H*C |  | 66300 | 20 | 48800 | 4 | 5.525
215405069 | Ground Loop | DAIKIN | WSSV060F3*H*C |  | 66300 | 19.8 | 48800 | 3.96 | 5.525
215405070 | Ground Loop | DAIKIN | WSSV060K3*H*C |  | 66300 | 19.8 | 48800 | 3.92 | 5.525
215405071 | Ground Loop | DAIKIN | WSSV060L3*H*C |  | 66300 | 19.4 | 48800 | 3.88 | 5.525
215405076 | Ground Loop | DAIKIN | WSSV070E1*H*T |  | 75400 | 19.4 | 54700 | 3.8 | 6.2833
215405077 | Ground Loop | DAIKIN | WSSV070F3*H*T |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833
215405078 | Ground Loop | DAIKIN | WSSV070K3*H*T |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833
215405079 | Ground Loop | DAIKIN | WSSV070L3*H*T |  | 75400 | 18.82 | 54700 | 3.69 | 6.2833
215405084 | Ground Loop | DAIKIN | WSSV070E1*H*C |  | 75400 | 19.4 | 54700 | 3.8 | 6.2833
215405085 | Ground Loop | DAIKIN | WSSV070F3*H*C |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833
215405086 | Ground Loop | DAIKIN | WSSV070K3*H*C |  | 75400 | 19.21 | 54700 | 3.76 | 6.2833
215405087 | Ground Loop | DAIKIN | WSSV070L3*H*C |  | 75400 | 18.82 | 54700 | 3.69 | 6.2833
215415734 | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)024A*B |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333
215415735 | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)024A*C |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333
215415736 | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)024A*VB |  | 25800 | 18 | 19000 | 3.7 | 2.15
215415737 | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)024A*VC |  | 25800 | 18 | 19000 | 3.7 | 2.15
215415740 | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)030A*VB |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417
215415741 | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)030A*VC |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417
215415744 | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)036A*VB |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333
215415745 | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)036A*VC |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333
217754394 | Ground Loop | DAIKIN | WSSH036K1*H*C |  | 40300 | 21.19 | 27600 | 3.6 | 3.3583
217754396 | Ground Loop | DAIKIN | WSSH042F1*H*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667
217754397 | Ground Loop | DAIKIN | WSSH042K1*H*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667
217754399 | Ground Loop | DAIKIN | WSSH042F1*H*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667
217754400 | Ground Loop | DAIKIN | WSSH042K1*H*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667
217754402 | Ground Loop | DAIKIN | WSSH048F1*H*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667
217754403 | Ground Loop | DAIKIN | WSSH048K1*H*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667
217754404 | Ground Loop | DAIKIN | WSSH048L1*H*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667
217754406 | Ground Loop | DAIKIN | WSSH048F1*H*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667
217754407 | Ground Loop | DAIKIN | WSSH048K1*H*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667
217754408 | Ground Loop | DAIKIN | WSSH048L1*H*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667
217754418 | Ground Loop | DAIKIN | WSSH070F1*H*T |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083
217754419 | Ground Loop | DAIKIN | WSSH070K1*H*T |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083
217754422 | Ground Loop | DAIKIN | WSSH070F1*H*C |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083
217754423 | Ground Loop | DAIKIN | WSSH070K1*H*C |  | 73300 | 19.53 | 53600 | 3.6 | 6.1083
7519551 | Ground Loop | TETCO | TVS024*A |  | 26000 | 19.7 | 19400 | 4 | 2.1667
7519552 | Ground Loop | GEOCOMFORT | GVS024*2 |  | 26000 | 19.7 | 19400 | 4 | 2.1667
7519553 | Ground Loop | HYDRON MODULE | HVS024*2 |  | 26000 | 19.7 | 19400 | 4 | 2.1667
7519554 | Ground Loop | TETCO | TVS024*2 |  | 26000 | 19.7 | 19400 | 4 | 2.1667
7519555 | Ground Loop | GEOCOMFORT | GVS024*3 |  | 26000 | 19.7 | 19400 | 4 | 2.1667
7519556 | Ground Loop | HYDRON MODULE | HVS024*3 |  | 26000 | 19.7 | 19400 | 4 | 2.1667
7519557 | Ground Loop | TETCO | TVS024*3 |  | 26000 | 19.7 | 19400 | 4 | 2.1667
7519558 | Ground Loop | GEOCOMFORT | GVS024*4 |  | 26000 | 19.7 | 19400 | 4 | 2.1667
7519559 | Ground Loop | HYDRON MODULE | HVS024*4 |  | 26000 | 19.7 | 19400 | 4 | 2.1667
7519560 | Ground Loop | TETCO | TVS024*4 |  | 26000 | 19.7 | 19400 | 4 | 2.1667
7519561 | Ground Loop | GEOCOMFORT | GVS030*A |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083
7519562 | Ground Loop | HYDRON MODULE | HVS030*A |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083
7519563 | Ground Loop | TETCO | TVS030*A |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083
7519564 | Ground Loop | GEOCOMFORT | GVS030*2 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083
7519565 | Ground Loop | HYDRON MODULE | HVS030*2 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083
7519566 | Ground Loop | TETCO | TVS030*2 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083
203113888 | Ground Loop | GEOSTAR | 103J036**1 | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55
203113890 | Ground Loop | GEOSTAR | 103J042**1 | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15
203113892 | Ground Loop | GEOSTAR | 103J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3
203113894 | Ground Loop | GEOSTAR | 104J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3
203143108 | Ground Loop | GEOCOMFORT | GVS041 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225
203143111 | Ground Loop | GEOCOMFORT | GVS041*2 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225
203143114 | Ground Loop | GEOCOMFORT | GVS041*3 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225
203143119 | Ground Loop | GEOCOMFORT | GVS041*4 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225
203143124 | Ground Loop | HYDRON MODULE | HVS041 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225
203143129 | Ground Loop | HYDRON MODULE | HVS041*2 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225
203143133 | Ground Loop | HYDRON MODULE | HVS041*3 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225
203143138 | Ground Loop | HYDRON MODULE | HVS041*4 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225
203143143 | Ground Loop | TETCO | TVS041 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225
203143148 | Ground Loop | TETCO | TVS041*2 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225
203143153 | Ground Loop | TETCO | TVS041*3 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225
203143157 | Ground Loop | TETCO | TVS041*4 |  | 38700 | 17.1 | 31100 | 3.6 | 3.225
203143746 | Ground Loop | GEOCOMFORT | GVS041*****1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167
203143749 | Ground Loop | GEOCOMFORT | GVS041*2***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167
203143752 | Ground Loop | GEOCOMFORT | GVS041*3***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167
203143764 | Ground Loop | HYDRON MODULE | HVS041*****1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167
203143767 | Ground Loop | HYDRON MODULE | HVS041*2***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167
203143770 | Ground Loop | HYDRON MODULE | HVS041*3***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167
203143781 | Ground Loop | TETCO | TVS041*****1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167
203143785 | Ground Loop | TETCO | TVS041*2***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167
203143790 | Ground Loop | TETCO | TVS041*3***1 |  | 39800 | 17.8 | 31200 | 3.7 | 3.3167
203238019 | Ground Loop | BOSCH-GEO | BP042-1HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203238919 | Ground Loop | BOSCH-GEO | SM024-1VT/CFN-*****A |  | 26600 | 18.2 | 18000 | 3.7 | 2.2167
203238923 | Ground Loop | BOSCH-GEO | SM024-1HZC-*****A |  | 26600 | 19.9 | 18000 | 3.7 | 2.2167
203238926 | Ground Loop | BOSCH-GEO | SM024-1HZN-*****A |  | 26600 | 18.3 | 18000 | 3.7 | 2.2167
203253412 | Ground Loop | BOSCH | BP042-1HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203253413 | Ground Loop | BOSCH | SM024-1HZC-*****A |  | 26600 | 19.9 | 18000 | 3.7 | 2.2167
203253414 | Ground Loop | BOSCH | SM024-1HZC-*****C |  | 26600 | 19.9 | 18000 | 3.7 | 2.2167
203253415 | Ground Loop | BOSCH | SM024-1HZN-*****A |  | 26600 | 18.3 | 18000 | 3.7 | 2.2167
203253416 | Ground Loop | BOSCH | SM024-1HZN-*****C |  | 26600 | 18.3 | 18000 | 3.7 | 2.2167
203254061 | Ground Loop | BOSCH-GEO | SM070-1VT*-*****C |  | 71500 | 17.3 | 56000 | 3.7 | 5.9583
203254465 | Ground Loop | BOSCH | SM070-1VT*******C |  | 71500 | 17.3 | 56000 | 3.7 | 5.9583
203254606 | Ground Loop | CARRIER | GB042H******1**1 |  | 40600 | 19.5 | 26800 | 4 | 3.3833
205754414 | Ground Loop | ICE AIR LLC | 8VSHPGE30** |  | 30000 | 17.3 | 21900 | 3.6 | 2.5
205754885 | Ground Loop | Johnson Controls | JCH/V015A*W/K B |  | 14800 | 18 | 11000 | 3.6 | 1.2333
205754886 | Ground Loop | SKYMARK | JCH/V015A*W/K C |  | 14800 | 18 | 11000 | 3.6 | 1.2333
205754889 | Ground Loop | Johnson Controls | JCH/V018A*W/K B |  | 19500 | 17.1 | 14100 | 3.7 | 1.625
205754890 | Ground Loop | SKYMARK | JCH/V018A*W/K C |  | 19500 | 17.1 | 14100 | 3.7 | 1.625
214595658 | Ground Loop | AAON, Inc. | RN-009-2-0-FCAY-S0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425
214595659 | Ground Loop | AAON, Inc. | RN-009-3-0-FCAY-S0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425
214595660 | Ground Loop | AAON, Inc. | RN-009-4-0-FCAY-S0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425
214595661 | Ground Loop | AAON, Inc. | RN-009-2-0-GCAY-V0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425
214595662 | Ground Loop | AAON, Inc. | RN-009-3-0-GCAY-V0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425
214595663 | Ground Loop | AAON, Inc. | RN-009-4-0-GCAY-V0-10-000-A |  | 101100 | 18.7 | 66200 | 3.8 | 8.425
215224824 | Ground Loop | KEEPRITE | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224825 | Ground Loop | TEMPSTAR | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224826 | Ground Loop | COMFORTMAKER | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224827 | Ground Loop | DAY & NIGHT | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224828 | Ground Loop | HEIL | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224829 | Ground Loop | ARCOAIRE | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224830 | Ground Loop | KEEPRITE | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224831 | Ground Loop | TEMPSTAR | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224832 | Ground Loop | COMFORTMAKER | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224833 | Ground Loop | DAY & NIGHT | HBR24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
217193306 | Ground Loop | WaterFurnace | V7A(V/H)024*V0**1* |  | 25500 | 23 | 17800 | 3.9 | 2.125
217193307 | Ground Loop | WaterFurnace | V7A(V/H)036*V0**1* |  | 39000 | 20 | 29000 | 3.8 | 3.25
217193308 | Ground Loop | WaterFurnace | V7A(V/H)048*V0**1* |  | 48000 | 20 | 38000 | 3.8 | 4
217193309 | Ground Loop | WaterFurnace | V7A(V/H)060*V0**1* |  | 62500 | 17.5 | 46500 | 3.7 | 5.2083
217193552 | Ground Loop | WaterFurnace | V7A(V/H)024*V3**1* |  | 25500 | 23 | 17800 | 3.9 | 2.125
217193553 | Ground Loop | WaterFurnace | V7A(V/H)024*V4**1* |  | 25500 | 23 | 17800 | 3.9 | 2.125
217193554 | Ground Loop | WaterFurnace | V7A(V/H)036*V3**1* |  | 39000 | 20 | 29000 | 3.8 | 3.25
217193555 | Ground Loop | WaterFurnace | V7A(V/H)036*V4**1* |  | 39000 | 20 | 29000 | 3.8 | 3.25
217193556 | Ground Loop | WaterFurnace | V7A(V/H)048*V3**1* |  | 48000 | 20 | 38000 | 3.8 | 4
217193557 | Ground Loop | WaterFurnace | V7A(V/H)048*V4**1* |  | 48000 | 20 | 38000 | 3.8 | 4
217193558 | Ground Loop | WaterFurnace | V7A(V/H)060*V3**1* |  | 62500 | 17.5 | 46500 | 3.7 | 5.2083
217193559 | Ground Loop | WaterFurnace | V7A(V/H)060*V4**1* |  | 62500 | 17.5 | 46500 | 3.7 | 5.2083
217212043 | Ground Loop | FHP | CP024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
217212044 | Ground Loop | FHP | CP024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
217212045 | Ground Loop | FHP | CP024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
217212046 | Ground Loop | FHP | CP024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
217212048 | Ground Loop | FHP | CP024-2HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
217212049 | Ground Loop | FHP | CP024-2HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
217212050 | Ground Loop | FHP | CP024-2VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
217212051 | Ground Loop | FHP | CP024-2VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
217212052 | Ground Loop | FHP | CP024-3HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
217212054 | Ground Loop | FHP | CP024-3HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
217212055 | Ground Loop | FHP | CP024-3VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
217212056 | Ground Loop | FHP | CP024-3VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
201864513 | Ground Loop | GEOCOMFORT | GZT024*A |  | 26400 | 18.3 | 18300 | 3.9 | 2.2
201864514 | Ground Loop | HYDRON MODULE | HZT024*A |  | 26400 | 18.3 | 18300 | 3.9 | 2.2
201864515 | Ground Loop | TETCO | TZT024*A |  | 26400 | 18.3 | 18300 | 3.9 | 2.2
201864519 | Ground Loop | GEOCOMFORT | GZT024*3 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2
201864521 | Ground Loop | HYDRON MODULE | HZT024*3 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2
201864523 | Ground Loop | TETCO | TZT024*3 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2
206342117 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*3 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167
206342118 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*4 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167
206342119 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV080T*5 |  | 83000 | 19.7 | 55000 | 3.7 | 6.9167
206342120 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*3 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167
206342121 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*4 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167
206342122 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV095T*5 |  | 95000 | 19.6 | 65000 | 3.8 | 7.9167
206342123 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*3 |  | 122000 | 18 | 83000 | 3.6 | 10.1667
206342124 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*5 |  | 122000 | 18 | 83000 | 3.6 | 10.1667
206342125 | Ground Loop | YORK BY JOHNSON CONTROLS | YLLV/YLXV120T*4 |  | 122000 | 18 | 83000 | 3.6 | 10.1667
202330514 | Ground Loop | AAON, Inc. | M2-003-1-H-BCBC-V0-10-000-A |  | 41900 | 18.4 | 28900 | 3.6 | 3.4917
206900573 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV084**5 |  | 90000 | 18.5 | 67000 | 3.8 | 7.5
206900574 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLH084**3 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333
206900575 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLH084**4 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333
206900576 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLH084**5 |  | 88000 | 17.5 | 67000 | 3.6 | 7.3333
206900577 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV096**3 |  | 98000 | 17 | 76000 | 3.8 | 8.1667
206900578 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV096**4 |  | 98000 | 17 | 76000 | 3.8 | 8.1667
206900579 | Ground Loop | YORK BY JOHNSON CONTROLS | YDLV096**5 |  | 98000 | 17 | 76000 | 3.8 | 8.1667
5220710 | Ground Loop | DAIKIN | WGTV/WGTH026B*K |  | 27600 | 19.27 | 18100 | 4.1 | 2.3
5220933 | Ground Loop | DAIKIN | WGTV/WGTH032B*E |  | 33800 | 18.9 | 23700 | 4.1 | 2.8167
5220934 | Ground Loop | DAIKIN | WGTV/WGTH032B*F |  | 33800 | 18.9 | 23700 | 4.1 | 2.8167
5220935 | Ground Loop | DAIKIN | WGTV/WGTH032B*J |  | 33800 | 18.9 | 23700 | 4.1 | 2.8167
5220936 | Ground Loop | DAIKIN | WGTV/WGTH032B*K |  | 33800 | 18.9 | 23700 | 4.1 | 2.8167
5220980 | Ground Loop | DAIKIN | WGTV/WGTH038B*E |  | 40200 | 20.1 | 28100 | 4.2 | 3.35
5220981 | Ground Loop | DAIKIN | WGTV/WGTH038B*F |  | 40200 | 20.1 | 28100 | 4.2 | 3.35
5220982 | Ground Loop | DAIKIN | WGTV/WGTH038B*K |  | 40200 | 20.1 | 28100 | 4.2 | 3.35
5220983 | Ground Loop | DAIKIN | WGTV/WGTH044B*E |  | 45900 | 19.8 | 31700 | 4 | 3.825
5220984 | Ground Loop | DAIKIN | WGTV/WGTH044B*F |  | 45900 | 19.8 | 31700 | 4 | 3.825
5220985 | Ground Loop | DAIKIN | WGTV/WGTH044B*K |  | 45900 | 19.8 | 31700 | 4 | 3.825
5220987 | Ground Loop | DAIKIN | WGTV/WGTH049B*E |  | 50600 | 19.2 | 35900 | 4 | 4.2167
5220988 | Ground Loop | DAIKIN | WGTV/WGTH049B*F |  | 50600 | 19.2 | 35900 | 4 | 4.2167
5220989 | Ground Loop | DAIKIN | WGTV/WGTH049B*K |  | 50600 | 19.2 | 35900 | 4 | 4.2167
5220990 | Ground Loop | DAIKIN | WGTV/WGTH064B*E |  | 67100 | 19.7 | 47000 | 3.9 | 5.5917
5220991 | Ground Loop | DAIKIN | WGTV/WGTH064B*F |  | 67100 | 19.7 | 47000 | 3.9 | 5.5917
5220992 | Ground Loop | DAIKIN | WGTV/WGTH064B*K |  | 67100 | 19.7 | 47000 | 3.9 | 5.5917
5295936 | Ground Loop | WaterFurnace | NBV/NBH015**0*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25
5295937 | Ground Loop | WaterFurnace | NBV/NBH015**2*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25
5295944 | Ground Loop | WaterFurnace | NBV/NBH015**2*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25
5295945 | Ground Loop | WaterFurnace | NBV/NBH015**2*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25
5295947 | Ground Loop | WaterFurnace | NBV/NBH015**0*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25
5295948 | Ground Loop | WaterFurnace | NBV/NBH015**0*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25
5295964 | Ground Loop | WaterFurnace | NBV/NBH018**2*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
207822807 | Ground Loop | HYDROTECH | HRCX30*-6 |  | 28000 | 18 | 20000 | 3.6 | 2.3333
207822813 | Ground Loop | HYDROTECH | HRCX36*-6 |  | 34100 | 17.1 | 25000 | 3.6 | 2.8417
208106952 | Ground Loop | 5 SERIES GEO-READY | NGV/NGH038*1*(1,2) |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
208106953 | Ground Loop | 5 SERIES GEO-READY | NGV/NGH049*1*(1,2) |  | 50800 | 19.3 | 38200 | 4 | 4.2333
208106954 | Ground Loop | 5 SERIES GEO-READY | NGV/NGH064*1*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
215400156 | Ground Loop | DAIKIN | WSMV060E1*G/J*T |  | 63500 | 17.8 | 46100 | 3.7 | 5.2917
215400157 | Ground Loop | DAIKIN | WSMV060F3*G/J*T |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917
215400160 | Ground Loop | DAIKIN | WSMV060E1*G/J*C |  | 63500 | 17.8 | 46100 | 3.7 | 5.2917
215400161 | Ground Loop | DAIKIN | WSMV060F3*G/J*C |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917
215400171 | Ground Loop | DAIKIN | WSSV012E1*H*T |  | 12200 | 20.4 | 8500 | 3.61 | 1.0167
215400173 | Ground Loop | DAIKIN | WSSV015E1*H*T |  | 17000 | 23.75 | 10500 | 3.87 | 1.4167
215400175 | Ground Loop | DAIKIN | WSSV015E1*H*C |  | 17000 | 23.75 | 10500 | 3.87 | 1.4167
215400177 | Ground Loop | DAIKIN | WSSV019E1*H*T |  | 20600 | 20.96 | 14100 | 3.73 | 1.7167
215400179 | Ground Loop | DAIKIN | WSSV019E1*H*C |  | 20600 | 20.96 | 14100 | 3.73 | 1.7167
215400182 | Ground Loop | DAIKIN | WSSV024J1*H*T |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167
215400183 | Ground Loop | DAIKIN | WSSV024K3*H*T |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167
215400186 | Ground Loop | DAIKIN | WSSV024J1*H*C |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167
215400187 | Ground Loop | DAIKIN | WSSV024K3*H*C |  | 25400 | 20.59 | 15700 | 3.7 | 2.1167
215400190 | Ground Loop | DAIKIN | WSSV030J1*H*T |  | 30200 | 20.49 | 20700 | 3.83 | 2.5167
215400191 | Ground Loop | DAIKIN | WSSV030K3*H*T |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167
215400194 | Ground Loop | DAIKIN | WSSV030J1*H*C |  | 30200 | 20.49 | 20700 | 3.83 | 2.5167
215400195 | Ground Loop | DAIKIN | WSSV030K3*H*C |  | 30200 | 21.36 | 20700 | 3.99 | 2.5167
215400198 | Ground Loop | DAIKIN | WSSV036J1*H*T |  | 40500 | 20.65 | 27600 | 3.84 | 3.375
215400199 | Ground Loop | DAIKIN | WSSV036K3*H*T |  | 40500 | 21.09 | 27600 | 3.83 | 3.375
215400202 | Ground Loop | DAIKIN | WSSV036J1*H*C |  | 40500 | 20.65 | 27600 | 3.84 | 3.375
215400203 | Ground Loop | DAIKIN | WSSV036K3*H*C |  | 40500 | 21.09 | 27600 | 3.83 | 3.375
215400206 | Ground Loop | DAIKIN | WSSV042E1*H*T |  | 44800 | 21.3 | 29000 | 3.92 | 3.7333
215400207 | Ground Loop | DAIKIN | WSSV042F3*H*T |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587
217752403 | Ground Loop | ClimateMaster | SL(A/*)*06A |  | 6300 | 20.5 | 4600 | 3.6 | 0.525
217752677 | Ground Loop | DAIKIN | WSSH024J1*H*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417
217752679 | Ground Loop | DAIKIN | WSSH024J1*H*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417
217752681 | Ground Loop | DAIKIN | WSSH030J1*H*T |  | 30600 | 21.15 | 21200 | 3.95 | 2.55
217752683 | Ground Loop | DAIKIN | WSSH030J1*H*C |  | 30600 | 21.15 | 21200 | 3.95 | 2.55
217752685 | Ground Loop | DAIKIN | WSSH036J1*H*T |  | 40300 | 20.75 | 27600 | 3.61 | 3.3583
207657665 | Ground Loop | ClimateMaster | TSL24 D |  | 26500 | 19.4 | 18500 | 3.6 | 2.2083
207657667 | Ground Loop | ClimateMaster | TSL30 D |  | 29500 | 18.4 | 21000 | 3.7 | 2.4583
214771937 | Ground Loop | TRANE | EXVK036A |  | 36600 | 20.8 | 27200 | 4.11 | 3.05
214771938 | Ground Loop | TRANE | EXVK042A |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083
214771939 | Ground Loop | TRANE | EXVK048A |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083
214771940 | Ground Loop | TRANE | EXVK060A |  | 62700 | 19.7 | 45200 | 3.82 | 5.225
201907610 | Ground Loop | WaterFurnace | URS036*0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
201907611 | Ground Loop | WaterFurnace | URS036*0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
201907612 | Ground Loop | WaterFurnace | URS036*0*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
201907613 | Ground Loop | WaterFurnace | URS036*3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
201907614 | Ground Loop | WaterFurnace | URS036*3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
201907615 | Ground Loop | WaterFurnace | URS036*3*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
201907616 | Ground Loop | WaterFurnace | URS036*4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
201907617 | Ground Loop | WaterFurnace | URS036*4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
201907618 | Ground Loop | WaterFurnace | URS036*4*5 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
201907619 | Ground Loop | WaterFurnace | URS048*0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
206726680 | Ground Loop | WaterFurnace | UVV/UVH024**0*1 |  | 25500 | 23.6 | 17800 | 3.9 | 2.125
214841657 | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333
214841658 | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15
214841660 | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417
214841662 | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333
216739922 | Ground Loop | DAIKIN | WSNH030E1*G/J*C |  | 32100 | 18.3 | 23800 | 3.6 | 2.675
216739930 | Ground Loop | DAIKIN | WSNH036E1*G/J*C |  | 35700 | 19.6 | 25500 | 3.6 | 2.975
214595621 | Ground Loop | AAON, Inc. | M2-004-2-H-GCBC-V0-10-000-A |  | 51900 | 18.4 | 33800 | 3.7 | 4.325
214595625 | Ground Loop | AAON, Inc. | M2-004-3-H-GCBC-V0-10-000-A |  | 51900 | 18.4 | 33800 | 3.7 | 4.325
214595629 | Ground Loop | AAON, Inc. | M2-004-4-H-GCBC-V0-10-000-A |  | 51900 | 18.4 | 33800 | 3.7 | 4.325
215851780 | Ground Loop | DAIKIN | WSTH048K3*G/J*C |  | 49300 | 19.19 | 36300 | 3.79 | 4.1083
215851781 | Ground Loop | DAIKIN | WSTH048L3*G/J*C |  | 49300 | 19 | 36300 | 3.76 | 4.1083
215851786 | Ground Loop | DAIKIN | WSTH060K3*G/J*C |  | 61600 | 18.62 | 44200 | 3.63 | 5.1333
215851798 | Ground Loop | DAIKIN | WSTV024J1*G/J*C |  | 22400 | 17.63 | 17200 | 3.9 | 1.8667
215851800 | Ground Loop | DAIKIN | WSTV024K3*G/J*C |  | 22400 | 17.45 | 17200 | 3.86 | 1.8667
215851805 | Ground Loop | DAIKIN | WSTV030J1*G/J*C |  | 32200 | 19.09 | 20800 | 3.7 | 2.6833
215851806 | Ground Loop | DAIKIN | WSTV030K3*G/J*C |  | 32200 | 18.9 | 20800 | 3.66 | 2.6833
215851812 | Ground Loop | DAIKIN | WSTV036J1*G/J*C |  | 39100 | 20.7 | 25600 | 3.61 | 3.2583
215851817 | Ground Loop | DAIKIN | WSTV042K3*G/J*C |  | 44800 | 18.96 | 27600 | 3.62 | 3.7333
215851821 | Ground Loop | DAIKIN | WSTV048K3*G/J*C |  | 52400 | 19.76 | 35200 | 3.82 | 4.3667
215851823 | Ground Loop | DAIKIN | WSTV048L3*G/J*C |  | 52400 | 19.56 | 35200 | 3.78 | 4.3667
215851828 | Ground Loop | DAIKIN | WSTV060K3*G/J*C |  | 63100 | 19.21 | 46800 | 4.02 | 5.2583
215851830 | Ground Loop | DAIKIN | WSTV060L3*G/J*C |  | 63100 | 19.01 | 46800 | 3.98 | 5.2583
215852848 | Ground Loop | DAIKIN | WSTH024E1*G/J*C |  | 25100 | 19.92 | 17200 | 3.92 | 2.0917
215852849 | Ground Loop | DAIKIN | WSTH024F3*G/J*C |  | 25100 | 19.52 | 17200 | 3.84 | 2.0917
215268318 | Ground Loop | WaterFurnace | V3A(V/H)024*S0**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
215268320 | Ground Loop | WaterFurnace | V3A(V/H)036*S0**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
215268321 | Ground Loop | WaterFurnace | V3A(V/H)042*S0**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
215268323 | Ground Loop | WaterFurnace | V3A(V/H)060*S0**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
217212078 | Ground Loop | FHP | CP048-4VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083
217212079 | Ground Loop | FHP | CP060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25
217212080 | Ground Loop | FHP | CP060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083
217212082 | Ground Loop | FHP | CP060-3VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25
217212083 | Ground Loop | FHP | CP060-3VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083
217212084 | Ground Loop | FHP | CP060-4VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25
217212085 | Ground Loop | FHP | CP060-4VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083
217212086 | Ground Loop | FHP | CP070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217212089 | Ground Loop | FHP | CP070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217212091 | Ground Loop | FHP | CP070-3HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217212094 | Ground Loop | FHP | CP070-3VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217212097 | Ground Loop | FHP | CP070-4HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217212099 | Ground Loop | FHP | CP070-4VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217212102 | Ground Loop | BOSCH | RP024-1HZC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
217212103 | Ground Loop | BOSCH | RP024-1HZN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
217212105 | Ground Loop | BOSCH | RP024-1VTC-*****A |  | 25500 | 18.5 | 18000 | 4 | 2.125
217212106 | Ground Loop | BOSCH | RP024-1VTN-*****A |  | 25000 | 18.5 | 17500 | 4 | 2.0833
217212107 | Ground Loop | BOSCH | RP036-1VT/HZC-*****A |  | 39000 | 18.5 | 28000 | 4 | 3.25
217212108 | Ground Loop | BOSCH | RP036-1VT/HZN-*****A |  | 38500 | 18.3 | 27500 | 4 | 3.2083
217212109 | Ground Loop | BOSCH | RP048-1VT/HZC-*****A |  | 51000 | 18 | 38000 | 4 | 4.25
217212111 | Ground Loop | BOSCH | RP048-1VT/HZN-*****A |  | 50500 | 17.5 | 37500 | 4 | 4.2083
217212112 | Ground Loop | BOSCH | RP060-1VT/HZC-*****A |  | 63000 | 18 | 48000 | 4 | 5.25
217212113 | Ground Loop | BOSCH | RP060-1VT/HZN-*****A |  | 62500 | 18 | 47500 | 4 | 5.2083
217212114 | Ground Loop | BOSCH | RP070-1HZC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217212116 | Ground Loop | BOSCH | RP070-1VTC-*****A |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217351071 | Ground Loop | BOSCH | CP024-1CSC-*****A | BIVA-24RCB-M20X | 26000 | 18.3 | 18400 | 4 | 2.1667
217351072 | Ground Loop | BOSCH | CP024-1CSN-*****A | BIVA-24RCB-M20X | 26000 | 18.8 | 18200 | 4.1 | 2.1667
204031803 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT049**1*J | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
204031812 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT049**1*J | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
5440703 | Ground Loop | GEOCOMFORT | GXT060D3 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25
5440704 | Ground Loop | HYDRON MODULE | HXT060D3 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25
5440705 | Ground Loop | TETCO | TXT060D3 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25
5440708 | Ground Loop | GEOCOMFORT | GXT072D3 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925
5440709 | Ground Loop | HYDRON MODULE | HXT072D3 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925
5440710 | Ground Loop | TETCO | TXT072D3 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925
5599272 | Ground Loop | BOSCH-GEO | SM036-1CF/HZ/VT |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
5599275 | Ground Loop | BOSCH-GEO | SM060-1CF/HZ/VT |  | 65100 | 17.6 | 45500 | 3.7 | 5.425
202443461 | Ground Loop | GeoSmart Energy | GSZ036*1*J | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55
202443462 | Ground Loop | GeoSmart Energy | GSZ042*1*J | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15
202443463 | Ground Loop | GeoSmart Energy | GTZ038*1*J | SAH038* | 36000 | 19 | 27900 | 4 | 3
202443470 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55
202443471 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS042**1*J | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15
202443472 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT038**1*J | SAH036* | 36000 | 19 | 27900 | 4 | 3
202443473 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST038**1*J | SAH036* | 36000 | 19 | 27900 | 4 | 3
207200579 | Ground Loop | GeoSmart Energy | GTS026*1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207200580 | Ground Loop | GeoSmart Energy | GTS049*1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207200581 | Ground Loop | GeoSmart Energy | GTS049*1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207200582 | Ground Loop | GeoSmart Energy | GTS064*1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207200583 | Ground Loop | GeoSmart Energy | GTS064*1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
8738037 | Ground Loop | GEOCOMFORT | GVT060*3 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075
8738038 | Ground Loop | HYDRON MODULE | HVT060*3 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075
8738039 | Ground Loop | TETCO | TVT060*3 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075
8738051 | Ground Loop | GEOCOMFORT | GVS042 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333
8738052 | Ground Loop | HYDRON MODULE | HVS042 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333
8738053 | Ground Loop | TETCO | TVS042 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333
8738054 | Ground Loop | GEOCOMFORT | GVS042*2 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333
8738055 | Ground Loop | HYDRON MODULE | HVS042*2 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333
8738056 | Ground Loop | TETCO | TVS042*2 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333
8738057 | Ground Loop | GEOCOMFORT | GVS042*3 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333
8738058 | Ground Loop | HYDRON MODULE | HVS042*3 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333
8738059 | Ground Loop | TETCO | TVS042*3 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333
8738060 | Ground Loop | GEOCOMFORT | GVS042*4 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333
8738061 | Ground Loop | HYDRON MODULE | HVS042*4 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333
8738062 | Ground Loop | TETCO | TVS042*4 |  | 43600 | 18.6 | 32000 | 3.8 | 3.6333
8738067 | Ground Loop | GEOCOMFORT | GVS048 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083
8738068 | Ground Loop | HYDRON MODULE | HVS048 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083
8738069 | Ground Loop | TETCO | TVS048 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083
8738070 | Ground Loop | GEOCOMFORT | GVS048*2 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083
8738071 | Ground Loop | HYDRON MODULE | HVS048*2 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083
8738072 | Ground Loop | TETCO | TVS048*2 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083
8738073 | Ground Loop | GEOCOMFORT | GVS048*3 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083
8738074 | Ground Loop | HYDRON MODULE | HVS048*3 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083
8738075 | Ground Loop | TETCO | TVS048*3 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083
8738076 | Ground Loop | GEOCOMFORT | GVS048*4 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083
8738077 | Ground Loop | HYDRON MODULE | HVS048*4 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083
8738078 | Ground Loop | TETCO | TVS048*4 |  | 50500 | 17.6 | 39600 | 3.6 | 4.2083
204272856 | Ground Loop | GeoSmart Energy | GT064**1*(1,4)*J |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
204272857 | Ground Loop | GeoSmart Energy | GTS064*1*J | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
204272858 | Ground Loop | GeoSmart Energy | GTS064*1*J | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
204272859 | Ground Loop | GeoSmart Energy | GTZ064*1*J | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
204272860 | Ground Loop | GeoSmart Energy | GTZ064*1*J | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
204272890 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT064**1*(1,4)*J |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
204272892 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT064**1*J | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
204272893 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT064**1*J | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
204276830 | Ground Loop | GEOSTAR | 104J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3
204276831 | Ground Loop | GEOSTAR | 103J038**1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3
204278291 | Ground Loop | WaterFurnace | SDV038J1*(1,2) |  | 36000 | 18.7 | 27400 | 3.9 | 3
204346746 | Ground Loop | GeoCool | GCHPV/H/D024T**A*** |  | 27000 | 17.95 | 18500 | 4.2 | 2.25
204346873 | Ground Loop | GeoCool | GCHPV/H/D036T**A*** |  | 39000 | 17.86 | 26900 | 4.4 | 3.25
205767582 | Ground Loop | ClimateMaster | TES/P038B | TAH038C | 37700 | 17.8 | 26200 | 3.8 | 3.1417
205767586 | Ground Loop | ClimateMaster | TES/P026B | TAH026C***A* | 24700 | 17.7 | 18800 | 3.6 | 2.0583
205767587 | Ground Loop | ClimateMaster | TES/P026B | TAH026C***B* | 25800 | 18.3 | 18700 | 3.8 | 2.15
205767588 | Ground Loop | ClimateMaster | TES/P026B | TAC026B***A* | 24000 | 17.4 | 18800 | 3.9 | 2
205767589 | Ground Loop | ClimateMaster | TES/P026B | TAC026B***B* | 26000 | 18 | 18600 | 3.8 | 2.1667
205767592 | Ground Loop | ClimateMaster | TRE060D |  | 62100 | 17.6 | 45600 | 3.6 | 5.175
205767606 | Ground Loop | ClimateMaster | VEV/H/D0930 |  | 24000 | 24.3 | 30000 | 3.6 | 2
205767612 | Ground Loop | ClimateMaster | TZV/H060D |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667
205767615 | Ground Loop | ClimateMaster | QEV/H/D0930 |  | 24000 | 24.3 | 30000 | 3.6 | 2
205767616 | Ground Loop | ClimateMaster | TYV/H060B |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667
214771941 | Ground Loop | TRANE | EXVK070A |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917
214771943 | Ground Loop | TRANE | GEHK009A |  | 8800 | 19.6 | 6400 | 3.96 | 0.73333
214771945 | Ground Loop | TRANE | GEHK015A |  | 15900 | 18.2 | 12500 | 3.85 | 1.325
214771946 | Ground Loop | TRANE | GEHK018A |  | 18500 | 17.3 | 15300 | 3.76 | 1.5417
214771947 | Ground Loop | TRANE | GEHK024A |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167
214771948 | Ground Loop | TRANE | GEHK030A |  | 30000 | 18.2 | 23700 | 3.66 | 2.5
214771951 | Ground Loop | TRANE | GEHK048A |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417
214771952 | Ground Loop | TRANE | GEHK060A |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083
214771953 | Ground Loop | TRANE | EXHK009A |  | 9000 | 21.2 | 6100 | 3.91 | 0.75
214771954 | Ground Loop | TRANE | EXHK012A |  | 11900 | 19.8 | 8500 | 3.78 | 0.99167
214771955 | Ground Loop | TRANE | EXHK015A |  | 16200 | 18.7 | 11800 | 3.73 | 1.35
214771956 | Ground Loop | TRANE | EXHK018A |  | 19700 | 20.8 | 14400 | 3.93 | 1.6417
214771957 | Ground Loop | TRANE | EXHK024A |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833
214771958 | Ground Loop | TRANE | EXHK030A |  | 31800 | 21.3 | 22900 | 4.17 | 2.65
214771959 | Ground Loop | TRANE | EXHK036A |  | 36600 | 20.8 | 27200 | 4.11 | 3.05
214771960 | Ground Loop | TRANE | EXHK042A |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083
214771961 | Ground Loop | TRANE | EXHK048A |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083
214771962 | Ground Loop | TRANE | EXHK060A |  | 62700 | 19.7 | 45200 | 3.82 | 5.225
214771963 | Ground Loop | TRANE | EXHK070A |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917
214772055 | Ground Loop | TRANE | GEVK0097 |  | 8800 | 19.6 | 6400 | 3.96 | 0.73333
214772057 | Ground Loop | TRANE | GEVK0157 |  | 15900 | 18.2 | 12500 | 3.85 | 1.325
214772058 | Ground Loop | TRANE | GEVK0187 |  | 18500 | 17.3 | 15300 | 3.76 | 1.5417
214772059 | Ground Loop | TRANE | GEVK024B |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167
214772060 | Ground Loop | TRANE | GEVK0244 |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167
214772061 | Ground Loop | TRANE | GEVK0247 |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167
214772062 | Ground Loop | TRANE | GEVK030B |  | 30000 | 18.2 | 23700 | 3.66 | 2.5
214772063 | Ground Loop | TRANE | GEVK0304 |  | 30000 | 18.2 | 23700 | 3.66 | 2.5
214772064 | Ground Loop | TRANE | GEVK0307 |  | 30000 | 18.2 | 23700 | 3.66 | 2.5
215415872 | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667
215415873 | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667
215415876 | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167
215415877 | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167
215415878 | Ground Loop | CENTURY | MZ(L/R/B/P/T/K)024A |  | 25000 | 18 | 18400 | 3.9 | 2.0833
215415879 | Ground Loop | COMFORT-AIRE | MZ(L/R/B/P/T/K)024A |  | 25000 | 18 | 18400 | 3.9 | 2.0833
215415886 | Ground Loop | CENTURY | MZ(L/R/B/P/T/K)048A |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833
215415887 | Ground Loop | COMFORT-AIRE | MZ(L/R/B/P/T/K)048A |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833
215415888 | Ground Loop | CENTURY | MZ(L/R/B/P/T/K)060A |  | 61500 | 17.8 | 44600 | 3.7 | 5.125
215415889 | Ground Loop | COMFORT-AIRE | MZ(L/R/B/P/T/K)060A |  | 61500 | 17.8 | 44600 | 3.7 | 5.125
215415909 | Ground Loop | CENTURY | ME(L/R/B/P/D/N/T/K)024A |  | 26300 | 19.9 | 17800 | 4.1 | 2.1917
215415910 | Ground Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)024A |  | 26300 | 19.9 | 17800 | 4.1 | 2.1917
215415911 | Ground Loop | CENTURY | ME(L/R/B/P/D/N/T/K)036A |  | 39200 | 18.6 | 28400 | 4.2 | 3.2667
215415912 | Ground Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)036A |  | 39200 | 18.6 | 28400 | 4.2 | 3.2667
215415913 | Ground Loop | CENTURY | ME(L/R/B/P/D/N/T/K)048A |  | 51700 | 19.4 | 38200 | 4 | 4.3083
215415914 | Ground Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)048A |  | 51700 | 19.4 | 38200 | 4 | 4.3083
215415915 | Ground Loop | CENTURY | ME(L/R/B/P/D/N/T/K)060A |  | 62600 | 18.7 | 44300 | 3.9 | 5.2167
215415916 | Ground Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)060A |  | 62600 | 18.7 | 44300 | 3.9 | 5.2167
215415917 | Ground Loop | CENTURY | ME(L/R/B/P/D/N/T/K)072A |  | 74700 | 18.4 | 54000 | 3.8 | 6.225
215415918 | Ground Loop | COMFORT-AIRE | ME(L/R/B/P/D/N/T/K)072A |  | 74700 | 18.4 | 54000 | 3.8 | 6.225
215415919 | Ground Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)024A |  | 26300 | 19.9 | 17800 | 4.1 | 2.1917
215415920 | Ground Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)024A |  | 26300 | 19.9 | 17800 | 4.1 | 2.1917
215415921 | Ground Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)036A |  | 39200 | 18.6 | 28400 | 4.2 | 3.2667
215415922 | Ground Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)036A |  | 39200 | 18.6 | 28400 | 4.2 | 3.2667
215415923 | Ground Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)048A |  | 51700 | 19.4 | 38200 | 4 | 4.3083
215415924 | Ground Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)048A |  | 51700 | 19.4 | 38200 | 4 | 4.3083
215415925 | Ground Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)060A |  | 62600 | 18.7 | 44300 | 3.9 | 5.2167
215415926 | Ground Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)060A |  | 62600 | 18.7 | 44300 | 3.9 | 5.2167
215415927 | Ground Loop | Johnson Controls | BE(L/R/B/P/D/N/T/K)072A |  | 74700 | 18.4 | 54000 | 3.8 | 6.225
215415928 | Ground Loop | SKYMARK | BE(L/R/B/P/D/N/T/K)072A |  | 74700 | 18.4 | 54000 | 3.8 | 6.225
217754567 | Ground Loop | DAIKIN | WSMH036F1*G/J*C |  | 38000 | 19.24 | 30000 | 3.89 | 3.1667
217754568 | Ground Loop | DAIKIN | WSMH036K1*G/J*C |  | 38000 | 19.16 | 30000 | 3.89 | 3.1667
217754572 | Ground Loop | DAIKIN | WSMH042E1*G/J*P |  | 39900 | 17.5 | 32500 | 3.7 | 3.325
217754573 | Ground Loop | DAIKIN | WSMH042F1*G/J*P |  | 39900 | 17.15 | 32500 | 3.63 | 3.325
217754574 | Ground Loop | DAIKIN | WSMH042K1*G/J*P |  | 39900 | 17.15 | 32500 | 3.63 | 3.325
217754578 | Ground Loop | DAIKIN | WSMH042E1*G/J*T |  | 40800 | 19.4 | 31600 | 3.8 | 3.4
217754579 | Ground Loop | DAIKIN | WSMH042F1*G/J*T |  | 40800 | 19.01 | 31600 | 3.72 | 3.4
217754580 | Ground Loop | DAIKIN | WSMH042K1*G/J*T |  | 40800 | 19.01 | 31600 | 3.72 | 3.4
217754584 | Ground Loop | DAIKIN | WSMH042E1*G/J*C |  | 40800 | 19.4 | 31600 | 3.8 | 3.4
217754585 | Ground Loop | DAIKIN | WSMH042F1*G/J*C |  | 40800 | 19.01 | 31600 | 3.72 | 3.4
217754586 | Ground Loop | DAIKIN | WSMH042K1*G/J*C |  | 40800 | 19.01 | 31600 | 3.72 | 3.4
216625840 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D0**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625841 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D2**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625842 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D3**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625843 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D3**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625844 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D3**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625845 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D4**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625846 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D4**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625847 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D4**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625848 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S0**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625849 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S0**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625850 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S0**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625851 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S2**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625852 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S3**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625853 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S3**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625854 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S3**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625855 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S4**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625856 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S4**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625857 | Ground Loop | GeoSmart Energy | S5A(V/H)048*S4**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625858 | Ground Loop | GeoSmart Energy | S5A(V/H)060*D0**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216625859 | Ground Loop | GeoSmart Energy | S5A(V/H)060*D0**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216625860 | Ground Loop | GeoSmart Energy | S5A(V/H)060*D3**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216625861 | Ground Loop | GeoSmart Energy | S5A(V/H)060*D3**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216625862 | Ground Loop | GeoSmart Energy | S5A(V/H)060*D4**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216625863 | Ground Loop | GeoSmart Energy | S5A(V/H)060*D4**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216625864 | Ground Loop | GeoSmart Energy | S5A(V/H)060*S0**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625865 | Ground Loop | GeoSmart Energy | S5A(V/H)060*S0**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625866 | Ground Loop | GeoSmart Energy | S5A(V/H)060*S3**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625867 | Ground Loop | GeoSmart Energy | S5A(V/H)060*S3**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625868 | Ground Loop | GeoSmart Energy | S5A(V/H)060*S4**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625869 | Ground Loop | GeoSmart Energy | S5A(V/H)060*S4**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625870 | Ground Loop | GeoSmart Energy | S5A(V/H)072*D0**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216625871 | Ground Loop | GeoSmart Energy | S5A(V/H)072*D0**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
202434484 | Ground Loop | BOSCH | SV024-1VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434485 | Ground Loop | BOSCH | SV024-3VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434486 | Ground Loop | BOSCH | SV024-4VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434487 | Ground Loop | BOSCH | SV024-2VTC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434492 | Ground Loop | BOSCH | SV024-1HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434493 | Ground Loop | BOSCH | SV024-3HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434494 | Ground Loop | BOSCH | SV024-4HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434495 | Ground Loop | BOSCH | SV024-2HZC-***T/A*D-**T/G |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434500 | Ground Loop | BOSCH | SV024-1VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434501 | Ground Loop | BOSCH | SV024-3VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434502 | Ground Loop | BOSCH | SV024-4VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434503 | Ground Loop | BOSCH | SV024-2VTN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434508 | Ground Loop | BOSCH | SV024-1HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434509 | Ground Loop | BOSCH | SV024-3HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434510 | Ground Loop | BOSCH | SV024-4HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434511 | Ground Loop | BOSCH | SV024-2HZN-***T/A*D-**T/G |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
8740368 | Ground Loop | GEOCOMFORT | GVS048*****1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3
8740369 | Ground Loop | HYDRON MODULE | HVS048*****1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3
8740370 | Ground Loop | TETCO | TVS048*****1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3
8740371 | Ground Loop | GEOCOMFORT | GVS048*2***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3
8740372 | Ground Loop | HYDRON MODULE | HVS048*2***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3
8740373 | Ground Loop | TETCO | TVS048*2***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3
8740374 | Ground Loop | GEOCOMFORT | GVS048*3***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3
8740375 | Ground Loop | HYDRON MODULE | HVS048*3***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3
8740376 | Ground Loop | TETCO | TVS048*3***1 |  | 51600 | 20.1 | 38700 | 3.9 | 4.3
8791878 | Ground Loop | GEOSTAR | 101/102H060**1*(1,4)***** |  | 62200 | 18.4 | 47900 | 4 | 5.1833
8791879 | Ground Loop | GeoSmart Energy | GS060**1*(1,4)********H |  | 62200 | 18.4 | 47900 | 4 | 5.1833
8791880 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS060**1*(1,4)****H |  | 62200 | 18.4 | 47900 | 4 | 5.1833
8791883 | Ground Loop | GEOSTAR | 101/102H060**1*0***** |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
8791884 | Ground Loop | GeoSmart Energy | GS060**1*0********H |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
8791885 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS060**1*0****H |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
10318050 | Ground Loop | GEOSTAR | 103H048**1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417
10318051 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS060**1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
10318052 | Ground Loop | GeoSmart Energy | GSZ060*1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
10318054 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS060**1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
10318055 | Ground Loop | GeoSmart Energy | GSZ060*1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
10318056 | Ground Loop | GEOSTAR | 103H060**1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
10318060 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS070**1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417
10318061 | Ground Loop | GEOSTAR | 103H070**1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417
10318062 | Ground Loop | GeoSmart Energy | GSZ070*1 | SRAA060* | 60500 | 17.1 | 50700 | 3.6 | 5.0417
10346237 | Ground Loop | GEOCOMFORT | GZT030******B |  | 32000 | 18 | 22600 | 3.7 | 2.6667
10346238 | Ground Loop | HYDRON MODULE | HZT030******B |  | 32000 | 18 | 22600 | 3.7 | 2.6667
10346239 | Ground Loop | TETCO | TZT030******B |  | 32000 | 18 | 22600 | 3.7 | 2.6667
10346240 | Ground Loop | GEOCOMFORT | GZT030*2****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667
10346241 | Ground Loop | HYDRON MODULE | HZT030*2****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667
10346242 | Ground Loop | TETCO | TZT030*2****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667
10346243 | Ground Loop | GEOCOMFORT | GZT030*3****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667
10346244 | Ground Loop | HYDRON MODULE | HZT030*3****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667
10346245 | Ground Loop | TETCO | TZT030*3****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667
10346246 | Ground Loop | GEOCOMFORT | GZT030*A****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667
10346247 | Ground Loop | HYDRON MODULE | HZT030*A****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667
10346248 | Ground Loop | TETCO | TZT030*A****B |  | 32000 | 18 | 22600 | 3.7 | 2.6667
10346253 | Ground Loop | GEOCOMFORT | GZT042******B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55
10346254 | Ground Loop | HYDRON MODULE | HZT042******B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55
10346255 | Ground Loop | TETCO | TZT042******B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55
10346256 | Ground Loop | GEOCOMFORT | GZT042*2****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55
10346257 | Ground Loop | HYDRON MODULE | HZT042*2****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55
10346258 | Ground Loop | TETCO | TZT042*2****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55
10346259 | Ground Loop | GEOCOMFORT | GZT042*3****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55
10346260 | Ground Loop | HYDRON MODULE | HZT042*3****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55
10346261 | Ground Loop | TETCO | TZT042*3****B |  | 42600 | 19.1 | 31500 | 3.7 | 3.55
205901397 | Ground Loop | DUAL AIR | CFX049 |  | 49000 | 17.1 | 31000 | 3.6 | 4.0833
205901398 | Ground Loop | MIAMI HEAT PUMP | HPX049 |  | 49000 | 17.1 | 31000 | 3.6 | 4.0833
205961529 | Ground Loop | Johnson Controls | JRE060D |  | 62100 | 17.6 | 45600 | 3.6 | 5.175
6501951 | Ground Loop | GEOSTAR | GBV/GBH042**0*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
6501952 | Ground Loop | GEOSTAR | GBV/GBH042**0*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
6501954 | Ground Loop | GEOSTAR | GBV/GBH042**3*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
6501955 | Ground Loop | GEOSTAR | GBV/GBH042**3*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
6501957 | Ground Loop | GEOSTAR | GBV/GBH042**4*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
6501958 | Ground Loop | GEOSTAR | GBV/GBH042**4*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
6501961 | Ground Loop | GEOSTAR | GBV/GBH048**0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
6501962 | Ground Loop | GEOSTAR | GBV/GBH048**0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
6501964 | Ground Loop | GEOSTAR | GBV/GBH048**3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
6501965 | Ground Loop | GEOSTAR | GBV/GBH048**3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
6501967 | Ground Loop | GEOSTAR | GBV/GBH048**4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
6501968 | Ground Loop | GEOSTAR | GBV/GBH048**4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
6501970 | Ground Loop | GEOSTAR | GBV/GBH049**0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
6501971 | Ground Loop | GEOSTAR | GBV/GBH049**0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
6501972 | Ground Loop | GEOSTAR | GBV/GBH049**3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
6501973 | Ground Loop | GEOSTAR | GBV/GBH049**3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
6501974 | Ground Loop | GEOSTAR | GBV/GBH049**4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
6501975 | Ground Loop | GEOSTAR | GBV/GBH049**4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
6501976 | Ground Loop | GEOSTAR | GBV/GBH060**0*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
6501977 | Ground Loop | GEOSTAR | GBV/GBH060**0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
6501978 | Ground Loop | GEOSTAR | GBV/GBH060**0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
6501979 | Ground Loop | GEOSTAR | GBV/GBH060**3*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
6501980 | Ground Loop | GEOSTAR | GBV/GBH060**3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
6501981 | Ground Loop | GEOSTAR | GBV/GBH060**3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
6501982 | Ground Loop | GEOSTAR | GBV/GBH060**4*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
6501983 | Ground Loop | GEOSTAR | GBV/GBH060**4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
6501984 | Ground Loop | GEOSTAR | GBV/GBH060**4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
6501985 | Ground Loop | GEOSTAR | GBV/GBH060**5*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
6501986 | Ground Loop | GEOSTAR | GBV/GBH064**0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
6501987 | Ground Loop | GEOSTAR | GBV/GBH064**0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
6501988 | Ground Loop | GEOSTAR | GBV/GBH064**3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
6501989 | Ground Loop | GEOSTAR | GBV/GBH064**3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
6501990 | Ground Loop | GEOSTAR | GBV/GBH064**4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
6501991 | Ground Loop | GEOSTAR | GBV/GBH064**4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
6501993 | Ground Loop | GEOSTAR | GBV/GBH070**0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
6501994 | Ground Loop | GEOSTAR | GBV/GBH070**0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
6501996 | Ground Loop | GEOSTAR | GBV/GBH070**3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
6501997 | Ground Loop | GEOSTAR | GBV/GBH070**3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
6501999 | Ground Loop | GEOSTAR | GBV/GBH070**4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
6502000 | Ground Loop | GEOSTAR | GBV/GBH070**4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
6502002 | Ground Loop | GEOSTAR | GBV/GBH072**0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
200083642 | Ground Loop | COMFORT-AIRE | HZV/H/D036B |  | 39000 | 20.3 | 29700 | 4.4 | 3.25
200083643 | Ground Loop | CENTURY | HZV/H/D036B |  | 39000 | 20.3 | 29700 | 4.4 | 3.25
200083644 | Ground Loop | COMFORT-AIRE | HZV/H/D024B |  | 26000 | 19.9 | 20200 | 4.1 | 2.1667
200083645 | Ground Loop | CENTURY | HZV/H/D024B |  | 26000 | 19.9 | 20200 | 4.1 | 2.1667
200083646 | Ground Loop | COMFORT-AIRE | HZV/H/D048B |  | 49600 | 19.3 | 36400 | 4 | 4.1333
216759817 | Ground Loop | WaterFurnace | W5SS036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833
216759818 | Ground Loop | WaterFurnace | W5SS048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925
216759819 | Ground Loop | WaterFurnace | W5SS060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917
216759821 | Ground Loop | GEOSTAR | G5SS024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833
216759822 | Ground Loop | GEOSTAR | G5SS036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833
216759823 | Ground Loop | GEOSTAR | G5SS048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925
216759824 | Ground Loop | GEOSTAR | G5SS060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917
216759826 | Ground Loop | WaterFurnace | W5SZ024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833
216759827 | Ground Loop | WaterFurnace | W5SZ036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833
216759828 | Ground Loop | WaterFurnace | W5SZ048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925
216759829 | Ground Loop | WaterFurnace | W5SZ060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917
216759831 | Ground Loop | GEOSTAR | G5SZ024BD1 | A5D(C/U)024B* | 23800 | 18.4 | 18800 | 3.9 | 1.9833
202434716 | Ground Loop | CARRIER | 50PCV036J/K*C3/CE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434717 | Ground Loop | CARRIER | 50PCV036J/K*C5/EE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434718 | Ground Loop | CARRIER | 50PCV036J/K*C6/FE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434719 | Ground Loop | CARRIER | 50PCV036J/K*C4/DE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434724 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C3/CE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434725 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C5/EE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434726 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C6/FE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434727 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C4/DE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
215837824 | Ground Loop | DAIKIN | WSSH024J1*G/J*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417
215837825 | Ground Loop | DAIKIN | WSSH024K3*G/J*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417
215837831 | Ground Loop | DAIKIN | WSSH030F3*G/J*T |  | 30600 | 22.05 | 21200 | 4.12 | 2.55
215837832 | Ground Loop | DAIKIN | WSSH030J1*G/J*T |  | 30600 | 21.15 | 21200 | 3.95 | 2.55
215837833 | Ground Loop | DAIKIN | WSSH030K3*G/J*T |  | 30600 | 22.05 | 21200 | 4.12 | 2.55
215837839 | Ground Loop | DAIKIN | WSSH030F3*G/J*C |  | 30600 | 22.05 | 21200 | 4.12 | 2.55
215837840 | Ground Loop | DAIKIN | WSSH030J1*G/J*C |  | 30600 | 21.15 | 21200 | 3.95 | 2.55
215837841 | Ground Loop | DAIKIN | WSSH030K3*G/J*C |  | 30600 | 22.05 | 21200 | 4.12 | 2.55
215837847 | Ground Loop | DAIKIN | WSSH036F3*G/J*T |  | 40300 | 21.27 | 27600 | 3.6 | 3.3583
215837848 | Ground Loop | DAIKIN | WSSH036J1*G/J*T |  | 40300 | 20.75 | 27600 | 3.61 | 3.3583
215837850 | Ground Loop | DAIKIN | WSSH036K3*G/J*T |  | 40300 | 21.19 | 27600 | 3.6 | 3.3583
215837855 | Ground Loop | DAIKIN | WSSH036F3*G/J*C |  | 40300 | 21.27 | 27600 | 3.6 | 3.3583
215837856 | Ground Loop | DAIKIN | WSSH036J1*G/J*C |  | 40300 | 20.75 | 27600 | 3.61 | 3.3583
215837857 | Ground Loop | DAIKIN | WSSH036K3*G/J*C |  | 40300 | 21.19 | 27600 | 3.6 | 3.3583
215837863 | Ground Loop | DAIKIN | WSSH042F3*G/J*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667
215837865 | Ground Loop | DAIKIN | WSSH042J1*G/J*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667
215837866 | Ground Loop | DAIKIN | WSSH042K3*G/J*T |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667
217967024 | Ground Loop | TRANE | VSHK050A |  | 52100 | 18.5 | 41300 | 4.2 | 4.3417
217967025 | Ground Loop | TRANE | VSVK050A |  | 50400 | 19.3 | 40400 | 4.3 | 4.2
217967026 | Ground Loop | TRANE | VSHK060A |  | 61900 | 17 | 51400 | 3.9 | 5.1583
217967027 | Ground Loop | TRANE | VSVK060A |  | 61200 | 17.9 | 49500 | 4.1 | 5.1
217967028 | Ground Loop | TRANE | VSHK024B |  | 25400 | 22.4 | 19200 | 4.4 | 2.1167
217967029 | Ground Loop | TRANE | VSVK024B |  | 26300 | 24.7 | 18800 | 4.6 | 2.1917
217967030 | Ground Loop | TRANE | VSHK033B |  | 33300 | 18.1 | 27700 | 4.1 | 2.775
217967031 | Ground Loop | TRANE | VSVK033B |  | 35300 | 20.3 | 25500 | 4.3 | 2.9417
217967032 | Ground Loop | TRANE | VSHK042B |  | 42200 | 21.3 | 32500 | 4.4 | 3.5167
217967033 | Ground Loop | TRANE | VSVK042B |  | 44900 | 22.7 | 34400 | 4.4 | 3.7417
217967034 | Ground Loop | TRANE | VSHK050B |  | 52100 | 18.5 | 41300 | 4.2 | 4.3417
217967035 | Ground Loop | TRANE | VSVK050B |  | 50400 | 19.3 | 40400 | 4.3 | 4.2
217967036 | Ground Loop | TRANE | VSHK060B |  | 61900 | 17 | 51400 | 3.9 | 5.1583
217967037 | Ground Loop | TRANE | VSVK060B |  | 61200 | 17.9 | 49500 | 4.1 | 5.1
217967038 | Ground Loop | TRANE | VSHK0244 |  | 25400 | 22.4 | 19200 | 4.4 | 2.1167
217967039 | Ground Loop | TRANE | VSVK0244 |  | 26300 | 24.7 | 18800 | 4.6 | 2.1917
217967040 | Ground Loop | TRANE | VSHK0334 |  | 33300 | 18.1 | 27700 | 4.1 | 2.775
217967041 | Ground Loop | TRANE | VSVK0334 |  | 35300 | 20.3 | 25500 | 4.3 | 2.9417
217967042 | Ground Loop | TRANE | VSHK0424 |  | 42200 | 21.3 | 32500 | 4.4 | 3.5167
217967043 | Ground Loop | TRANE | VSVK0424 |  | 44900 | 22.7 | 34400 | 4.4 | 3.7417
217967044 | Ground Loop | TRANE | VSHK0504 |  | 52100 | 18.5 | 41300 | 4.2 | 4.3417
217967045 | Ground Loop | TRANE | VSVK0504 |  | 50400 | 19.3 | 40400 | 4.3 | 4.2
217967046 | Ground Loop | TRANE | VSHK0604 |  | 61900 | 17 | 51400 | 3.9 | 5.1583
217967047 | Ground Loop | TRANE | VSVK0604 |  | 61200 | 17.9 | 49500 | 4.1 | 5.1
206346929 | Ground Loop | DAIKIN | WVFW*024*K***14 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917
206346930 | Ground Loop | DAIKIN | WVFW*030*K***14 |  | 30600 | 19.3 | 22300 | 4 | 2.55
206346937 | Ground Loop | DAIKIN | WCCW*019*E***14* |  | 20600 | 19 | 14000 | 3.7 | 1.7167
216625760 | Ground Loop | GeoSmart Energy | S5A(V/H)018*R2**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
216625761 | Ground Loop | GeoSmart Energy | S5A(V/H)018*R2**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
216625762 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D0**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216625763 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D0**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
203265288 | Ground Loop | BOSCH-GEO | SM048-1VT/CFC-*****A |  | 51300 | 18.15 | 36900 | 3.9 | 4.275
203265289 | Ground Loop | BOSCH-GEO | SM048-1VT/CFN-*****A |  | 51300 | 17.7 | 36900 | 3.6 | 4.275
203265290 | Ground Loop | BOSCH-GEO | SM048-1HZC-*****A |  | 51300 | 18.75 | 36900 | 4.1 | 4.275
203265291 | Ground Loop | BOSCH-GEO | SM048-1HZN-*****A |  | 51300 | 18 | 36900 | 4.1 | 4.275
203265529 | Ground Loop | BOSCH | SM048-1HZC-*****A |  | 51300 | 18.75 | 36900 | 4.1 | 4.275
203265533 | Ground Loop | BOSCH | SM048-1HZC-*****C |  | 51300 | 18.75 | 36900 | 4.1 | 4.275
203265538 | Ground Loop | BOSCH | SM048-1HZN-*****A |  | 51300 | 18 | 36900 | 4.1 | 4.275
203265540 | Ground Loop | BOSCH | SM048-1HZN-*****C |  | 51300 | 18 | 36900 | 4.1 | 4.275
203265973 | Ground Loop | CARRIER | GC048V/C**C***1**1 |  | 51300 | 18.15 | 36900 | 3.9 | 4.275
203265976 | Ground Loop | BRYANT | GC048V/C**C***1*X1 |  | 51300 | 18.15 | 36900 | 3.9 | 4.275
203265980 | Ground Loop | CARRIER | GC048V/C**N***1**1 |  | 51300 | 17.7 | 36900 | 3.6 | 4.275
203265983 | Ground Loop | BRYANT | GC048V/C**N***1*X1 |  | 51300 | 17.7 | 36900 | 3.6 | 4.275
203265987 | Ground Loop | CARRIER | GC048H**C***1**1 |  | 51300 | 18.75 | 36900 | 4.1 | 4.275
203265989 | Ground Loop | BRYANT | GC048H**C***1*X1 |  | 51300 | 18.75 | 36900 | 4.1 | 4.275
203265990 | Ground Loop | CARRIER | GC048H**N***1**1 |  | 51300 | 18 | 36900 | 4.1 | 4.275
203265991 | Ground Loop | BRYANT | GC048H**N***1*X1 |  | 51300 | 18 | 36900 | 4.1 | 4.275
203268807 | Ground Loop | BOSCH | SM060-1HZ*******C |  | 65100 | 17.6 | 45500 | 3.7 | 5.425
203303751 | Ground Loop | BOSCH-GEO | BP048-1HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203303774 | Ground Loop | BOSCH | BP048-1HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203303777 | Ground Loop | CARRIER | GB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203303778 | Ground Loop | BRYANT | GB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203303779 | Ground Loop | HEIL | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203303780 | Ground Loop | ARCOAIRE | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203303781 | Ground Loop | KEEPRITE | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203303782 | Ground Loop | TEMPSTAR | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203303783 | Ground Loop | COMFORTMAKER | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
208556821 | Ground Loop | HYDRON MODULE | HRT036 | EED036 | 37700 | 17.9 | 28400 | 4.1 | 3.1417
208556822 | Ground Loop | TETCO | TRT036 | EED036 | 37700 | 17.9 | 28400 | 4.1 | 3.1417
208556825 | Ground Loop | GEOCOMFORT | GRT048 | EED048 | 49800 | 17.4 | 38200 | 3.8 | 4.15
208556827 | Ground Loop | HYDRON MODULE | HRT048 | EED048 | 49800 | 17.4 | 38200 | 3.8 | 4.15
208556829 | Ground Loop | TETCO | TRT048 | EED060 | 49800 | 17.4 | 38200 | 3.8 | 4.15
208556831 | Ground Loop | GEOCOMFORT | GRT060 | EED060 | 61600 | 17.3 | 45800 | 3.6 | 5.1333
208556832 | Ground Loop | HYDRON MODULE | HRT060 | EED060 | 61600 | 17.3 | 45800 | 3.6 | 5.1333
208556834 | Ground Loop | TETCO | TRT060 | EED060 | 61600 | 17.3 | 45800 | 3.6 | 5.1333
208771547 | Ground Loop | HYDROTECH | WSV6012B* |  | 12500 | 19 | 9000 | 3.6 | 1.0417
208771548 | Ground Loop | HYDROTECH | WSV6024B* |  | 24000 | 18 | 17500 | 3.6 | 2
208771549 | Ground Loop | HYDROTECH | WSV6030B* |  | 33500 | 17.5 | 25000 | 3.6 | 2.7917
208856966 | Ground Loop | HYDROTECH | WSV6060B* |  | 63000 | 18 | 42500 | 3.6 | 5.25
208856967 | Ground Loop | HYDROTECH | WSV6072B* |  | 73500 | 18 | 52000 | 3.6 | 6.125
208856972 | Ground Loop | AE Air | WSV6012B* |  | 12500 | 19 | 9000 | 3.6 | 1.0417
208856973 | Ground Loop | AE Air | WSV6024B* |  | 24000 | 18 | 17500 | 3.6 | 2
208856974 | Ground Loop | AE Air | WSV6030B* |  | 33500 | 17.5 | 25000 | 3.6 | 2.7917
208856975 | Ground Loop | AE Air | WSV6060B* |  | 63000 | 18 | 42500 | 3.6 | 5.25
208856976 | Ground Loop | AE Air | WSV6072B* |  | 73500 | 18 | 52000 | 3.6 | 6.125
217351696 | Ground Loop | FHP | CP048-1CSC-*****A | BIVA-48RCB-M20X | 50600 | 18.1 | 38000 | 4.2 | 4.2167
217351697 | Ground Loop | FHP | CP048-1CSN-*****A | BIVA-48RCB-M20X | 50200 | 18.7 | 35400 | 4.1 | 4.1833
217351698 | Ground Loop | FHP | CP060-1CSC-*****A | BIVA-60RCB-M20X | 60800 | 17.7 | 50000 | 4 | 5.0667
217351699 | Ground Loop | FHP | CP060-1CSN-*****A | BIVA-60RCB-M20X | 60600 | 17.5 | 51200 | 4.2 | 5.05
217351700 | Ground Loop | FHP | CP024-1CSC-*****A | BMAC2430BBTA | 25400 | 18.1 | 18800 | 4.1 | 2.1167
217351701 | Ground Loop | FHP | CP024-1CSN-*****A | BMAC2430BBTA | 26000 | 18.3 | 18800 | 4.3 | 2.1667
217351703 | Ground Loop | FHP | CP036-1CSN-*****A | BMAC3036BBTA | 38200 | 17.2 | 30800 | 4.2 | 3.1833
217351704 | Ground Loop | FHP | CP048-1CSC-*****A | BMAC4248CBTA | 50200 | 17.5 | 37200 | 3.9 | 4.1833
217351705 | Ground Loop | FHP | CP048-1CSN-*****A | BMAC4248CBTA | 51600 | 17.8 | 38200 | 4.1 | 4.3
217351730 | Ground Loop | CARRIER | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 26000 | 18.5 | 18800 | 4.1 | 2.1667
7487654 | Ground Loop | TETCO | TYT036 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333
7487655 | Ground Loop | TETCO | TYT036*2 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333
7487656 | Ground Loop | GEOCOMFORT | GYT036*2 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333
7487657 | Ground Loop | HYDRON MODULE | HYT036*2 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333
7487658 | Ground Loop | HYDRON MODULE | HYT036*3 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333
7487659 | Ground Loop | GEOCOMFORT | GYT036*3 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333
7487660 | Ground Loop | TETCO | TYT036*3 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333
7487661 | Ground Loop | GEOCOMFORT | GYT048 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417
7487662 | Ground Loop | HYDRON MODULE | HYT048 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417
7487663 | Ground Loop | TETCO | TYT048 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417
7487664 | Ground Loop | TETCO | TYT048*2 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417
7487665 | Ground Loop | HYDRON MODULE | HYT048*2 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417
7487666 | Ground Loop | GEOCOMFORT | GYT048*2 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417
7487667 | Ground Loop | GEOCOMFORT | GYT048*3 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417
7487668 | Ground Loop | HYDRON MODULE | HYT048*3 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417
7487669 | Ground Loop | TETCO | TYT048*3 |  | 53300 | 20.2 | 39900 | 4.3 | 4.4417
7499543 | Ground Loop | FHP | LM024-1CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167
7499546 | Ground Loop | FHP | LM024-2CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167
7499547 | Ground Loop | FHP | LM024-3CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167
7499548 | Ground Loop | FHP | LM024-4CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167
7499550 | Ground Loop | FHP | LM036-1VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
7499552 | Ground Loop | FHP | LM036-2VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
7499553 | Ground Loop | FHP | LM036-3VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
7499554 | Ground Loop | FHP | LM036-4VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
7499556 | Ground Loop | FHP | LM048-1VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275
7499559 | Ground Loop | FHP | LM048-3VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275
7499560 | Ground Loop | FHP | LM048-4VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275
7499562 | Ground Loop | FHP | LM060-1VT/CF/HZ*-*****A |  | 65100 | 17.65 | 45500 | 3.7 | 5.425
7499565 | Ground Loop | FHP | LM060-3VT/CF/HZ*-*****A |  | 65100 | 17.65 | 45500 | 3.7 | 5.425
7499566 | Ground Loop | FHP | LM060-4VT/CF/HZ*-*****A |  | 65100 | 17.65 | 45500 | 3.7 | 5.425
7499702 | Ground Loop | BOSCH | SM036-1CF/HZ/VT |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
7519546 | Ground Loop | GEOCOMFORT | GVS018*A |  | 21400 | 20 | 16300 | 3.9 | 1.7833
7519547 | Ground Loop | HYDRON MODULE | HVS018*A |  | 21400 | 20 | 16300 | 3.9 | 1.7833
7519548 | Ground Loop | TETCO | TVS018*A |  | 21400 | 20 | 16300 | 3.9 | 1.7833
7519549 | Ground Loop | GEOCOMFORT | GVS024*A |  | 26000 | 19.7 | 19400 | 4 | 2.1667
7519550 | Ground Loop | HYDRON MODULE | HVS024*A |  | 26000 | 19.7 | 19400 | 4 | 2.1667
217754629 | Ground Loop | DAIKIN | WSMV024F1*G/J*P |  | 25500 | 19.07 | 18900 | 3.62 | 2.125
217754630 | Ground Loop | DAIKIN | WSMV024K1*G/J*P |  | 25500 | 19.07 | 18900 | 3.62 | 2.125
217754633 | Ground Loop | DAIKIN | WSMV024F1*G/J*T |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333
217754634 | Ground Loop | DAIKIN | WSMV024K1*G/J*T |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333
217754637 | Ground Loop | DAIKIN | WSMV024F1*G/J*C |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333
217754638 | Ground Loop | DAIKIN | WSMV024K1*G/J*C |  | 25600 | 20.39 | 18600 | 3.77 | 2.1333
217754657 | Ground Loop | DAIKIN | WSMV036F1*G/J*T |  | 37100 | 19.24 | 27700 | 3.72 | 3.0917
217754658 | Ground Loop | DAIKIN | WSMV036K1*G/J*T |  | 37100 | 19.16 | 27700 | 3.72 | 3.0917
217754661 | Ground Loop | DAIKIN | WSMV036F1*G/J*C |  | 37100 | 19.24 | 27700 | 3.72 | 3.0917
217754662 | Ground Loop | DAIKIN | WSMV036K1*G/J*C |  | 37100 | 19.16 | 27700 | 3.72 | 3.0917
217754670 | Ground Loop | DAIKIN | WSMV042K1*G/J*T |  | 42600 | 19.67 | 29700 | 3.63 | 3.55
217754674 | Ground Loop | DAIKIN | WSMV042K1*G/J*C |  | 42600 | 19.67 | 29700 | 3.63 | 3.55
205737516 | Ground Loop | ICE AIR LLC | 8VSHPGE15** |  | 15000 | 17.5 | 10500 | 3.7 | 1.25
205746250 | Ground Loop | ICE AIR LLC | 8VSHPGE09** |  | 11000 | 21.3 | 6500 | 3.64 | 0.91667
205746251 | Ground Loop | ICE AIR LLC | 8VSHPGE12** |  | 13800 | 20.1 | 9000 | 3.7 | 1.15
205746252 | Ground Loop | ICE AIR LLC | 8VSHPGE18** |  | 19500 | 18.7 | 13400 | 3.63 | 1.625
205746253 | Ground Loop | ICE AIR LLC | 8VSHPGE24** |  | 24800 | 18.4 | 17000 | 3.66 | 2.0667
217897411 | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333
217897412 | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333
217897413 | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15
217897414 | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15
217897417 | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417
217897418 | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417
215224810 | Ground Loop | HEIL | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224811 | Ground Loop | ARCOAIRE | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224812 | Ground Loop | KEEPRITE | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224813 | Ground Loop | TEMPSTAR | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224814 | Ground Loop | COMFORTMAKER | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224815 | Ground Loop | DAY & NIGHT | HBR18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224816 | Ground Loop | HEIL | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224817 | Ground Loop | ARCOAIRE | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224818 | Ground Loop | KEEPRITE | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224819 | Ground Loop | TEMPSTAR | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224820 | Ground Loop | COMFORTMAKER | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224821 | Ground Loop | DAY & NIGHT | HBR18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224822 | Ground Loop | HEIL | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224823 | Ground Loop | ARCOAIRE | HBR24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
7422072 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
7422083 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
7422093 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH064**4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
7422134 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
7422147 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
7422187 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
7422202 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
7422225 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
7422234 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH070**4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
7422268 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
7422280 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
7422290 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
7422299 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
7422309 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
7422322 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH072**4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
7423168 | Ground Loop | WaterFurnace | NBV/NBH026**4*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
7423169 | Ground Loop | GEOSTAR | GBV/GBH026**4*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
7423171 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH026**4*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
7487652 | Ground Loop | GEOCOMFORT | GYT036 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333
7487653 | Ground Loop | HYDRON MODULE | HYT036 |  | 41200 | 20.9 | 29100 | 4.5 | 3.4333
215224599 | Ground Loop | CARRIER | 50WD*007***3*(A-H)** |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224600 | Ground Loop | CARRIER | 50WD*007***3*(J-R)** |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224601 | Ground Loop | CARRIER | 50WD*007***4*(A-H)** |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224602 | Ground Loop | CARRIER | 50WD*007***4*(J-R)** |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224603 | Ground Loop | CARRIER | 50WD*009***3*(A-H)** |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
215224604 | Ground Loop | CARRIER | 50WD*009***3*(J-R)** |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
215224605 | Ground Loop | CARRIER | 50WD*009***4*(A-H)** |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
215224606 | Ground Loop | CARRIER | 50WD*009***4*(J-R)** |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
215224607 | Ground Loop | CARRIER | 50WD*012***3*(A-H)** |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224608 | Ground Loop | CARRIER | 50WD*012***3*(J-R)** |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224609 | Ground Loop | CARRIER | 50WD*012***4*(A-H)** |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224610 | Ground Loop | CARRIER | 50WD*012***4*(J-R)** |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224611 | Ground Loop | CARRIER | 50WD*015***3*(A-H)** |  | 15700 | 18 | 11000 | 3.6 | 1.3083
215224612 | Ground Loop | CARRIER | 50WD*015***3*(J-R)** |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917
215224613 | Ground Loop | CARRIER | 50WD*015***4*(A-H)** |  | 15700 | 18 | 11000 | 3.6 | 1.3083
215224614 | Ground Loop | CARRIER | 50WD*015***4*(J-R)** |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917
215224615 | Ground Loop | CARRIER | 50WD*018***3*(A-H)** |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224616 | Ground Loop | CARRIER | 50WD*018***3*(J-R)** |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224617 | Ground Loop | CARRIER | 50WD*018***4*(A-H)** |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224618 | Ground Loop | CARRIER | 50WD*018***4*(J-R)** |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224619 | Ground Loop | CARRIER | 50WD*024***3*(A-H)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224620 | Ground Loop | CARRIER | 50WD*024***3*(J-R)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833
216979853 | Ground Loop | COMFORTMAKER | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
216979854 | Ground Loop | DAY & NIGHT | HCR24H**C******1 |  | 25500 | 18.5 | 18000 | 4 | 2.125
216979855 | Ground Loop | HEIL | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979856 | Ground Loop | ARCOAIRE | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979857 | Ground Loop | KEEPRITE | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979858 | Ground Loop | TEMPSTAR | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979859 | Ground Loop | COMFORTMAKER | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979860 | Ground Loop | DAY & NIGHT | HCR24H**N******1 |  | 25000 | 18.5 | 17500 | 4 | 2.0833
216979861 | Ground Loop | HEIL | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25
216979862 | Ground Loop | ARCOAIRE | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25
216979863 | Ground Loop | KEEPRITE | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25
216979864 | Ground Loop | TEMPSTAR | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25
216979865 | Ground Loop | COMFORTMAKER | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25
216979866 | Ground Loop | DAY & NIGHT | HCR36V/H**C******1 |  | 39000 | 18.5 | 28000 | 4 | 3.25
216979867 | Ground Loop | HEIL | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216979868 | Ground Loop | ARCOAIRE | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216979869 | Ground Loop | KEEPRITE | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216979870 | Ground Loop | TEMPSTAR | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216979871 | Ground Loop | COMFORTMAKER | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216979872 | Ground Loop | DAY & NIGHT | HCR36V/H**N******1 |  | 38500 | 18.3 | 27500 | 4 | 3.2083
216979873 | Ground Loop | HEIL | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25
216979874 | Ground Loop | ARCOAIRE | HCR48V/H**C******1 |  | 51000 | 18 | 38000 | 4 | 4.25
216625516 | Ground Loop | GEOSTAR | G5A(V/H)048*S3**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625517 | Ground Loop | GEOSTAR | G5A(V/H)048*S4**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625518 | Ground Loop | GEOSTAR | G5A(V/H)048*D4**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625519 | Ground Loop | GEOSTAR | G5A(V/H)048*D2**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625520 | Ground Loop | GEOSTAR | G5A(V/H)048*D4**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625521 | Ground Loop | GEOSTAR | G5A(V/H)048*D4**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625522 | Ground Loop | GEOSTAR | G5A(V/H)060*S3**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625523 | Ground Loop | GEOSTAR | G5A(V/H)060*S4**1 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625524 | Ground Loop | GEOSTAR | G5A(V/H)060*S0**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625525 | Ground Loop | GEOSTAR | G5A(V/H)060*S3**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625526 | Ground Loop | GEOSTAR | G5A(V/H)060*S4**4 |  | 63000 | 19.2 | 47900 | 3.9 | 5.25
216625527 | Ground Loop | GEOSTAR | G5A(V/H)060*D4**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216625528 | Ground Loop | GEOSTAR | G5A(V/H)060*D4**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216625529 | Ground Loop | GEOSTAR | G5A(V/H)072*S3**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216625530 | Ground Loop | GEOSTAR | G5A(V/H)072*S4**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216625531 | Ground Loop | GEOSTAR | G5A(V/H)072*S0**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216625532 | Ground Loop | GEOSTAR | G5A(V/H)072*S3**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216625533 | Ground Loop | GEOSTAR | G5A(V/H)072*S4**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216625534 | Ground Loop | GEOSTAR | G5A(V/H)072*D4**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216625535 | Ground Loop | GEOSTAR | G5A(V/H)072*D4**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216625542 | Ground Loop | GEOSTAR | G5A(V/H)042*S4**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625543 | Ground Loop | GEOSTAR | G5A(V/H)042*S2**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625616 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)012*R0**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833
216625617 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)012*R2**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833
216625618 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R0**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
216625619 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R0**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
216625620 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R2**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
216625621 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)015*R2**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
216625622 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*D0**1 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583
216625623 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*D0**4 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583
216625624 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R0**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
216625625 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R0**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
216625626 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R2**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
216625627 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)018*R2**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
216625628 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D0**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216625629 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D0**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216625630 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D2**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216625631 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D2**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216625632 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D3**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216625633 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D3**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216625634 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D4**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216625635 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*D4**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216625636 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S0**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625637 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S0**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625638 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S2**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625639 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S2**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625640 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S3**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625641 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S3**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625642 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S4**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625643 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)024*S4**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625644 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D0**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625645 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D0**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
214067603 | Ground Loop | GeoSmart Energy | GBV/GBH070**4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
214067604 | Ground Loop | GeoSmart Energy | GBV/GBH070**4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
214067606 | Ground Loop | GeoSmart Energy | GBV/GBH072**3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
214067607 | Ground Loop | GeoSmart Energy | GBV/GBH072**3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
214067608 | Ground Loop | GeoSmart Energy | GBV/GBH072**4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
214067609 | Ground Loop | GeoSmart Energy | GBV/GBH072**4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
214067866 | Ground Loop | GeoSmart Energy | GBV/GBH048**3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
214067867 | Ground Loop | GeoSmart Energy | GBV/GBH048**3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
214067871 | Ground Loop | GeoSmart Energy | GBV/GBH048**0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
214067872 | Ground Loop | GeoSmart Energy | GBV/GBH048**0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
214390535 | Ground Loop | Dandelion Geo | DP1G060V3A1000S |  | 62000 | 17 | 53000 | 4.5 | 5.1667
214437585 | Ground Loop | Dandelion Geo | DP1G036V3A1000S |  | 39200 | 19.8 | 31000 | 4.6 | 3.2667
214437586 | Ground Loop | Dandelion Geo | DP1G048V3A1000S |  | 51500 | 18.8 | 41500 | 4.4 | 4.2917
215837873 | Ground Loop | DAIKIN | WSSH042F3*G/J*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667
215837874 | Ground Loop | DAIKIN | WSSH042J1*G/J*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667
215837876 | Ground Loop | DAIKIN | WSSH042K3*G/J*C |  | 44000 | 21.27 | 29000 | 3.82 | 3.6667
215837882 | Ground Loop | DAIKIN | WSSH048F3*G/J*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667
215837883 | Ground Loop | DAIKIN | WSSH048K3*G/J*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667
215837884 | Ground Loop | DAIKIN | WSSH048L3*G/J*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667
215837891 | Ground Loop | DAIKIN | WSSH048F3*G/J*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667
215837892 | Ground Loop | DAIKIN | WSSH048K3*G/J*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667
215837893 | Ground Loop | DAIKIN | WSSH048L3*G/J*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667
217897450 | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667
217897453 | Ground Loop | CENTURY | MR(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167
217897454 | Ground Loop | COMFORT-AIRE | MR(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167
217897455 | Ground Loop | CENTURY | MJN024A | MKN024A | 23700 | 17.8 | 18300 | 3.8 | 1.975
217897456 | Ground Loop | COMFORT-AIRE | MJN024A | MKN024A | 23700 | 17.8 | 18300 | 3.8 | 1.975
217897457 | Ground Loop | CENTURY | MJN036A | MKN036A | 36800 | 18.2 | 27300 | 3.9 | 3.0667
217897458 | Ground Loop | COMFORT-AIRE | MJN036A | MKN036A | 36800 | 18.2 | 27300 | 3.9 | 3.0667
217897463 | Ground Loop | CENTURY | MJN024A | MAN024A | 23900 | 19 | 17900 | 4 | 1.9917
217897464 | Ground Loop | COMFORT-AIRE | MJN024A | MAN024A | 23900 | 19 | 17900 | 4 | 1.9917
217897465 | Ground Loop | CENTURY | MJN036A | MAN036A | 38300 | 18.4 | 26900 | 4 | 3.1917
217897466 | Ground Loop | COMFORT-AIRE | MJN036A | MAN036A | 38300 | 18.4 | 26900 | 4 | 3.1917
217897467 | Ground Loop | CENTURY | MJN048A | MAN048A | 49000 | 18.1 | 35500 | 3.7 | 4.0833
217897468 | Ground Loop | COMFORT-AIRE | MJN048A | MAN048A | 49000 | 18.1 | 35500 | 3.7 | 4.0833
217897469 | Ground Loop | CENTURY | MJN060A | MAN060A | 60200 | 17.6 | 45000 | 3.7 | 5.0167
217897470 | Ground Loop | COMFORT-AIRE | MJN060A | MAN060A | 60200 | 17.6 | 45000 | 3.7 | 5.0167
10384616 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ070H1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417
10435614 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS070**1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417
10435615 | Ground Loop | GEOSTAR | 103H070**1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417
10435616 | Ground Loop | GeoSmart Energy | GSZ070*1 | SAH066* | 60500 | 17.1 | 50700 | 3.6 | 5.0417
10581121 | Ground Loop | GEOSTAR | 107H064**1*1 |  | 62500 | 18.2 | 46300 | 3.8 | 5.2083
202147010 | Ground Loop | TETCO | TZS036*2 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05
202147011 | Ground Loop | TETCO | TZS036*3 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05
202147012 | Ground Loop | TETCO | TZS036*4 |  | 36600 | 17.9 | 28300 | 3.7 | 3.05
202147013 | Ground Loop | TETCO | TZS036*A |  | 36600 | 17.9 | 28300 | 3.7 | 3.05
202147014 | Ground Loop | TETCO | TZS036*****1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1
202147015 | Ground Loop | TETCO | TZS036*2***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1
202147016 | Ground Loop | TETCO | TZS036*3***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1
202147017 | Ground Loop | TETCO | TZS036*A***1 |  | 37200 | 18.8 | 27500 | 3.9 | 3.1
202147018 | Ground Loop | GEOCOMFORT | GZS042 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425
202147019 | Ground Loop | GEOCOMFORT | GZS042*2 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425
202147020 | Ground Loop | GEOCOMFORT | GZS042*3 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425
202147021 | Ground Loop | GEOCOMFORT | GZS042*4 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425
202147022 | Ground Loop | GEOCOMFORT | GZS042*****1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917
202147023 | Ground Loop | GEOCOMFORT | GZS042*2***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917
202147024 | Ground Loop | HYDRON MODULE | HZS042 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425
202147025 | Ground Loop | HYDRON MODULE | HZS042*2 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425
202147026 | Ground Loop | HYDRON MODULE | HZS042*3 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425
202147027 | Ground Loop | HYDRON MODULE | HZS042*4 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425
202147028 | Ground Loop | HYDRON MODULE | HZS042*****1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917
202147029 | Ground Loop | HYDRON MODULE | HZS042*2***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917
202147030 | Ground Loop | TETCO | TZS042 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425
202147031 | Ground Loop | TETCO | TZS042*2 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425
202147032 | Ground Loop | TETCO | TZS042*3 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425
202147033 | Ground Loop | TETCO | TZS042*4 |  | 41100 | 17.9 | 31700 | 3.7 | 3.425
202147034 | Ground Loop | TETCO | TZS042*****1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917
202147035 | Ground Loop | TETCO | TZS042*2***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917
206438871 | Ground Loop | CARRIER | 50PSH/V009***3/CA* |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167
206438872 | Ground Loop | CARRIER | 50PSH/V009***4/DA* |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167
206438873 | Ground Loop | CARRIER | 50PSH/V012***3/CA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438874 | Ground Loop | CARRIER | 50PSH/V015***3/CA* |  | 16200 | 19.8 | 11000 | 3.63 | 1.35
206438875 | Ground Loop | CARRIER | 50PSH/V015***4/DA* |  | 16200 | 19.8 | 11000 | 3.63 | 1.35
206438876 | Ground Loop | CARRIER | 50PSH/V030***4/DA* |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
206438877 | Ground Loop | CARRIER | 50PSH/V030***6/FA* |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
206438878 | Ground Loop | CARRIER | 50PSH/V030***5/EA* |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
206438879 | Ground Loop | CARRIER | 50PSH/V030***3/CA* |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
206438880 | Ground Loop | CARRIER | 50PSH/V060***6/FA* |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
206438881 | Ground Loop | CARRIER | 50PSH/V060***5/EA* |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
206438882 | Ground Loop | CARRIER | 50PSH/V060***3/CA* |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
206438883 | Ground Loop | CARRIER | 50PSH/V070***3/CA* |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
206438884 | Ground Loop | CARRIER | 50PSH/V070***5/EA* |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
206438885 | Ground Loop | CARRIER | 50PSH/V070***6/FA* |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
206438903 | Ground Loop | CARRIER | 50PSV012**C3/CA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438904 | Ground Loop | CARRIER | 50PSH012**C3/CA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438907 | Ground Loop | CARRIER | 50PSV012**C0/BA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438908 | Ground Loop | CARRIER | 50PSV012**C4/DA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438909 | Ground Loop | CARRIER | 50PSH012**C0/BA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438910 | Ground Loop | CARRIER | 50PSH012**C4/DA* |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
216621339 | Ground Loop | GEOSTAR | G5A(V/H)036*D0**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216621340 | Ground Loop | GEOSTAR | G5A(V/H)036*D3**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216621341 | Ground Loop | GEOSTAR | G5A(V/H)036*D0**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216621342 | Ground Loop | GEOSTAR | G5A(V/H)036*D3**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216621343 | Ground Loop | GEOSTAR | G5A(V/H)042*D0**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216621344 | Ground Loop | GEOSTAR | G5A(V/H)042*D3**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216621345 | Ground Loop | GEOSTAR | G5A(V/H)042*D0**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216621346 | Ground Loop | GEOSTAR | G5A(V/H)042*D3**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216621347 | Ground Loop | GEOSTAR | G5A(V/H)042*D0**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216621348 | Ground Loop | GEOSTAR | G5A(V/H)042*D3**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216621349 | Ground Loop | GEOSTAR | G5A(V/H)048*D0**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216621350 | Ground Loop | GEOSTAR | G5A(V/H)048*D3**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216621351 | Ground Loop | GEOSTAR | G5A(V/H)048*D0**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216621352 | Ground Loop | GEOSTAR | G5A(V/H)048*D3**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216621353 | Ground Loop | GEOSTAR | G5A(V/H)048*D0**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216621354 | Ground Loop | GEOSTAR | G5A(V/H)048*D3**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216621355 | Ground Loop | GEOSTAR | G5A(V/H)060*D0**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216621356 | Ground Loop | GEOSTAR | G5A(V/H)060*D3**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216621357 | Ground Loop | GEOSTAR | G5A(V/H)060*D0**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216621358 | Ground Loop | GEOSTAR | G5A(V/H)060*D3**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
216621359 | Ground Loop | GEOSTAR | G5A(V/H)072*D0**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216621360 | Ground Loop | GEOSTAR | G5A(V/H)072*D3**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216621361 | Ground Loop | GEOSTAR | G5A(V/H)072*D0**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216621362 | Ground Loop | GEOSTAR | G5A(V/H)072*D3**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
216625456 | Ground Loop | GEOSTAR | G5A(V/H)012*R2**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833
216625457 | Ground Loop | GEOSTAR | G5A(V/H)015*R2**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
216625458 | Ground Loop | GEOSTAR | G5A(V/H)015*R0**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
216625459 | Ground Loop | GEOSTAR | G5A(V/H)015*R2**4 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
215268334 | Ground Loop | WaterFurnace | V3A(V/H)024*S0**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
215268335 | Ground Loop | WaterFurnace | V3A(V/H)024*S2**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
215268336 | Ground Loop | WaterFurnace | V3A(V/H)024*S2**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
215268337 | Ground Loop | WaterFurnace | V3A(V/H)024*S3**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
215268338 | Ground Loop | WaterFurnace | V3A(V/H)024*S3**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
215268339 | Ground Loop | WaterFurnace | V3A(V/H)024*S4**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
215268340 | Ground Loop | WaterFurnace | V3A(V/H)024*S4**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
215268348 | Ground Loop | WaterFurnace | V3A(V/H)036*S0**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
215268349 | Ground Loop | WaterFurnace | V3A(V/H)036*S2**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
215268350 | Ground Loop | WaterFurnace | V3A(V/H)036*S2**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
215268351 | Ground Loop | WaterFurnace | V3A(V/H)036*S3**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
215268352 | Ground Loop | WaterFurnace | V3A(V/H)036*S3**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
215268353 | Ground Loop | WaterFurnace | V3A(V/H)036*S4**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
215268354 | Ground Loop | WaterFurnace | V3A(V/H)036*S4**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
215268355 | Ground Loop | WaterFurnace | V3A(V/H)042*S0**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
215268356 | Ground Loop | WaterFurnace | V3A(V/H)042*S3**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
215268357 | Ground Loop | WaterFurnace | V3A(V/H)042*S3**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
215268358 | Ground Loop | WaterFurnace | V3A(V/H)042*S4**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
215268359 | Ground Loop | WaterFurnace | V3A(V/H)042*S4**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
215268365 | Ground Loop | WaterFurnace | V3A(V/H)060*S0**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
215268366 | Ground Loop | WaterFurnace | V3A(V/H)060*S3**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
215268367 | Ground Loop | WaterFurnace | V3A(V/H)060*S3**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
215268368 | Ground Loop | WaterFurnace | V3A(V/H)060*S4**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
215268369 | Ground Loop | WaterFurnace | V3A(V/H)060*S4**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
215268664 | Ground Loop | WaterFurnace | V5A(V/H)012*R0**6 |  | 13000 | 18 | 9500 | 3.6 | 1.0833
215268665 | Ground Loop | WaterFurnace | V5A(V/H)015*R0**1 |  | 15500 | 19.5 | 12000 | 4.1 | 1.2917
215268666 | Ground Loop | WaterFurnace | V5A(V/H)018*R0**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
215268667 | Ground Loop | WaterFurnace | V5A(V/H)024*S0**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
215268668 | Ground Loop | WaterFurnace | V5A(V/H)030*S0**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
217642898 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S2**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
217642899 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S2**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
217642900 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S3**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
217642901 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S3**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
217642902 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S4**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
217642903 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S4**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
217642911 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S0**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642912 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S2**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642913 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S2**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642914 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S3**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642915 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S3**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642916 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S4**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642917 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S4**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642918 | Ground Loop | GeoSmart Energy | S3A(V/H)042*S0**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
217642919 | Ground Loop | GeoSmart Energy | S3A(V/H)042*S3**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
217642920 | Ground Loop | GeoSmart Energy | S3A(V/H)042*S3**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
217642921 | Ground Loop | GeoSmart Energy | S3A(V/H)042*S4**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
217642922 | Ground Loop | GeoSmart Energy | S3A(V/H)042*S4**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
9038316 | Ground Loop | GEOCOMFORT | GZT048*3****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15
204835632 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ038J1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3
204835633 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS038J1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3
205129920 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ036J1 | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55
205129921 | Ground Loop | GEOSTAR | 103J036**1 | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55
205145424 | Ground Loop | GEOCOMFORT | GVT030*****1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833
205145425 | Ground Loop | GEOCOMFORT | GVT030*2***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833
205145426 | Ground Loop | GEOCOMFORT | GVT030*3***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833
205145427 | Ground Loop | HYDRON MODULE | HVT030*****1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833
205145428 | Ground Loop | HYDRON MODULE | HVT030*2***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833
205145429 | Ground Loop | HYDRON MODULE | HVT030*3***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833
205145430 | Ground Loop | TETCO | TVT030*****1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833
205145431 | Ground Loop | TETCO | TVT030*2***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833
205145432 | Ground Loop | TETCO | TVT030*3***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833
205145433 | Ground Loop | GEOCOMFORT | GVT042*****1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825
205145434 | Ground Loop | GEOCOMFORT | GVT042*2***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825
205145435 | Ground Loop | GEOCOMFORT | GVT042*3***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825
205145436 | Ground Loop | HYDRON MODULE | HVT042*****1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825
205145437 | Ground Loop | HYDRON MODULE | HVT042*2***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825
205145438 | Ground Loop | HYDRON MODULE | HVT042*3***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825
205145439 | Ground Loop | TETCO | TVT042*2***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825
205145527 | Ground Loop | GEOCOMFORT | GVT030*A***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833
205145528 | Ground Loop | HYDRON MODULE | HVT030*A***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833
205145529 | Ground Loop | TETCO | TVT030*A***1 |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833
205145530 | Ground Loop | TETCO | TVT042*****1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825
205145531 | Ground Loop | TETCO | TVT042*3***1 |  | 45900 | 18.5 | 32400 | 3.9 | 3.825
214063740 | Ground Loop | GeoSmart Energy | GBV/GBH015**0*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25
214063741 | Ground Loop | GeoSmart Energy | GBV/GBH015**0*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25
214063742 | Ground Loop | GeoSmart Energy | GBV/GBH015**0*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25
214063743 | Ground Loop | GeoSmart Energy | GBV/GBH015**2*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25
214063744 | Ground Loop | GeoSmart Energy | GBV/GBH015**2*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25
214063745 | Ground Loop | GeoSmart Energy | GBV/GBH015**2*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25
214063747 | Ground Loop | GeoSmart Energy | GBV/GBH018**0*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
214063748 | Ground Loop | GeoSmart Energy | GBV/GBH018**0*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
214063750 | Ground Loop | GeoSmart Energy | GBV/GBH018**2*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
214063751 | Ground Loop | GeoSmart Energy | GBV/GBH018**2*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
214063752 | Ground Loop | GeoSmart Energy | GBV/GBH024**0*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
214063753 | Ground Loop | GeoSmart Energy | GBV/GBH024**0*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
214063754 | Ground Loop | GeoSmart Energy | GBV/GBH024**0*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
214063755 | Ground Loop | GeoSmart Energy | GBV/GBH024**2*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
215402569 | Ground Loop | DAIKIN | WSSV036F3*H*T |  | 40500 | 21.18 | 27600 | 3.83 | 3.375
215402572 | Ground Loop | DAIKIN | WSSV036E1*H*C |  | 40500 | 21.9 | 27600 | 3.84 | 3.375
215402573 | Ground Loop | DAIKIN | WSSV036F3*H*C |  | 40500 | 21.18 | 27600 | 3.83 | 3.375
217752725 | Ground Loop | DAIKIN | WSTH024K1*H*C |  | 25100 | 19.32 | 17200 | 3.8 | 2.0917
217752727 | Ground Loop | DAIKIN | WSTH030K1*H*C |  | 32700 | 19.1 | 20600 | 3.64 | 2.725
217752729 | Ground Loop | DAIKIN | WSTH036K1*H*C |  | 38700 | 20.02 | 25900 | 3.64 | 3.225
217752734 | Ground Loop | DAIKIN | WSTH048K1*H*C |  | 49300 | 19.19 | 36300 | 3.79 | 4.1083
217752735 | Ground Loop | DAIKIN | WSTH048L1*H*C |  | 49300 | 19 | 36300 | 3.76 | 4.1083
217752738 | Ground Loop | DAIKIN | WSTH060K1*H*C |  | 61600 | 18.62 | 44200 | 3.63 | 5.1333
217752745 | Ground Loop | DAIKIN | WSTV024K1*H*C |  | 22400 | 17.45 | 17200 | 3.86 | 1.8667
217752747 | Ground Loop | DAIKIN | WSTV030K1*H*C |  | 32200 | 18.9 | 20800 | 3.66 | 2.6833
217752751 | Ground Loop | DAIKIN | WSTV042K1*H*C |  | 44800 | 18.96 | 27600 | 3.62 | 3.7333
217752754 | Ground Loop | DAIKIN | WSTV048K1*H*C |  | 52400 | 19.76 | 35200 | 3.82 | 4.3667
217752755 | Ground Loop | DAIKIN | WSTV048L1*H*C |  | 52400 | 19.56 | 35200 | 3.78 | 4.3667
217752758 | Ground Loop | DAIKIN | WSTV060K1*H*C |  | 63100 | 19.21 | 46800 | 4.02 | 5.2583
217752759 | Ground Loop | DAIKIN | WSTV060L1*H*C |  | 63100 | 19.01 | 46800 | 3.98 | 5.2583
217752762 | Ground Loop | DAIKIN | WSTV070K1*H*C |  | 74600 | 18.62 | 56000 | 3.92 | 6.2167
217752763 | Ground Loop | DAIKIN | WSTV070L1*H*C |  | 74600 | 18.43 | 56000 | 3.88 | 6.2167
217754378 | Ground Loop | DAIKIN | WSSH024F1*H*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417
217754379 | Ground Loop | DAIKIN | WSSH024K1*H*T |  | 25700 | 21.15 | 17100 | 4 | 2.1417
217754381 | Ground Loop | DAIKIN | WSSH024F1*H*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417
217754382 | Ground Loop | DAIKIN | WSSH024K1*H*C |  | 25700 | 21.15 | 17100 | 4 | 2.1417
217754384 | Ground Loop | DAIKIN | WSSH030F1*H*T |  | 30600 | 22.05 | 21200 | 4.12 | 2.55
217754385 | Ground Loop | DAIKIN | WSSH030K1*H*T |  | 30600 | 22.05 | 21200 | 4.12 | 2.55
217754387 | Ground Loop | DAIKIN | WSSH030F1*H*C |  | 30600 | 22.05 | 21200 | 4.12 | 2.55
217754388 | Ground Loop | DAIKIN | WSSH030K1*H*C |  | 30600 | 22.05 | 21200 | 4.12 | 2.55
217754390 | Ground Loop | DAIKIN | WSSH036F1*H*T |  | 40300 | 21.27 | 27600 | 3.6 | 3.3583
217754391 | Ground Loop | DAIKIN | WSSH036K1*H*T |  | 40300 | 21.19 | 27600 | 3.6 | 3.3583
217754393 | Ground Loop | DAIKIN | WSSH036F1*H*C |  | 40300 | 21.27 | 27600 | 3.6 | 3.3583
8964157 | Ground Loop | BRYANT | GC036C/H/V******1*X1 + UI |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
8964158 | Ground Loop | CARRIER | GC036C/H/V******1**1 + UI |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
8964161 | Ground Loop | BRYANT | GC060C/H/V******1*X1 + UI |  | 65100 | 17.6 | 45500 | 3.7 | 5.425
8964162 | Ground Loop | CARRIER | GC060C/H/V******1**1 + UI |  | 65100 | 17.6 | 45500 | 3.7 | 5.425
215866227 | Ground Loop | ClimateMaster | SMT15A*L |  | 15400 | 18.8 | 11000 | 3.7 | 1.2833
215866229 | Ground Loop | ClimateMaster | SMT18A*L |  | 18900 | 17.8 | 13500 | 3.6 | 1.575
215866231 | Ground Loop | ClimateMaster | SMT24A*L |  | 25900 | 20.5 | 18000 | 3.7 | 2.1583
215866233 | Ground Loop | ClimateMaster | SMT30A*L |  | 30000 | 19 | 22300 | 3.7 | 2.5
215866540 | Ground Loop | DAIKIN | WSTH048E1*G/J*C |  | 49300 | 19.59 | 36300 | 3.87 | 4.1083
215866541 | Ground Loop | DAIKIN | WSTH048F3*G/J*C |  | 49300 | 19.19 | 36300 | 3.79 | 4.1083
215866542 | Ground Loop | DAIKIN | WSTV024E1*G/J*C |  | 22400 | 17.99 | 17200 | 3.98 | 1.8667
215866543 | Ground Loop | DAIKIN | WSTV024F3*G/J*C |  | 22400 | 17.63 | 17200 | 3.9 | 1.8667
215866544 | Ground Loop | DAIKIN | WSTV048E1*G/J*C |  | 52400 | 20.17 | 35200 | 3.9 | 4.3667
215866545 | Ground Loop | DAIKIN | WSTV048F3*G/J*C |  | 52400 | 19.76 | 35200 | 3.82 | 4.3667
207349379 | Ground Loop | WaterFurnace | NBV/NBH026**0*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
207349380 | Ground Loop | WaterFurnace | NBV/NBH026**3*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
207349381 | Ground Loop | WaterFurnace | NBV/NBH026**2*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
207349382 | Ground Loop | WaterFurnace | NBV/NBH026**4*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
207349383 | Ground Loop | WaterFurnace | NBV/NBH026**0*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
207349384 | Ground Loop | WaterFurnace | NBV/NBH026**3*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
207349385 | Ground Loop | WaterFurnace | NBV/NBH026**4*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
207349386 | Ground Loop | WaterFurnace | NBV/NBH026**2*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
207349387 | Ground Loop | WaterFurnace | NBV/NBH038**0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207349388 | Ground Loop | WaterFurnace | NBV/NBH038**3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207349389 | Ground Loop | WaterFurnace | NBV/NBH038**2*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207349390 | Ground Loop | WaterFurnace | NBV/NBH038**4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207349391 | Ground Loop | WaterFurnace | NBV/NBH038**0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207349392 | Ground Loop | WaterFurnace | NBV/NBH038**3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207349393 | Ground Loop | WaterFurnace | NBV/NBH038**4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207349394 | Ground Loop | WaterFurnace | NBV/NBH038**2*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207349395 | Ground Loop | WaterFurnace | NBV/NBH049**0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207349396 | Ground Loop | WaterFurnace | NBV/NBH049**3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207349397 | Ground Loop | WaterFurnace | NBV/NBH049**4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207349398 | Ground Loop | WaterFurnace | NBV/NBH049**0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207349399 | Ground Loop | WaterFurnace | NBV/NBH049**3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207349400 | Ground Loop | WaterFurnace | NBV/NBH049**4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207349401 | Ground Loop | WaterFurnace | NBV/NBH064**0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207349402 | Ground Loop | WaterFurnace | NBV/NBH064**3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207349403 | Ground Loop | WaterFurnace | NBV/NBH064**4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
7167551 | Ground Loop | CARRIER | 50PTD/H/V060***6/FA |  | 65100 | 17.65 | 45500 | 3.7 | 5.425
7170602 | Ground Loop | GEOCOMFORT | GVS018 |  | 21400 | 20 | 16300 | 3.9 | 1.7833
7170603 | Ground Loop | HYDRON MODULE | HVS018 |  | 21400 | 20 | 16300 | 3.9 | 1.7833
7170604 | Ground Loop | TETCO | TVS018 |  | 21400 | 20 | 16300 | 3.9 | 1.7833
7170606 | Ground Loop | GEOCOMFORT | GVS024 |  | 26000 | 19.7 | 19400 | 4 | 2.1667
7170607 | Ground Loop | HYDRON MODULE | HVS024 |  | 26000 | 19.7 | 19400 | 4 | 2.1667
7170608 | Ground Loop | TETCO | TVS024 |  | 26000 | 19.7 | 19400 | 4 | 2.1667
7170609 | Ground Loop | GEOCOMFORT | GVS030 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083
7170610 | Ground Loop | HYDRON MODULE | HVS030 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083
7170611 | Ground Loop | TETCO | TVS030 |  | 30100 | 18.5 | 22300 | 3.9 | 2.5083
7170612 | Ground Loop | GEOCOMFORT | GVS036 |  | 37800 | 18 | 30200 | 3.9 | 3.15
7170613 | Ground Loop | HYDRON MODULE | HVS036 |  | 37800 | 18 | 30200 | 3.9 | 3.15
7170614 | Ground Loop | TETCO | TVS036 |  | 37800 | 18 | 30200 | 3.9 | 3.15
7795914 | Ground Loop | GEOCOMFORT | GVT024 |  | 25800 | 18.6 | 19400 | 4 | 2.15
7795915 | Ground Loop | HYDRON MODULE | HVT024 |  | 25800 | 18.6 | 19400 | 4 | 2.15
7795916 | Ground Loop | TETCO | TVT024 |  | 25800 | 18.6 | 19400 | 4 | 2.15
7795918 | Ground Loop | GEOCOMFORT | GVT024*2 |  | 25800 | 18.6 | 19400 | 4 | 2.15
7795919 | Ground Loop | HYDRON MODULE | HVT024*2 |  | 25800 | 18.6 | 19400 | 4 | 2.15
7795920 | Ground Loop | TETCO | TVT024*2 |  | 25800 | 18.6 | 19400 | 4 | 2.15
7795921 | Ground Loop | GEOCOMFORT | GVT024*3 |  | 25800 | 18.6 | 19400 | 4 | 2.15
7795922 | Ground Loop | HYDRON MODULE | HVT024*3 |  | 25800 | 18.6 | 19400 | 4 | 2.15
7795923 | Ground Loop | TETCO | TVT024*3 |  | 25800 | 18.6 | 19400 | 4 | 2.15
7795924 | Ground Loop | GEOCOMFORT | GVT024*A |  | 25800 | 18.6 | 19400 | 4 | 2.15
7795925 | Ground Loop | HYDRON MODULE | HVT024*A |  | 25800 | 18.6 | 19400 | 4 | 2.15
203303784 | Ground Loop | DAY & NIGHT | HB048H******1**1 |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203337768 | Ground Loop | BOSCH-GEO | CE025-1VT/HZ/CF*-*****B |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917
203337769 | Ground Loop | BOSCH | CE025-1VT/HZ/CF*-*****B |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917
203337770 | Ground Loop | CARRIER | GP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917
203337771 | Ground Loop | BRYANT | GP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917
203337772 | Ground Loop | HEIL | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917
203337773 | Ground Loop | ARCOAIRE | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917
203337774 | Ground Loop | KEEPRITE | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917
203337775 | Ground Loop | TEMPSTAR | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917
203337776 | Ground Loop | COMFORTMAKER | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917
203337777 | Ground Loop | DAY & NIGHT | HP024V/H/C******1**1 |  | 27500 | 17.7 | 18600 | 3.6 | 2.2917
203343532 | Ground Loop | BOSCH-GEO | SM024-1CS*******A | SM024-1AV/AH*-*****A | 26200 | 17 | 17700 | 3.75 | 2.1833
203343535 | Ground Loop | BOSCH | SM024-1CS*******A | SM024-1AV/AH*-*****A | 26200 | 17 | 17700 | 3.75 | 2.1833
4236565 | Ground Loop | DAIKIN | WVFW1030*E***01 |  | 30700 | 19.1 | 22300 | 3.9 | 2.5583
4236634 | Ground Loop | DAIKIN | WVFW1030*F***01 |  | 30700 | 19.1 | 22300 | 3.9 | 2.5583
4236635 | Ground Loop | DAIKIN | WVFW1030*J***01 |  | 30700 | 19.1 | 22300 | 3.9 | 2.5583
4504310 | Ground Loop | BOSCH-GEO | BP012-1HZ/VT |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
4509712 | Ground Loop | BOSCH-GEO | BP024-1HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
4510474 | Ground Loop | BOSCH-GEO | BP030-1HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
4547265 | Ground Loop | DUAL AIR | CFX024 |  | 25000 | 17.1 | 16000 | 3.6 | 2.0833
4547266 | Ground Loop | DUAL AIR | CFX031 |  | 31200 | 17.1 | 19500 | 3.6 | 2.6
4547267 | Ground Loop | DUAL AIR | CFX036 |  | 35500 | 17.1 | 25500 | 3.6 | 2.9583
4547268 | Ground Loop | DUAL AIR | CFX041 |  | 40500 | 17.1 | 26000 | 3.6 | 3.375
4547869 | Ground Loop | MIAMI HEAT PUMP | HPX024 |  | 25000 | 17.1 | 16000 | 3.6 | 2.0833
4547870 | Ground Loop | MIAMI HEAT PUMP | HPX031 |  | 31200 | 17.1 | 19500 | 3.6 | 2.6
4547871 | Ground Loop | MIAMI HEAT PUMP | HPX036 |  | 35500 | 17.1 | 25500 | 3.6 | 2.9583
4547872 | Ground Loop | MIAMI HEAT PUMP | HPX041 |  | 40500 | 17.1 | 26000 | 3.6 | 3.375
4651271 | Ground Loop | WaterFurnace | USH023**0*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
4651272 | Ground Loop | WaterFurnace | USH023**2*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
4651273 | Ground Loop | WaterFurnace | USH023**3*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
206422420 | Ground Loop | COMFORT-AIRE | HBH/V018*W/K |  | 19500 | 17.1 | 14100 | 3.7 | 1.625
216625460 | Ground Loop | GEOSTAR | G5A(V/H)018*R2**1 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
216625461 | Ground Loop | GEOSTAR | G5A(V/H)018*R0**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
216625462 | Ground Loop | GEOSTAR | G5A(V/H)018*R2**4 |  | 18500 | 18.3 | 14500 | 4 | 1.5417
216625463 | Ground Loop | GEOSTAR | G5A(V/H)024*S2**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625464 | Ground Loop | GEOSTAR | G5A(V/H)024*S3**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625465 | Ground Loop | GEOSTAR | G5A(V/H)024*S4**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625466 | Ground Loop | GEOSTAR | G5A(V/H)024*S0**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625467 | Ground Loop | GEOSTAR | G5A(V/H)024*S2**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625468 | Ground Loop | GEOSTAR | G5A(V/H)024*S3**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625469 | Ground Loop | GEOSTAR | G5A(V/H)024*S4**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625470 | Ground Loop | GEOSTAR | G5A(V/H)030*S2**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625471 | Ground Loop | GEOSTAR | G5A(V/H)030*S3**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625472 | Ground Loop | GEOSTAR | G5A(V/H)030*S4**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625473 | Ground Loop | GEOSTAR | G5A(V/H)030*S0**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625474 | Ground Loop | GEOSTAR | G5A(V/H)030*S2**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625475 | Ground Loop | GEOSTAR | G5A(V/H)030*S3**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625476 | Ground Loop | GEOSTAR | G5A(V/H)030*S4**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625477 | Ground Loop | GEOSTAR | G5A(V/H)030*D2**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625478 | Ground Loop | GEOSTAR | G5A(V/H)030*D4**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625479 | Ground Loop | GEOSTAR | G5A(V/H)030*D2**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625480 | Ground Loop | GEOSTAR | G5A(V/H)030*D4**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625481 | Ground Loop | GEOSTAR | G5A(V/H)036*S2**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625482 | Ground Loop | GEOSTAR | G5A(V/H)036*S3**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625483 | Ground Loop | GEOSTAR | G5A(V/H)036*S4**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625484 | Ground Loop | GEOSTAR | G5A(V/H)036*S0**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625485 | Ground Loop | GEOSTAR | G5A(V/H)036*S2**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625486 | Ground Loop | GEOSTAR | G5A(V/H)036*S3**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625487 | Ground Loop | GEOSTAR | G5A(V/H)036*S4**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625488 | Ground Loop | GEOSTAR | G5A(V/H)036*S0**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625489 | Ground Loop | GEOSTAR | G5A(V/H)036*S2**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625490 | Ground Loop | GEOSTAR | G5A(V/H)036*S3**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625491 | Ground Loop | GEOSTAR | G5A(V/H)036*S4**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625492 | Ground Loop | GEOSTAR | G5A(V/H)036*D2**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625493 | Ground Loop | GEOSTAR | G5A(V/H)036*D4**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625494 | Ground Loop | GEOSTAR | G5A(V/H)036*D2**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625495 | Ground Loop | GEOSTAR | G5A(V/H)036*D4**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625496 | Ground Loop | GEOSTAR | G5A(V/H)036*D2**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625497 | Ground Loop | GEOSTAR | G5A(V/H)036*D4**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625498 | Ground Loop | GEOSTAR | G5A(V/H)042*S3**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625499 | Ground Loop | GEOSTAR | G5A(V/H)042*S0**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625500 | Ground Loop | GEOSTAR | G5A(V/H)042*S3**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625501 | Ground Loop | GEOSTAR | G5A(V/H)042*S4**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625502 | Ground Loop | GEOSTAR | G5A(V/H)042*S0**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625503 | Ground Loop | GEOSTAR | G5A(V/H)042*S3**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625504 | Ground Loop | GEOSTAR | G5A(V/H)042*S4**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625505 | Ground Loop | GEOSTAR | G5A(V/H)042*D4**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625506 | Ground Loop | GEOSTAR | G5A(V/H)042*D2**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
203372397 | Ground Loop | HEIL | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
203372398 | Ground Loop | ARCOAIRE | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
203372399 | Ground Loop | KEEPRITE | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
203372400 | Ground Loop | TEMPSTAR | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
203372401 | Ground Loop | COMFORTMAKER | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
203372402 | Ground Loop | DAY & NIGHT | HB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
203372403 | Ground Loop | HEIL | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
203372404 | Ground Loop | ARCOAIRE | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
203372405 | Ground Loop | KEEPRITE | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
203372406 | Ground Loop | TEMPSTAR | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
203372407 | Ground Loop | COMFORTMAKER | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
203372408 | Ground Loop | DAY & NIGHT | HB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
203372993 | Ground Loop | BOSCH | SM060-1HZ*-*****A |  | 65100 | 17.6 | 45500 | 3.7 | 5.425
203380957 | Ground Loop | BOSCH | EP018-1VT*******B |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
203380958 | Ground Loop | BOSCH | EP018-2VT*******B |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
203380959 | Ground Loop | BOSCH | EP018-1HZ*******B |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
203380960 | Ground Loop | BOSCH | EP018-2HZ*******B |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
203380963 | Ground Loop | BOSCH | EP042-1VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
203380964 | Ground Loop | BOSCH | EP042-3VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
203380965 | Ground Loop | BOSCH | EP042-4VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
203380966 | Ground Loop | BOSCH | EP042-1HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203380967 | Ground Loop | BOSCH | EP042-3HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203380968 | Ground Loop | BOSCH | EP042-4HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203380969 | Ground Loop | BOSCH | EP048-1VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
203380970 | Ground Loop | BOSCH | EP048-3VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
203380971 | Ground Loop | BOSCH | EP048-4VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
203380972 | Ground Loop | BOSCH | EP048-1HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203380973 | Ground Loop | BOSCH | EP048-3HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203380974 | Ground Loop | BOSCH | EP048-4HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203383876 | Ground Loop | CARRIER | 50PSV018***3/CA |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
203383877 | Ground Loop | CARRIER | 50PSV018***4/DA |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
203383878 | Ground Loop | CARRIER | 50PSH018***3/CA |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
203383879 | Ground Loop | CARRIER | 50PSH018***4/DA |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
203383880 | Ground Loop | CARRIER | 50PSV042***3/CA |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
203383881 | Ground Loop | CARRIER | 50PSV042***5/EA |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
203383882 | Ground Loop | CARRIER | 50PSV042***6/FA |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
203383883 | Ground Loop | CARRIER | 50PSH042***3/CA |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203383884 | Ground Loop | CARRIER | 50PSH042***5/EA |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203383885 | Ground Loop | CARRIER | 50PSH042***6/FA |  | 40600 | 19.5 | 26800 | 4 | 3.3833
211594244 | Ground Loop | TRANE | EXHG0157 |  | 15800 | 19 | 12100 | 3.8 | 1.3167
211594245 | Ground Loop | TRANE | EXHG0187 |  | 19600 | 20.6 | 14600 | 4.1 | 1.6333
211594246 | Ground Loop | TRANE | EXHG024B |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333
211594247 | Ground Loop | TRANE | EXHG0244 |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333
211594248 | Ground Loop | TRANE | EXHG0247 |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333
211594249 | Ground Loop | TRANE | EXHG030B |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333
211594250 | Ground Loop | TRANE | EXHG0304 |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333
211594251 | Ground Loop | TRANE | EXHG0307 |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333
211594252 | Ground Loop | TRANE | EXHG036B |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917
5295998 | Ground Loop | WaterFurnace | NBV/NBH030**3*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
5295999 | Ground Loop | WaterFurnace | NBV/NBH030**4*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
5296000 | Ground Loop | WaterFurnace | NBV/NBH030**4*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
5296001 | Ground Loop | WaterFurnace | NBV/NBH030**3*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
5296002 | Ground Loop | WaterFurnace | NBV/NBH030**0*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
5296003 | Ground Loop | WaterFurnace | NBV/NBH030**2*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
5296004 | Ground Loop | WaterFurnace | NBV/NBH036**0*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
5296005 | Ground Loop | WaterFurnace | NBV/NBH036**3*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
5296006 | Ground Loop | WaterFurnace | NBV/NBH036**4*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
5296007 | Ground Loop | WaterFurnace | NBV/NBH036**2*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
5296008 | Ground Loop | WaterFurnace | NBV/NBH036**0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
5296009 | Ground Loop | WaterFurnace | NBV/NBH036**3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
5296010 | Ground Loop | WaterFurnace | NBV/NBH036**4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
5296011 | Ground Loop | WaterFurnace | NBV/NBH036**2*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
5296012 | Ground Loop | WaterFurnace | NBV/NBH036**2*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
5296013 | Ground Loop | WaterFurnace | NBV/NBH036**0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
5296014 | Ground Loop | WaterFurnace | NBV/NBH036**3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
5296015 | Ground Loop | WaterFurnace | NBV/NBH036**4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
5296225 | Ground Loop | WaterFurnace | NBV/NBH042**0*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
5296226 | Ground Loop | WaterFurnace | NBV/NBH042**3*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
5296227 | Ground Loop | WaterFurnace | NBV/NBH042**4*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
5296228 | Ground Loop | WaterFurnace | NBV/NBH042**4*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
5296229 | Ground Loop | WaterFurnace | NBV/NBH042**3*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
5296230 | Ground Loop | WaterFurnace | NBV/NBH042**0*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
5315758 | Ground Loop | WaterFurnace | NBV/NBH048**0*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
5315759 | Ground Loop | WaterFurnace | NBV/NBH048**3*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
5315760 | Ground Loop | WaterFurnace | NBV/NBH048**4*1 |  | 45900 | 18.8 | 36400 | 4 | 3.825
202434652 | Ground Loop | CARRIER | 50PCV024J/K*C3/CE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434653 | Ground Loop | CARRIER | 50PCV024J/K*C5/EE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434654 | Ground Loop | CARRIER | 50PCV024J/K*C6/FE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434655 | Ground Loop | CARRIER | 50PCV024J/K*C4/DE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434660 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C3/CE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434661 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C5/EE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434662 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C6/FE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434663 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C4/DE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
202434668 | Ground Loop | CARRIER | 50PCV024J/K*N3/CE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434669 | Ground Loop | CARRIER | 50PCV024J/K*N5/EE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434670 | Ground Loop | CARRIER | 50PCV024J/K*N6/FE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434671 | Ground Loop | CARRIER | 50PCV024J/K*N4/DE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434676 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N3/CE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434677 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N5/EE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434678 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N6/FE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
202434679 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N4/DE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
7022707 | Ground Loop | GeoSmart Energy | ZS060**3*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
7022708 | Ground Loop | GEOSTAR | ZS060**3*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
9910756 | Ground Loop | HYDRON MODULE | HZS060*2***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583
9910757 | Ground Loop | TETCO | TZS060*2***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583
9910758 | Ground Loop | GEOCOMFORT | GZS060*3***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583
9910759 | Ground Loop | HYDRON MODULE | HZS060*3***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583
9910760 | Ground Loop | TETCO | TZS060*3***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583
9910764 | Ground Loop | GEOCOMFORT | GZS060******B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417
9910765 | Ground Loop | HYDRON MODULE | HZS060******B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417
9910766 | Ground Loop | TETCO | TZS060******B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417
9910767 | Ground Loop | GEOCOMFORT | GZS060*2****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417
9910768 | Ground Loop | HYDRON MODULE | HZS060*2****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417
9910769 | Ground Loop | TETCO | TZS060*2****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417
9910770 | Ground Loop | GEOCOMFORT | GZS060*3****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417
9910771 | Ground Loop | HYDRON MODULE | HZS060*3****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417
9910772 | Ground Loop | TETCO | TZS060*3****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417
9910773 | Ground Loop | GEOCOMFORT | GZS060*4****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417
9910774 | Ground Loop | HYDRON MODULE | HZS060*4****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417
9910775 | Ground Loop | TETCO | TZS060*4****B |  | 60500 | 17.8 | 49200 | 3.8 | 5.0417
9910780 | Ground Loop | GEOCOMFORT | GZS072*****1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083
9910781 | Ground Loop | HYDRON MODULE | HZS072*****1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083
9910782 | Ground Loop | TETCO | TZS072*****1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083
9910783 | Ground Loop | GEOCOMFORT | GZS072*2***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083
9910784 | Ground Loop | HYDRON MODULE | HZS072*2***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083
9910785 | Ground Loop | TETCO | TZS072*2***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083
9910786 | Ground Loop | GEOCOMFORT | GZS072*3***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083
9910787 | Ground Loop | HYDRON MODULE | HZS072*3***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083
9910788 | Ground Loop | TETCO | TZS072*3***1B |  | 72100 | 17.7 | 56600 | 3.7 | 6.0083
205767513 | Ground Loop | ClimateMaster | TSH/V/D024C |  | 25300 | 18.9 | 19200 | 4 | 2.1083
205767514 | Ground Loop | ClimateMaster | TSH/V/D024C*K |  | 25500 | 20.9 | 19100 | 4.2 | 2.125
205767515 | Ground Loop | ClimateMaster | TSH/V/D030C |  | 29200 | 18.5 | 22200 | 3.9 | 2.4333
205767516 | Ground Loop | ClimateMaster | TSH/V/D030C*K |  | 29200 | 19.4 | 22000 | 4.1 | 2.4333
205767517 | Ground Loop | ClimateMaster | TSH/V/D036C |  | 34300 | 19.2 | 25900 | 4.1 | 2.8583
205767518 | Ground Loop | ClimateMaster | TSH/V/D036C*K |  | 34600 | 20.4 | 25600 | 4.3 | 2.8833
205767519 | Ground Loop | ClimateMaster | TSH/V/D042C |  | 40100 | 19.4 | 28700 | 3.8 | 3.3417
205767520 | Ground Loop | ClimateMaster | TSH/V/D042C*K |  | 40700 | 21.9 | 27400 | 4.1 | 3.3917
205767521 | Ground Loop | ClimateMaster | TSH/V/D048C*K |  | 50600 | 18.8 | 36100 | 3.7 | 4.2167
205767522 | Ground Loop | ClimateMaster | TSH/V/D060C |  | 63900 | 17.2 | 46900 | 3.7 | 5.325
205767523 | Ground Loop | ClimateMaster | TSH/V/D060C*K |  | 64400 | 18.4 | 46400 | 3.9 | 5.3667
205767525 | Ground Loop | ClimateMaster | TSH/V/D070C*K |  | 73000 | 17.2 | 53000 | 3.6 | 6.0833
205767532 | Ground Loop | ClimateMaster | TSM15 B |  | 15500 | 18.8 | 11000 | 3.6 | 1.2917
205767538 | Ground Loop | ClimateMaster | TSM30 B |  | 29000 | 17.6 | 22200 | 3.6 | 2.4167
205767541 | Ground Loop | ClimateMaster | TCH/V018A*W/K |  | 19500 | 17.1 | 14100 | 3.7 | 1.625
205767548 | Ground Loop | ClimateMaster | TRH/V018A*W/K |  | 19500 | 17.1 | 14100 | 3.7 | 1.625
215837711 | Ground Loop | DAIKIN | WSMH030F3*G/J*C |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583
215837712 | Ground Loop | DAIKIN | WSMH030J1*G/J*C |  | 29500 | 19.36 | 21900 | 3.76 | 2.4583
215837714 | Ground Loop | DAIKIN | WSMH030K3*G/J*C |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583
215837719 | Ground Loop | DAIKIN | WSMH036F3*G/J*P |  | 37800 | 18.18 | 30700 | 3.79 | 3.15
215837721 | Ground Loop | DAIKIN | WSMH036J1*G/J*P |  | 37800 | 17.73 | 30700 | 3.8 | 3.15
215837722 | Ground Loop | DAIKIN | WSMH036K3*G/J*P |  | 37800 | 18.1 | 30700 | 3.79 | 3.15
215837728 | Ground Loop | DAIKIN | WSMH036F3*G/J*T |  | 38000 | 19.24 | 30000 | 3.89 | 3.1667
215837730 | Ground Loop | DAIKIN | WSMH036J1*G/J*T |  | 38000 | 18.77 | 30000 | 3.9 | 3.1667
215837731 | Ground Loop | DAIKIN | WSMH036K3*G/J*T |  | 38000 | 19.16 | 30000 | 3.89 | 3.1667
215837737 | Ground Loop | DAIKIN | WSMH036F3*G/J*C |  | 38000 | 19.24 | 30000 | 3.89 | 3.1667
215837739 | Ground Loop | DAIKIN | WSMH036J1*G/J*C |  | 38000 | 18.77 | 30000 | 3.9 | 3.1667
215837740 | Ground Loop | DAIKIN | WSMH036K3*G/J*C |  | 38000 | 19.16 | 30000 | 3.89 | 3.1667
215837744 | Ground Loop | DAIKIN | WSMH042F3*G/J*P |  | 39900 | 17.15 | 32500 | 3.63 | 3.325
215837746 | Ground Loop | DAIKIN | WSMH042K3*G/J*P |  | 39900 | 17.15 | 32500 | 3.63 | 3.325
215837750 | Ground Loop | DAIKIN | WSMH042F3*G/J*T |  | 40800 | 19.01 | 31600 | 3.72 | 3.4
215837751 | Ground Loop | DAIKIN | WSMH042K3*G/J*T |  | 40800 | 19.01 | 31600 | 3.72 | 3.4
215837756 | Ground Loop | DAIKIN | WSMH042F3*G/J*C |  | 40800 | 19.01 | 31600 | 3.72 | 3.4
215837757 | Ground Loop | DAIKIN | WSMH042K3*G/J*C |  | 40800 | 19.01 | 31600 | 3.72 | 3.4
215837763 | Ground Loop | DAIKIN | WSMH048F3*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075
215837764 | Ground Loop | DAIKIN | WSMH048K3*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075
215837766 | Ground Loop | DAIKIN | WSMH048L3*G/J*P |  | 48900 | 18.13 | 37600 | 3.69 | 4.075
215837771 | Ground Loop | DAIKIN | WSMH048F3*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075
215837773 | Ground Loop | DAIKIN | WSMH048K3*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075
215837774 | Ground Loop | DAIKIN | WSMH048L3*G/J*T |  | 48900 | 18.68 | 37500 | 3.8 | 4.075
215837780 | Ground Loop | DAIKIN | WSMH048F3*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075
215837781 | Ground Loop | DAIKIN | WSMH048K3*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075
215837783 | Ground Loop | DAIKIN | WSMH048L3*G/J*C |  | 48900 | 18.68 | 37500 | 3.8 | 4.075
217903468 | Ground Loop | WaterFurnace | V5R036*D0**1* |  | 37000 | 20 | 28400 | 4 | 3.0833
217903469 | Ground Loop | WaterFurnace | V5R036*D0**4* |  | 37000 | 20 | 28400 | 4 | 3.0833
217903470 | Ground Loop | WaterFurnace | V5R036*D0**5* |  | 37000 | 20 | 28400 | 4 | 3.0833
217903471 | Ground Loop | WaterFurnace | V5R036*D3**1* |  | 37000 | 20 | 28400 | 4 | 3.0833
217903472 | Ground Loop | WaterFurnace | V5R036*D3**4* |  | 37000 | 20 | 28400 | 4 | 3.0833
217903473 | Ground Loop | WaterFurnace | V5R036*D3**5* |  | 37000 | 20 | 28400 | 4 | 3.0833
217903474 | Ground Loop | WaterFurnace | V5R048*D0**1* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417
217903475 | Ground Loop | WaterFurnace | V5R048*D0**4* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417
217903476 | Ground Loop | WaterFurnace | V5R048*D0**5* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417
217903477 | Ground Loop | WaterFurnace | V5R048*D3**1* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417
217903478 | Ground Loop | WaterFurnace | V5R048*D3**4* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417
217903479 | Ground Loop | WaterFurnace | V5R048*D3**5* |  | 48500 | 18.1 | 38500 | 3.8 | 4.0417
217903480 | Ground Loop | WaterFurnace | V5R060*D0**1* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833
217903481 | Ground Loop | WaterFurnace | V5R060*D0**4* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833
217903482 | Ground Loop | WaterFurnace | V5R060*D0**5* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833
217903483 | Ground Loop | WaterFurnace | V5R060*D3**1* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833
217903484 | Ground Loop | WaterFurnace | V5R060*D3**4* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833
217903485 | Ground Loop | WaterFurnace | V5R060*D3**5* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833
217903486 | Ground Loop | WaterFurnace | V5R072*D0**1* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875
217903487 | Ground Loop | WaterFurnace | V5R072*D0**4* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875
217903488 | Ground Loop | WaterFurnace | V5R072*D0**5* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875
217903489 | Ground Loop | WaterFurnace | V5R072*D3**1* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875
217903490 | Ground Loop | WaterFurnace | V5R072*D3**4* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875
217903491 | Ground Loop | WaterFurnace | V5R072*D3**5* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875
217903492 | Ground Loop | WaterFurnace | V5R096*T3**5* |  | 88100 | 18 | 69900 | 3.8 | 7.3417
217903493 | Ground Loop | WaterFurnace | V5R120*T3**5* |  | 119400 | 17.7 | 92000 | 3.8 | 9.95
217754504 | Ground Loop | DAIKIN | WSTV024F1*H*C |  | 22400 | 17.63 | 17200 | 3.9 | 1.8667
9038317 | Ground Loop | HYDRON MODULE | HZT048*3****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15
9038318 | Ground Loop | TETCO | TZT048*3****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15
9038319 | Ground Loop | GEOCOMFORT | GZT048*A****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15
9038320 | Ground Loop | HYDRON MODULE | HZT048*A****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15
9038321 | Ground Loop | TETCO | TZT048*A****B |  | 49800 | 18.3 | 37900 | 3.9 | 4.15
9063210 | Ground Loop | DAIKIN | W.CCW.2.072.*.*.*.*.*.*.L |  | 80100 | 17.1 | 58700 | 3.75 | 6.675
9100310 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**0*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
9100311 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**0*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
9100313 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**2*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
9100314 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**2*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
9100316 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**3*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
9100317 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**3*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
9100319 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**4*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
9100320 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSH023**4*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
9100326 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**0*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225
9100328 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH015**2*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225
9100330 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH018**0*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417
9100332 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH018**2*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417
9100334 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**0*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
9100335 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**0*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
9100337 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**2*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
9100338 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**2*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
9100340 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**3*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
9100341 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**3*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
9100343 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH024**4*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
9100345 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**0*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
9100346 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**0*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
9100348 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**2*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
9100349 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**2*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
9100351 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**3*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
9100352 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**3*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
9100354 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**4*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
9100355 | Ground Loop | YORK BY JOHNSON CONTROLS | YGSV/YGSH030**4*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
216625764 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D2**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216625765 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D2**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216625766 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D3**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216625767 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D3**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216625768 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D4**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216625769 | Ground Loop | GeoSmart Energy | S5A(V/H)024*D4**4 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
216625770 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S0**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625771 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S0**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625772 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S2**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625773 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S2**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625774 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S3**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625775 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S3**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625776 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S4**1 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625777 | Ground Loop | GeoSmart Energy | S5A(V/H)024*S4**4 |  | 26000 | 20.6 | 19000 | 4 | 2.1667
216625778 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D0**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625779 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D0**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625780 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D2**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625781 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D2**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625782 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D3**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625783 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D3**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625784 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D4**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625785 | Ground Loop | GeoSmart Energy | S5A(V/H)030*D4**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625786 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S0**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625787 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S0**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625788 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S2**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625789 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S2**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625790 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S3**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625791 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S3**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625792 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S4**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625793 | Ground Loop | GeoSmart Energy | S5A(V/H)030*S4**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625794 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D0**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625795 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D0**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625796 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D0**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625797 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D2**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625798 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D2**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625799 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D2**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625800 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D3**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625801 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D3**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625802 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D3**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625803 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D4**1 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625804 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D4**2 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625805 | Ground Loop | GeoSmart Energy | S5A(V/H)036*D4**4 |  | 38500 | 20.8 | 29600 | 4.5 | 3.2083
216625806 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S0**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625807 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S0**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625808 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S0**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625809 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S2**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625810 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S2**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625811 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S2**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625812 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S3**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625813 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S3**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625814 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S3**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625815 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S4**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
207335399 | Ground Loop | GeoSmart Energy | GT049**1*(1,2,4)*K |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207335400 | Ground Loop | GeoSmart Energy | GT064**1*(1,4)*K |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207335401 | Ground Loop | GeoSmart Energy | GT072**1*(1,4)*J |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207335403 | Ground Loop | GeoSmart Energy | GS018**1*(1,4)*J |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
207335406 | Ground Loop | GeoSmart Energy | GS022**1*(1,4)*J |  | 19200 | 18.7 | 15000 | 4 | 1.6
207335407 | Ground Loop | GeoSmart Energy | GS030**1*(0,3)*J |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
207335408 | Ground Loop | GeoSmart Energy | GS030**1*(1,4)*J |  | 28100 | 22 | 20500 | 3.9 | 2.3417
207335409 | Ground Loop | GeoSmart Energy | GS036**1*(0,3)*K |  | 33700 | 22 | 24400 | 4.2 | 2.8083
207335410 | Ground Loop | GeoSmart Energy | GS036**1*(1,2,4)*K |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
207335413 | Ground Loop | GeoSmart Energy | GS048**1*(1,2,4)*K |  | 45900 | 18.8 | 36400 | 4 | 3.825
207335414 | Ground Loop | GeoSmart Energy | GS060**1*(1,4)*K |  | 62200 | 18.4 | 47900 | 4 | 5.1833
207335415 | Ground Loop | GeoSmart Energy | GS060**1*0*K |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
207335416 | Ground Loop | GeoSmart Energy | GS070**1*(1,4)*J |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
207335514 | Ground Loop | GeoSmart Energy | GS042**1*(1,2,4)*K |  | 40700 | 21.7 | 28900 | 4 | 3.3917
207335571 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS018**1*(1,4)****J |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
207335572 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS022**1*(1,4)****J |  | 19200 | 18.7 | 15000 | 4 | 1.6
207335573 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****J |  | 28100 | 22 | 20500 | 3.9 | 2.3417
207335574 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS036**1*(1,2,4)*K |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
207335575 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*K |  | 40700 | 21.7 | 28900 | 4 | 3.3917
207335576 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS048**1*(1,2,4)*K |  | 45900 | 18.8 | 36400 | 4 | 3.825
207335577 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS060**1*(1,4)****K |  | 62200 | 18.4 | 47900 | 4 | 5.1833
207335578 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS070**1*(1,4)****J |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
207335579 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT026**1*(1,4)****J |  | 26400 | 19.6 | 19500 | 4 | 2.2
207335580 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,4)*K |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207335581 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,4)*K |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207335582 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT064**1*(1,4)*K |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207335583 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT072**1*(1,4)****J |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207335584 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT026**1*(1,4)****H |  | 26400 | 19.6 | 19500 | 4 | 2.2
207335585 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*J |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207335586 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*J |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207335587 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT064**1*(1,4)*J |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207335588 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT072**1*(1,4)****H |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207335589 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT026**1*(1,4)****J |  | 26400 | 19.6 | 19500 | 4 | 2.2
207335590 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT038**1*(1,4)*K |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207335591 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT049**1*(1,4)*K |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207335592 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT064**1*(1,4)*K |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207335593 | Ground Loop | YORK BY JOHNSON CONTROLS | YZFT072**1*(1,4)****J |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
202211051 | Ground Loop | WaterFurnace | URD049*3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
202211052 | Ground Loop | WaterFurnace | URD049*3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
202211053 | Ground Loop | WaterFurnace | URD049*3*5 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
202211054 | Ground Loop | WaterFurnace | URD064*0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
202211055 | Ground Loop | WaterFurnace | URD064*0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
202211056 | Ground Loop | WaterFurnace | URD064*0*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
202211057 | Ground Loop | WaterFurnace | URD064*3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
202211058 | Ground Loop | WaterFurnace | URD064*3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
202211059 | Ground Loop | WaterFurnace | URD064*3*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
202211060 | Ground Loop | WaterFurnace | URD072*0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
202211061 | Ground Loop | WaterFurnace | URD072*0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
202211062 | Ground Loop | WaterFurnace | URD072*0*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
202211063 | Ground Loop | WaterFurnace | URD072*3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
202211064 | Ground Loop | WaterFurnace | URD072*3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
202211065 | Ground Loop | WaterFurnace | URD072*3*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
202211066 | Ground Loop | WaterFurnace | URT096*3*5 |  | 91800 | 18.8 | 72800 | 4 | 7.65
202262237 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ036J1 | SAH036* | 30600 | 20.4 | 23100 | 4 | 2.55
202262238 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ042J1 | SAH042* | 37800 | 19.5 | 27400 | 3.9 | 3.15
202272873 | Ground Loop | BOSCH-GEO | BP018-1VT*******C |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
206726691 | Ground Loop | WaterFurnace | UVV/UVH024**3*1 |  | 25500 | 23.6 | 17800 | 3.9 | 2.125
206726692 | Ground Loop | WaterFurnace | UVV/UVH024**4*1 |  | 25500 | 23.6 | 17800 | 3.9 | 2.125
206726812 | Ground Loop | GEOCOMFORT | GBS018 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417
206726813 | Ground Loop | GEOCOMFORT | GBS018 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167
206726814 | Ground Loop | HYDRON MODULE | HBS018 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417
206726815 | Ground Loop | HYDRON MODULE | HBS018 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167
206726816 | Ground Loop | TETCO | TBS018 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417
206726817 | Ground Loop | TETCO | TBS018 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167
206726818 | Ground Loop | GEOCOMFORT | GBS018*2 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417
206726819 | Ground Loop | GEOCOMFORT | GBS018*2 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167
206726820 | Ground Loop | HYDRON MODULE | HBS018*2 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417
206726821 | Ground Loop | HYDRON MODULE | HBS018*2 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167
206726822 | Ground Loop | TETCO | TBS018*2 | EED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417
206726823 | Ground Loop | TETCO | TBS018*2 | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167
206726824 | Ground Loop | GEOCOMFORT | GBT036 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333
206726825 | Ground Loop | GEOCOMFORT | GBT036 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075
206726826 | Ground Loop | HYDRON MODULE | HBT036 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333
206726827 | Ground Loop | HYDRON MODULE | HBT036 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075
206726828 | Ground Loop | TETCO | TBT036 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333
206726829 | Ground Loop | TETCO | TBT036 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075
206726830 | Ground Loop | GEOCOMFORT | GBT036*2 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333
206726831 | Ground Loop | GEOCOMFORT | GBT036*2 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075
206726832 | Ground Loop | HYDRON MODULE | HBT036*2 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333
206726833 | Ground Loop | HYDRON MODULE | HBT036*2 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075
206726834 | Ground Loop | TETCO | TBT036*2 | EED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333
206726835 | Ground Loop | TETCO | TBT036*2 | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075
206726836 | Ground Loop | GEOCOMFORT | GBT048 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275
206726837 | Ground Loop | GEOCOMFORT | GBT048 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917
206726838 | Ground Loop | HYDRON MODULE | HBT048 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275
206726839 | Ground Loop | HYDRON MODULE | HBT048 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917
206726840 | Ground Loop | TETCO | TBT048 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275
206726841 | Ground Loop | TETCO | TBT048 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917
206726842 | Ground Loop | GEOCOMFORT | GBT048*2 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275
206726843 | Ground Loop | GEOCOMFORT | GBT048*2 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917
206726844 | Ground Loop | HYDRON MODULE | HBT048*2 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275
206726845 | Ground Loop | HYDRON MODULE | HBT048*2 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917
206726846 | Ground Loop | TETCO | TBT048*2 | EED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275
206726847 | Ground Loop | TETCO | TBT048*2 | EAD048 | 50300 | 18.4 | 40700 | 3.8 | 4.1917
206726848 | Ground Loop | GEOCOMFORT | GBT060 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833
4651274 | Ground Loop | WaterFurnace | USH023**4*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
4651339 | Ground Loop | WaterFurnace | USV/USH024**0*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
4651340 | Ground Loop | WaterFurnace | USV/USH024**2*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
4651341 | Ground Loop | WaterFurnace | USV/USH024**3*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
4651342 | Ground Loop | WaterFurnace | USV/USH024**4*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
4651403 | Ground Loop | WaterFurnace | USV/USH030**0*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
4651404 | Ground Loop | WaterFurnace | USV/USH030**2*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
4651405 | Ground Loop | WaterFurnace | USV/USH030**3*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
4651407 | Ground Loop | WaterFurnace | USV/USH030**4*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
4651417 | Ground Loop | WaterFurnace | USV/USH036**0*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
4651418 | Ground Loop | WaterFurnace | USV/USH036**2*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
4651419 | Ground Loop | WaterFurnace | USV/USH036**3*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
4651420 | Ground Loop | WaterFurnace | USV/USH036**4*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
4651530 | Ground Loop | WaterFurnace | USV/USH042**0*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
4651532 | Ground Loop | WaterFurnace | USV/USH042**3*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
4651533 | Ground Loop | WaterFurnace | USV/USH042**4*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
4651546 | Ground Loop | WaterFurnace | USV/USH048**0*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
4651547 | Ground Loop | WaterFurnace | USV/USH048**3*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
4651548 | Ground Loop | WaterFurnace | USV/USH048**4*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
4651574 | Ground Loop | WaterFurnace | USV/USH060**0*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
4651575 | Ground Loop | WaterFurnace | USV/USH060**3*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
4651576 | Ground Loop | WaterFurnace | USV/USH060**4*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
4651577 | Ground Loop | WaterFurnace | USV/USH070**0*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
4651578 | Ground Loop | WaterFurnace | USV/USH070**3*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
4651579 | Ground Loop | WaterFurnace | USV/USH070**4*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
4651610 | Ground Loop | GEOSTAR | ZS023**0*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
4651611 | Ground Loop | GeoSmart Energy | ZS023**0*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
4651614 | Ground Loop | GEOSTAR | ZS024**0*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
4651615 | Ground Loop | GeoSmart Energy | ZS024**0*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
4651618 | Ground Loop | GEOSTAR | ZS024**2*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
4651619 | Ground Loop | GeoSmart Energy | ZS024**2*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
4651622 | Ground Loop | GEOSTAR | ZS024**3*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
4651623 | Ground Loop | GeoSmart Energy | ZS024**3*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
4651626 | Ground Loop | GEOSTAR | ZS024**4*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
4651627 | Ground Loop | GeoSmart Energy | ZS024**4*4 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
4651630 | Ground Loop | GEOSTAR | ZS030**0*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
4651631 | Ground Loop | GeoSmart Energy | ZS030**0*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
4651634 | Ground Loop | GEOSTAR | ZS030**2*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
4651635 | Ground Loop | GeoSmart Energy | ZS030**2*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
4651639 | Ground Loop | GEOSTAR | ZS030**3*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
4651640 | Ground Loop | GeoSmart Energy | ZS030**3*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
4651644 | Ground Loop | GEOSTAR | ZS030**4*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
4651645 | Ground Loop | GeoSmart Energy | ZS030**4*4 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
4651657 | Ground Loop | GEOSTAR | ZS036**0*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
4651658 | Ground Loop | GeoSmart Energy | ZS036**0*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
4651665 | Ground Loop | GEOSTAR | ZS036**2*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
4651666 | Ground Loop | GeoSmart Energy | ZS036**2*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
4651726 | Ground Loop | GEOSTAR | ZS036**3*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
4651727 | Ground Loop | GeoSmart Energy | ZS036**3*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
4651732 | Ground Loop | GEOSTAR | ZS036**4*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
4651733 | Ground Loop | GeoSmart Energy | ZS036**4*4 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
217037827 | Ground Loop | GeoSmart Energy | S5SZ036BD1 | A5D(C/U)036B* | 37000 | 19.8 | 28400 | 4.2 | 3.0833
217037828 | Ground Loop | GeoSmart Energy | S5SZ048BD1 | A5D(C/U)048B* | 47100 | 18.2 | 37900 | 4.2 | 3.925
217037829 | Ground Loop | GeoSmart Energy | S5SZ060BD1 | A5D(C/U)060B* | 59900 | 18.2 | 46700 | 3.9 | 4.9917
213307834 | Ground Loop | GeoSmart Energy | QT038**1*(1,2)*****K |  | 36000 | 18.7 | 27400 | 3.9 | 3
213307835 | Ground Loop | GeoSmart Energy | QT049**1*(1,2)*****J |  | 47700 | 18.2 | 38000 | 3.8 | 3.975
213307837 | Ground Loop | GeoSmart Energy | QT072**1*1*****J |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083
213502489 | Ground Loop | DAIKIN | WSMH007A1*G/J*T |  | 7400 | 18.8 | 5500 | 3.6 | 0.61667
213502493 | Ground Loop | DAIKIN | WSMH007E1*G/J*T |  | 7600 | 19 | 5500 | 3.6 | 0.63333
217351882 | Ground Loop | HEIL | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325
217351883 | Ground Loop | HEIL | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167
217351884 | Ground Loop | HEIL | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333
217351892 | Ground Loop | KEEPRITE | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667
217351893 | Ground Loop | KEEPRITE | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167
217351896 | Ground Loop | KEEPRITE | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25
217351897 | Ground Loop | KEEPRITE | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667
217351898 | Ground Loop | KEEPRITE | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417
7795926 | Ground Loop | TETCO | TVT024*A |  | 25800 | 18.6 | 19400 | 4 | 2.15
7795943 | Ground Loop | GEOCOMFORT | GVT036 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167
7795944 | Ground Loop | HYDRON MODULE | HVT036 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167
209180335 | Ground Loop | AE Air | WSV6018B* |  | 18000 | 17.2 | 13500 | 3.6 | 1.5
209180336 | Ground Loop | AE Air | WSV6036B* |  | 37000 | 18 | 28000 | 3.6 | 3.0833
209180337 | Ground Loop | AE Air | WSV6042B* |  | 42000 | 18.5 | 30000 | 3.6 | 3.5
209180338 | Ground Loop | AE Air | WSV6048B* |  | 51000 | 17.7 | 37000 | 3.6 | 4.25
209323637 | Ground Loop | HYDROTECH | WSV6009B* |  | 10000 | 19 | 7500 | 3.7 | 0.83333
209323638 | Ground Loop | AE Air | WSV6009B* |  | 10000 | 19 | 7500 | 3.7 | 0.83333
209945912 | Ground Loop | WaterFurnace | NBV/NBH009**0*6 |  | 9800 | 17.1 | 7800 | 3.6 | 0.81667
209945913 | Ground Loop | WaterFurnace | NBV/NBH009**2*6 |  | 9800 | 17.1 | 7800 | 3.6 | 0.81667
209945914 | Ground Loop | WaterFurnace | NBV/NBH012**0*6 |  | 12200 | 17.1 | 9500 | 3.6 | 1.0167
209945915 | Ground Loop | WaterFurnace | NBV/NBH012**2*6 |  | 12200 | 17.1 | 9500 | 3.6 | 1.0167
210286836 | Ground Loop | Energy Catalyst | DHHP036TV | DHHP036TV | 37500 | 17 | 29300 | 4.3 | 3.125
210286837 | Ground Loop | Energy Catalyst | DHHP036TH | DHHP036TH | 37500 | 17 | 29300 | 4.3 | 3.125
215415816 | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)015A*VB |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667
215415817 | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)015A*VC |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667
215415820 | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)018A*VB |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167
215415821 | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)018A*VC |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167
215415822 | Ground Loop | Johnson Controls | BY(L/R/B/P/T/K)024A*B |  | 25000 | 18 | 18400 | 3.9 | 2.0833
215415823 | Ground Loop | SKYMARK | BY(L/R/B/P/T/K)024A*C |  | 25000 | 18 | 18400 | 3.9 | 2.0833
215415830 | Ground Loop | Johnson Controls | BY(L/R/B/P/T/K)048A*B |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833
215415831 | Ground Loop | SKYMARK | BY(L/R/B/P/T/K)048A*C |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833
215415832 | Ground Loop | Johnson Controls | BY(L/R/B/P/T/K)060A*B |  | 61500 | 17.8 | 44600 | 3.7 | 5.125
215415833 | Ground Loop | SKYMARK | BY(L/R/B/P/T/K)060A*C |  | 61500 | 17.8 | 44600 | 3.7 | 5.125
215415834 | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333
215746921 | Ground Loop | TRANE | GSK102A3 |  | 120545 | 19.6 | 87192 | 4.05 | 10.0454
215746922 | Ground Loop | TRANE | GSK120A3 |  | 133334 | 20.1 | 96739 | 4.13 | 11.1112
215746923 | Ground Loop | TRANE | GSK036A4 |  | 41280 | 22.1 | 29804 | 4.28 | 3.44
215746924 | Ground Loop | TRANE | GSK036AW |  | 41280 | 22.1 | 29804 | 4.28 | 3.44
215746925 | Ground Loop | TRANE | GSK048A4 |  | 55159 | 20.4 | 39719 | 4.14 | 4.5966
215746926 | Ground Loop | TRANE | GSK048AW |  | 55159 | 20.4 | 39719 | 4.14 | 4.5966
215746927 | Ground Loop | TRANE | GSK060A4 |  | 66724 | 20.1 | 47737 | 3.95 | 5.5603
215746928 | Ground Loop | TRANE | GSK060AW |  | 66724 | 20.1 | 47737 | 3.95 | 5.5603
215746929 | Ground Loop | TRANE | GSK072A4 |  | 86809 | 21.4 | 59774 | 4.1 | 7.2341
215746930 | Ground Loop | TRANE | GSK072AW |  | 86809 | 21.4 | 59774 | 4.1 | 7.2341
215746931 | Ground Loop | TRANE | GSK090A4 |  | 102892 | 20.6 | 67696 | 3.86 | 8.5743
215746932 | Ground Loop | TRANE | GSK090AW |  | 102892 | 20.6 | 67696 | 3.86 | 8.5743
215746933 | Ground Loop | TRANE | GSK102A4 |  | 120545 | 19.6 | 87192 | 4.05 | 10.0454
215746934 | Ground Loop | TRANE | GSK102AW |  | 120545 | 19.6 | 87192 | 4.05 | 10.0454
215746935 | Ground Loop | TRANE | GSK120A4 |  | 133334 | 20.1 | 96739 | 4.13 | 11.1112
215746936 | Ground Loop | TRANE | GSK120AW |  | 133334 | 20.1 | 96739 | 4.13 | 11.1112
215748220 | Ground Loop | ClimateMaster | SMS(S,M)15A*Q |  | 14800 | 17.5 | 11100 | 3.6 | 1.2333
215748221 | Ground Loop | ClimateMaster | SMT(S,M)15A*Q |  | 15400 | 18.8 | 11000 | 3.7 | 1.2833
215748224 | Ground Loop | ClimateMaster | SMT(S,M)18A*Q |  | 19000 | 17.8 | 13600 | 3.6 | 1.5833
215748226 | Ground Loop | ClimateMaster | SMS(S,M)24A*Q |  | 24800 | 18.6 | 18400 | 3.6 | 2.0667
215748227 | Ground Loop | ClimateMaster | SMT(S,M)24A*Q |  | 25900 | 20.4 | 18000 | 3.7 | 2.1583
215748230 | Ground Loop | ClimateMaster | SMT(S,M)30A*Q |  | 30000 | 19 | 22300 | 3.7 | 2.5
217754678 | Ground Loop | DAIKIN | WSMV048F1*G/J*P |  | 50200 | 18.61 | 37100 | 3.64 | 4.1833
217754679 | Ground Loop | DAIKIN | WSMV048K1*G/J*P |  | 50200 | 18.61 | 37100 | 3.64 | 4.1833
217754680 | Ground Loop | DAIKIN | WSMV048L1*G/J*P |  | 49700 | 18.61 | 36700 | 3.64 | 4.1417
217754683 | Ground Loop | DAIKIN | WSMV048F1*G/J*T |  | 49800 | 19.09 | 36400 | 3.75 | 4.15
217754684 | Ground Loop | DAIKIN | WSMV048K1*G/J*T |  | 49800 | 19.09 | 36400 | 3.75 | 4.15
217754687 | Ground Loop | DAIKIN | WSMV048F1*G/J*C |  | 49800 | 19.09 | 36400 | 3.75 | 4.15
217754688 | Ground Loop | DAIKIN | WSMV048K1*G/J*C |  | 49800 | 19.09 | 36400 | 3.75 | 4.15
217754697 | Ground Loop | DAIKIN | WSMV060F1*G/J*T |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917
217754698 | Ground Loop | DAIKIN | WSMV060K1*G/J*T |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917
217754701 | Ground Loop | DAIKIN | WSMV060F1*G/J*C |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917
217754702 | Ground Loop | DAIKIN | WSMV060K1*G/J*C |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917
8735477 | Ground Loop | GEOCOMFORT | GVT048 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275
8735495 | Ground Loop | HYDRON MODULE | HVT048 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275
8735512 | Ground Loop | TETCO | TVT048 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275
8735538 | Ground Loop | GEOCOMFORT | GVT048*2 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275
8735552 | Ground Loop | HYDRON MODULE | HVT048*2 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275
8735567 | Ground Loop | TETCO | TVT048*2 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275
8735607 | Ground Loop | GEOCOMFORT | GVT048*3 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275
8735711 | Ground Loop | HYDRON MODULE | HVT048*3 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275
8735721 | Ground Loop | TETCO | TVT048*3 |  | 51300 | 18.9 | 38300 | 3.9 | 4.275
8735754 | Ground Loop | GEOCOMFORT | GVT048*A |  | 51300 | 18.9 | 38300 | 3.9 | 4.275
8735767 | Ground Loop | HYDRON MODULE | HVT048*A |  | 51300 | 18.9 | 38300 | 3.9 | 4.275
8735778 | Ground Loop | TETCO | TVT048*A |  | 51300 | 18.9 | 38300 | 3.9 | 4.275
8735903 | Ground Loop | GEOCOMFORT | GVS042*****1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7
8735904 | Ground Loop | HYDRON MODULE | HVS042*****1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7
8735905 | Ground Loop | TETCO | TVS042*****1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7
8735906 | Ground Loop | GEOCOMFORT | GVS042*2***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7
8735907 | Ground Loop | HYDRON MODULE | HVS042*2***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7
8735908 | Ground Loop | TETCO | TVS042*2***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7
8735909 | Ground Loop | GEOCOMFORT | GVS042*3***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7
8735910 | Ground Loop | HYDRON MODULE | HVS042*3***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7
8735911 | Ground Loop | TETCO | TVS042*3***1 |  | 44400 | 21.2 | 31100 | 4.1 | 3.7
8737970 | Ground Loop | GEOCOMFORT | GVS060*****1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125
8737971 | Ground Loop | HYDRON MODULE | HVS060*****1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125
8737972 | Ground Loop | TETCO | TVS060*****1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125
8737973 | Ground Loop | GEOCOMFORT | GVS060*2***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125
8737974 | Ground Loop | HYDRON MODULE | HVS060*2***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125
8737975 | Ground Loop | TETCO | TVS060*2***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125
8737976 | Ground Loop | GEOCOMFORT | GVS060*3***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125
8737977 | Ground Loop | HYDRON MODULE | HVS060*3***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125
8737978 | Ground Loop | TETCO | TVS060*3***1 |  | 61500 | 18.2 | 46300 | 3.8 | 5.125
206185754 | Ground Loop | DAIKIN | WGCH015E1*G/J*P |  | 15100 | 18.1 | 11100 | 3.8 | 1.2583
206185755 | Ground Loop | DAIKIN | WGCH015E1*G/J*T |  | 15300 | 19.9 | 10700 | 3.9 | 1.275
206185756 | Ground Loop | DAIKIN | WGCH015E1*G/J*C |  | 15300 | 19.9 | 10700 | 3.9 | 1.275
206185757 | Ground Loop | DAIKIN | WGCH019E1*G/J*C |  | 18300 | 19 | 13200 | 3.9 | 1.525
202434439 | Ground Loop | FHP | LV036-2VTC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434444 | Ground Loop | FHP | LV036-1HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434445 | Ground Loop | FHP | LV036-3HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434446 | Ground Loop | FHP | LV036-4HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
202434447 | Ground Loop | FHP | LV036-2HZC-***T/A*D-**T/G |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
207177463 | Ground Loop | TRANE | EXVG0127 |  | 12300 | 19.5 | 9300 | 4 | 1.025
207177464 | Ground Loop | TRANE | EXVG015A |  | 15800 | 19 | 12100 | 3.8 | 1.3167
207177465 | Ground Loop | TRANE | EXVG0157 |  | 15800 | 19 | 12100 | 3.8 | 1.3167
207177466 | Ground Loop | TRANE | EXVG018A |  | 19600 | 20.6 | 14600 | 4.1 | 1.6333
207177467 | Ground Loop | TRANE | EXVG0187 |  | 19600 | 20.6 | 14600 | 4.1 | 1.6333
207177468 | Ground Loop | TRANE | EXVG024A |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333
207177469 | Ground Loop | TRANE | EXVG024B |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333
207177470 | Ground Loop | TRANE | EXVG0244 |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333
207177471 | Ground Loop | TRANE | EXVG0247 |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333
207177472 | Ground Loop | TRANE | EXVG030A |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333
207177473 | Ground Loop | TRANE | EXVG030B |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333
207177474 | Ground Loop | TRANE | EXVG0304 |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333
207177475 | Ground Loop | TRANE | EXVG0307 |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333
207177476 | Ground Loop | TRANE | EXVG036A |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917
207177477 | Ground Loop | TRANE | EXVG036B |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917
207177478 | Ground Loop | TRANE | EXVG0364 |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917
207177479 | Ground Loop | TRANE | EXVG0367 |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917
207177480 | Ground Loop | TRANE | EXVG042A |  | 40500 | 21.1 | 29400 | 4.3 | 3.375
207177481 | Ground Loop | TRANE | EXVG042B |  | 40500 | 21.1 | 29400 | 4.3 | 3.375
207177482 | Ground Loop | TRANE | EXVG0424 |  | 40500 | 21.1 | 29400 | 4.3 | 3.375
207177483 | Ground Loop | TRANE | EXVG048A |  | 47100 | 20.3 | 34600 | 4.3 | 3.925
207177484 | Ground Loop | TRANE | EXVG048B |  | 47100 | 20.3 | 34600 | 4.3 | 3.925
207177485 | Ground Loop | TRANE | EXVG0484 |  | 47100 | 20.3 | 34600 | 4.3 | 3.925
207177486 | Ground Loop | TRANE | EXVG060A |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083
207177487 | Ground Loop | TRANE | EXVG060B |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083
207177488 | Ground Loop | TRANE | EXVG0604 |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083
207177489 | Ground Loop | TRANE | EXVG070A |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083
207177490 | Ground Loop | TRANE | EXVG070B |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083
207177491 | Ground Loop | TRANE | EXVG0704 |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083
207177492 | Ground Loop | TRANE | DXVG024A |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583
207177493 | Ground Loop | TRANE | DXVG024B |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583
207177494 | Ground Loop | TRANE | DXVG0244 |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583
207177495 | Ground Loop | TRANE | DXVG0247 |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583
207177496 | Ground Loop | TRANE | DXVG036A |  | 34500 | 19.7 | 25500 | 4.1 | 2.875
207177497 | Ground Loop | TRANE | DXVG036B |  | 34500 | 19.7 | 25500 | 4.1 | 2.875
207177498 | Ground Loop | TRANE | DXVG0364 |  | 34500 | 19.7 | 25500 | 4.1 | 2.875
207177499 | Ground Loop | TRANE | DXVG0367 |  | 34500 | 19.7 | 25500 | 4.1 | 2.875
207177500 | Ground Loop | TRANE | DXVG048A |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833
207177501 | Ground Loop | TRANE | DXVG048B |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833
207177502 | Ground Loop | TRANE | DXVG0484 |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833
207177503 | Ground Loop | TRANE | DXVG060A |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917
207177504 | Ground Loop | TRANE | DXVG060B |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917
207177505 | Ground Loop | TRANE | DXVG0604 |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917
207177506 | Ground Loop | TRANE | DXVG070A |  | 66800 | 19.6 | 52900 | 4 | 5.5667
207177507 | Ground Loop | TRANE | DXVG070B |  | 66800 | 19.6 | 52900 | 4 | 5.5667
207177508 | Ground Loop | TRANE | DXVG0704 |  | 66800 | 19.6 | 52900 | 4 | 5.5667
207178484 | Ground Loop | GEOSTAR | 163H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207178485 | Ground Loop | GEOSTAR | 164H049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207178486 | Ground Loop | GEOSTAR | 164H049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207178492 | Ground Loop | GEOSTAR | 163J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3
211594123 | Ground Loop | TRANE | GEHG024A |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667
211594124 | Ground Loop | TRANE | GEHG030A |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167
211594125 | Ground Loop | TRANE | GEHG036A |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083
211594129 | Ground Loop | TRANE | EXHG009A |  | 8300 | 18.8 | 6100 | 3.7 | 0.69167
211594130 | Ground Loop | TRANE | EXHG012A |  | 12300 | 19.5 | 9300 | 4 | 1.025
211594131 | Ground Loop | TRANE | EXHG015A |  | 15800 | 19 | 12100 | 3.8 | 1.3167
211594132 | Ground Loop | TRANE | EXHG018A |  | 19600 | 20.6 | 14600 | 4.1 | 1.6333
211594133 | Ground Loop | TRANE | EXHG024A |  | 25600 | 20.3 | 19500 | 3.9 | 2.1333
211594134 | Ground Loop | TRANE | EXHG030A |  | 32800 | 20.7 | 23600 | 4.1 | 2.7333
211594135 | Ground Loop | TRANE | EXHG036A |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917
211594136 | Ground Loop | TRANE | EXHG042A |  | 40500 | 21.1 | 29400 | 4.3 | 3.375
211594137 | Ground Loop | TRANE | EXHG048A |  | 47100 | 20.3 | 34600 | 4.3 | 3.925
211594138 | Ground Loop | TRANE | EXHG060A |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083
211594139 | Ground Loop | TRANE | EXHG070A |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083
211594212 | Ground Loop | TRANE | DXHG024A |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583
211594213 | Ground Loop | TRANE | DXHG036A |  | 34500 | 19.7 | 25500 | 4.1 | 2.875
211594214 | Ground Loop | TRANE | DXHG048A |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833
211594215 | Ground Loop | TRANE | DXHG060A |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917
211594216 | Ground Loop | TRANE | DXHG070A |  | 66800 | 19.6 | 52900 | 4 | 5.5667
211594223 | Ground Loop | TRANE | GEHG0097 |  | 8900 | 17.8 | 6700 | 3.7 | 0.74167
211594224 | Ground Loop | TRANE | GEHG0127 |  | 12100 | 17.6 | 9400 | 3.7 | 1.0083
211594225 | Ground Loop | TRANE | GEHG0157 |  | 15500 | 17.4 | 12300 | 3.6 | 1.2917
211594226 | Ground Loop | TRANE | GEHG0187 |  | 18100 | 17.7 | 14300 | 3.6 | 1.5083
211594227 | Ground Loop | TRANE | GEHG024B |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667
211594228 | Ground Loop | TRANE | GEHG0244 |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667
211594229 | Ground Loop | TRANE | GEHG0247 |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667
211594230 | Ground Loop | TRANE | GEHG030B |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167
211594231 | Ground Loop | TRANE | GEHG0304 |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167
211594232 | Ground Loop | TRANE | GEHG0307 |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167
211594233 | Ground Loop | TRANE | GEHG036B |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083
211594234 | Ground Loop | TRANE | GEHG0364 |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083
211594235 | Ground Loop | TRANE | GEHG0367 |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083
211594242 | Ground Loop | TRANE | EXHG0097 |  | 8300 | 18.8 | 6100 | 3.7 | 0.69167
211594243 | Ground Loop | TRANE | EXHG0127 |  | 12300 | 19.5 | 9300 | 4 | 1.025
207198813 | Ground Loop | BOSCH | WQ024-1HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083
207198814 | Ground Loop | BOSCH | WQ024-1HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083
207198817 | Ground Loop | BOSCH | WQ030-1HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958
207198818 | Ground Loop | BOSCH | WQ030-1HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708
207198819 | Ground Loop | BOSCH | WQ030-1VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958
207198820 | Ground Loop | BOSCH | WQ030-1VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708
207198821 | Ground Loop | BOSCH | WQ036-1HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667
207198823 | Ground Loop | BOSCH | WQ036-1VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625
207198824 | Ground Loop | BOSCH | WQ036-1VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583
202350498 | Ground Loop | AAON, Inc. | M2-014-2-H-ACBC-C0-10-000-A |  | 128500 | 17.3 | 95900 | 3.6 | 10.7083
202350499 | Ground Loop | AAON, Inc. | M2-014-2-H-BCBC-V0-10-000-A |  | 128700 | 17.1 | 94800 | 3.6 | 10.725
202350500 | Ground Loop | AAON, Inc. | M2-014-3-H-ACBC-C0-10-000-A |  | 128500 | 17.3 | 95900 | 3.6 | 10.7083
202350501 | Ground Loop | AAON, Inc. | M2-014-3-H-BCBC-V0-10-000-A |  | 128700 | 17.1 | 94800 | 3.6 | 10.725
202350502 | Ground Loop | AAON, Inc. | M2-014-4-H-ACBC-C0-10-000-A |  | 128500 | 17.3 | 95900 | 3.6 | 10.7083
202350503 | Ground Loop | AAON, Inc. | M2-014-4-H-BCBC-V0-10-000-A |  | 128700 | 17.1 | 94800 | 3.6 | 10.725
207083921 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C/A6/FE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
207083923 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N/J6/FE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
207083925 | Ground Loop | CARRIER | 50PCV024J/K*C/A6/FE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
207083927 | Ground Loop | CARRIER | 50PCV024J/K*N/J6/FE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
207083961 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C/A3/CE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
207083965 | Ground Loop | CARRIER | 50PCV036J/K*C/A3/CE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
207083969 | Ground Loop | CARRIER | 50PCH036N/P/W/Y*C/A4/DE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
207083973 | Ground Loop | CARRIER | 50PCV036J/K*C/A4/DE |  | 38300 | 17.1 | 26700 | 3.6 | 3.1917
5615034 | Ground Loop | DAIKIN | WCCW5030*E*01* |  | 31500 | 17.7 | 23100 | 3.6 | 2.625
5615035 | Ground Loop | DAIKIN | WCCW5030*F*01* |  | 31500 | 17.7 | 23100 | 3.6 | 2.625
5615036 | Ground Loop | DAIKIN | WCCW5030*J*01* |  | 31500 | 17.7 | 23100 | 3.6 | 2.625
5615037 | Ground Loop | DAIKIN | WCCW5030*K*01* |  | 31500 | 17.7 | 23100 | 3.6 | 2.625
5615042 | Ground Loop | DAIKIN | WCCW5036*E*01* |  | 37800 | 17.7 | 28400 | 3.6 | 3.15
5615043 | Ground Loop | DAIKIN | WCCW5036*F*01* |  | 37800 | 17.7 | 28400 | 3.6 | 3.15
5615044 | Ground Loop | DAIKIN | WCCW5036*J*01* |  | 37800 | 17.7 | 28400 | 3.6 | 3.15
5615045 | Ground Loop | DAIKIN | WCCW5036*K*01* |  | 37800 | 17.7 | 28400 | 3.6 | 3.15
5615050 | Ground Loop | DAIKIN | WCCW5042*E*01* |  | 44500 | 17.1 | 33900 | 3.7 | 3.7083
5615051 | Ground Loop | DAIKIN | WCCW5042*F*01* |  | 44500 | 17.1 | 33900 | 3.7 | 3.7083
5615052 | Ground Loop | DAIKIN | WCCW5042*K*01* |  | 44500 | 17.1 | 33900 | 3.7 | 3.7083
5615053 | Ground Loop | DAIKIN | WCCW5042*L*01* |  | 44500 | 17.1 | 33900 | 3.7 | 3.7083
5646343 | Ground Loop | GEOCOMFORT | GXT024D |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667
5646344 | Ground Loop | HYDRON MODULE | HXT024D |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667
5646345 | Ground Loop | TETCO | TXT024D |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667
5646346 | Ground Loop | GEOCOMFORT | GXT024D2 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667
5646347 | Ground Loop | HYDRON MODULE | HXT024D2 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667
5646348 | Ground Loop | TETCO | TXT024D2 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667
5646349 | Ground Loop | GEOCOMFORT | GXT024D3 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667
5646350 | Ground Loop | HYDRON MODULE | HXT024D3 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667
5646351 | Ground Loop | TETCO | TXT024D3 |  | 27200 | 20.3 | 19800 | 4.3 | 2.2667
5646371 | Ground Loop | GEOCOMFORT | GXT036D |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417
5646372 | Ground Loop | HYDRON MODULE | HXT036D |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417
5646373 | Ground Loop | TETCO | TXT036D |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417
5646374 | Ground Loop | GEOCOMFORT | GXT036D2 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417
207083897 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C/A3/CE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
207083899 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N/J3/CE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
207083901 | Ground Loop | CARRIER | 50PCV024J/K*C/A3/CE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
207083903 | Ground Loop | CARRIER | 50PCV024J/K*N/J3/CE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
207083905 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C/A4/DE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
207083907 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N/J4/DE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
207083909 | Ground Loop | CARRIER | 50PCV024J/K*C/A4/DE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
207083911 | Ground Loop | CARRIER | 50PCV024J/K*N/J4/DE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
207083913 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*C/A5/EE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
207083915 | Ground Loop | CARRIER | 50PCH024N/P/W/Y*N/J5/EE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
207083917 | Ground Loop | CARRIER | 50PCV024J/K*C/A5/EE |  | 25800 | 17.65 | 17700 | 3.6 | 2.15
207083919 | Ground Loop | CARRIER | 50PCV024J/K*N/J5/EE |  | 25700 | 17.15 | 17400 | 3.6 | 2.1417
215399846 | Ground Loop | DAIKIN | WSMV060K3*G/J*T |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917
203383886 | Ground Loop | CARRIER | 50PSV048***3/CA |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
203383887 | Ground Loop | CARRIER | 50PSV048***5/EA |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
203383888 | Ground Loop | CARRIER | 50PSV048***6/FA |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
203383889 | Ground Loop | CARRIER | 50PSH048***3/CA |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203383890 | Ground Loop | CARRIER | 50PSH048***5/EA |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203383891 | Ground Loop | CARRIER | 50PSH048***6/FA |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203383892 | Ground Loop | FHP | EP018-1VT*******B |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
203383893 | Ground Loop | FHP | EP018-2VT*******B |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
203383894 | Ground Loop | FHP | EP018-1HZ*******B |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
203383895 | Ground Loop | FHP | EP018-2HZ*******B |  | 20500 | 17.9 | 14800 | 3.65 | 1.7083
203383896 | Ground Loop | FHP | EP042-1VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
203383897 | Ground Loop | FHP | EP042-3VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
203383898 | Ground Loop | FHP | EP042-4VT*******B |  | 40600 | 19.4 | 26800 | 3.7 | 3.3833
203383899 | Ground Loop | FHP | EP042-1HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203383900 | Ground Loop | FHP | EP042-3HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833
203383901 | Ground Loop | FHP | EP042-4HZ*******B |  | 40600 | 19.5 | 26800 | 4 | 3.3833
217903461 | Ground Loop | WaterFurnace | V5R060*D4**4* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833
217903462 | Ground Loop | WaterFurnace | V5R060*D4**5* |  | 63400 | 18.5 | 45700 | 3.6 | 5.2833
217903463 | Ground Loop | WaterFurnace | V5R072*D4**1* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875
217903464 | Ground Loop | WaterFurnace | V5R072*D4**4* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875
217903465 | Ground Loop | WaterFurnace | V5R072*D4**5* |  | 70500 | 17.6 | 55600 | 3.6 | 5.875
217903466 | Ground Loop | WaterFurnace | V5R096*T4**5* |  | 88100 | 18 | 69900 | 3.8 | 7.3417
217903467 | Ground Loop | WaterFurnace | V5R120*T4**5* |  | 119400 | 17.7 | 92000 | 3.8 | 9.95
202146936 | Ground Loop | GEOCOMFORT | GZS018*****1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675
202146939 | Ground Loop | HYDRON MODULE | HZS018*****1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675
202146942 | Ground Loop | TETCO | TZS018*****1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675
202146943 | Ground Loop | GEOCOMFORT | GZS024 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417
202146944 | Ground Loop | GEOCOMFORT | GZS024*2 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417
202146945 | Ground Loop | GEOCOMFORT | GZS024*3 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417
202146946 | Ground Loop | GEOCOMFORT | GZS024*4 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417
202146947 | Ground Loop | GEOCOMFORT | GZS024*A |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417
202146948 | Ground Loop | GEOCOMFORT | GZS024*****1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833
202146949 | Ground Loop | GEOCOMFORT | GZS024*2***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833
202146950 | Ground Loop | GEOCOMFORT | GZS024*3***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833
202146951 | Ground Loop | GEOCOMFORT | GZS024*A***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833
202146952 | Ground Loop | HYDRON MODULE | HZS024 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417
202146953 | Ground Loop | HYDRON MODULE | HZS024*2 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417
202146954 | Ground Loop | HYDRON MODULE | HZS024*3 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417
202146955 | Ground Loop | HYDRON MODULE | HZS024*4 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417
202146956 | Ground Loop | HYDRON MODULE | HZS024*A |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417
202146957 | Ground Loop | HYDRON MODULE | HZS024*****1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833
202146958 | Ground Loop | HYDRON MODULE | HZS024*2***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833
202146959 | Ground Loop | HYDRON MODULE | HZS024*3***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833
202146960 | Ground Loop | HYDRON MODULE | HZS024*A***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833
202146961 | Ground Loop | TETCO | TZS024 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417
202146962 | Ground Loop | TETCO | TZS024*2 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417
202146963 | Ground Loop | TETCO | TZS024*3 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417
202146964 | Ground Loop | TETCO | TZS024*4 |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417
202146965 | Ground Loop | TETCO | TZS024*A |  | 25700 | 17.4 | 18500 | 3.6 | 2.1417
202146966 | Ground Loop | TETCO | TZS024*****1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833
202146967 | Ground Loop | TETCO | TZS024*2***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833
202146968 | Ground Loop | TETCO | TZS024*3***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833
202146969 | Ground Loop | TETCO | TZS024*A***1 |  | 26200 | 19.6 | 18000 | 3.9 | 2.1833
202146970 | Ground Loop | GEOCOMFORT | GZS030 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475
202146971 | Ground Loop | GEOCOMFORT | GZS030*2 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475
202146972 | Ground Loop | GEOCOMFORT | GZS030*3 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475
202146973 | Ground Loop | GEOCOMFORT | GZS030*4 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475
202146974 | Ground Loop | GEOCOMFORT | GZS030*A |  | 29700 | 17.7 | 22900 | 3.6 | 2.475
202146975 | Ground Loop | GEOCOMFORT | GZS030*****1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167
202146976 | Ground Loop | GEOCOMFORT | GZS030*2***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167
202146977 | Ground Loop | HYDRON MODULE | HZS030 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475
202146978 | Ground Loop | HYDRON MODULE | HZS030*2 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475
202146979 | Ground Loop | HYDRON MODULE | HZS030*3 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475
202146980 | Ground Loop | HYDRON MODULE | HZS030*4 |  | 29700 | 17.7 | 22900 | 3.6 | 2.475
202146981 | Ground Loop | HYDRON MODULE | HZS030*A |  | 29700 | 17.7 | 22900 | 3.6 | 2.475
202146982 | Ground Loop | HYDRON MODULE | HZS030*****1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167
206438781 | Ground Loop | FHP | EP009-1HZ/VT*-*****B |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167
206438782 | Ground Loop | FHP | EP009-2HZ/VT*-*****B |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167
206438783 | Ground Loop | FHP | EP012-1HZ/VT*-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438784 | Ground Loop | FHP | EP015-1HZ/VT*-*****B |  | 16200 | 19.8 | 11000 | 3.63 | 1.35
206438785 | Ground Loop | FHP | EP015-2HZ/VT*-*****B |  | 16200 | 19.8 | 11000 | 3.63 | 1.35
206438786 | Ground Loop | FHP | EP030-2HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
206438787 | Ground Loop | FHP | EP030-4HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
206438788 | Ground Loop | FHP | EP030-3HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
206438789 | Ground Loop | FHP | EP030-1HZ/VT*-*****B |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
206438790 | Ground Loop | FHP | EP060-4HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
206438791 | Ground Loop | FHP | EP060-3HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
206438792 | Ground Loop | FHP | EP060-1HZ/VT*-*****B |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
206438793 | Ground Loop | FHP | EP070-1HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
206438794 | Ground Loop | FHP | EP070-3HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
206438795 | Ground Loop | FHP | EP070-4HZ/VT*-*****B |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
207335253 | Ground Loop | GEOSTAR | 161/162K049**1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207335255 | Ground Loop | GEOSTAR | 161/162J072**1*(1,4)***** |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207335335 | Ground Loop | GEOSTAR | 111J049**1*(1,2) |  | 47700 | 18.2 | 38000 | 3.8 | 3.975
207335337 | Ground Loop | GEOSTAR | 111J072**1*1 |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083
207335338 | Ground Loop | GEOSTAR | 111K038**1*(1,2)* |  | 36000 | 18.7 | 27400 | 3.9 | 3
207335397 | Ground Loop | GeoSmart Energy | GT026**1*(1,4)*J |  | 26400 | 19.6 | 19500 | 4 | 2.2
207335398 | Ground Loop | GeoSmart Energy | GT038**1*(1,2,4)*K |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
217351900 | Ground Loop | KEEPRITE | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417
217351901 | Ground Loop | KEEPRITE | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583
217351903 | Ground Loop | KEEPRITE | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583
217351904 | Ground Loop | KEEPRITE | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167
217351905 | Ground Loop | KEEPRITE | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167
217351906 | Ground Loop | KEEPRITE | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05
217351907 | Ground Loop | KEEPRITE | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833
217351909 | Ground Loop | KEEPRITE | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325
217351910 | Ground Loop | KEEPRITE | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167
217351911 | Ground Loop | KEEPRITE | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333
10298941 | Ground Loop | WaterFurnace | UVV/UVH048**0*1 |  | 48000 | 20 | 38000 | 3.8 | 4
10298942 | Ground Loop | WaterFurnace | UVV/UVH048**3*1 |  | 48000 | 20 | 38000 | 3.8 | 4
10298943 | Ground Loop | WaterFurnace | UVV/UVH048**4*1 |  | 48000 | 20 | 38000 | 3.8 | 4
10298944 | Ground Loop | WaterFurnace | UVV/UVH060**0*1 |  | 62000 | 17.8 | 45000 | 3.7 | 5.1667
10298946 | Ground Loop | WaterFurnace | UVV/UVH060**3*1 |  | 62000 | 17.8 | 45000 | 3.7 | 5.1667
10298947 | Ground Loop | WaterFurnace | UVV/UVH060**4*1 |  | 62000 | 17.8 | 45000 | 3.7 | 5.1667
10304639 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10304640 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10304641 | Ground Loop | GeoSmart Energy | GTZ026*1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10304642 | Ground Loop | GEOSTAR | 103H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10304646 | Ground Loop | GEOSTAR | 103H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10304657 | Ground Loop | GeoSmart Energy | GTZ026*1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10305457 | Ground Loop | GEOSTAR | 104H026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10305458 | Ground Loop | GEOSTAR | 104H026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10316642 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST026**1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10316643 | Ground Loop | GeoSmart Energy | GTS026*1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10316644 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST026**1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10316645 | Ground Loop | GeoSmart Energy | GTS026*1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
10316654 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
10316655 | Ground Loop | GEOSTAR | 104H049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
10316656 | Ground Loop | GeoSmart Energy | GTS049*1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
10316657 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
10316658 | Ground Loop | GeoSmart Energy | GTS049*1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
10316660 | Ground Loop | GEOSTAR | 104H049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
10316661 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
10316662 | Ground Loop | GEOSTAR | 104H064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
10316663 | Ground Loop | GeoSmart Energy | GTS064*1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
10316664 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
10316666 | Ground Loop | GEOSTAR | 104H064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
10316667 | Ground Loop | GeoSmart Energy | GTS064*1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
10318010 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS022**1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583
10318016 | Ground Loop | GeoSmart Energy | GSZ022*1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583
10318017 | Ground Loop | GEOSTAR | 103H022**1 | SAH022* | 18700 | 19.1 | 14000 | 3.8 | 1.5583
10318018 | Ground Loop | GeoSmart Energy | GSZ022*1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583
10318019 | Ground Loop | GEOSTAR | 103H022**1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583
10318020 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS022**1 | SRAA026* | 18700 | 19.1 | 14000 | 3.8 | 1.5583
10318021 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS030**1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05
10318022 | Ground Loop | GEOSTAR | 103H030**1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05
10318023 | Ground Loop | GeoSmart Energy | GSZ030*1 | SAH030* | 24600 | 18.9 | 19800 | 3.9 | 2.05
10318024 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS030**1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05
10318025 | Ground Loop | GeoSmart Energy | GSZ030*1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05
10318026 | Ground Loop | GEOSTAR | 103H030**1 | SRAA026* | 24600 | 18.9 | 19800 | 3.9 | 2.05
10318045 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS048**1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417
10318046 | Ground Loop | GeoSmart Energy | GSZ048*1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417
10318047 | Ground Loop | GEOSTAR | 103H048**1 | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417
202330542 | Ground Loop | AAON, Inc. | M2-004-4-H-BCBC-V0-10-000-A |  | 51900 | 18.8 | 35200 | 3.8 | 4.325
202330543 | Ground Loop | AAON, Inc. | M2-004-4-H-DCAC-S0-10-000-A |  | 49200 | 17.9 | 34800 | 3.6 | 4.1
202330544 | Ground Loop | AAON, Inc. | M2-004-4-H-DCBC-S0-10-000-A |  | 50900 | 18.2 | 35100 | 3.6 | 4.2417
202330562 | Ground Loop | AAON, Inc. | M2-006-2-H-ACBC-C0-10-000-A |  | 68400 | 17.6 | 44000 | 3.6 | 5.7
202330564 | Ground Loop | AAON, Inc. | M2-006-2-H-BCBC-V0-10-000-A |  | 68700 | 17.3 | 43100 | 3.6 | 5.725
202330566 | Ground Loop | AAON, Inc. | M2-006-3-H-ACBC-C0-10-000-A |  | 68400 | 17.6 | 44000 | 3.6 | 5.7
202330568 | Ground Loop | AAON, Inc. | M2-006-3-H-BCBC-V0-10-000-A |  | 68700 | 17.3 | 43100 | 3.6 | 5.725
202330570 | Ground Loop | AAON, Inc. | M2-006-4-H-ACBC-C0-10-000-A |  | 68400 | 17.6 | 44000 | 3.6 | 5.7
3706350 | Ground Loop | GEOSTAR | ZS015**0*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225
3706351 | Ground Loop | GEOSTAR | ZS015**2*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225
3706369 | Ground Loop | GEOSTAR | ZS018**0*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417
3706370 | Ground Loop | GEOSTAR | ZS018**2*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417
3706371 | Ground Loop | GEOSTAR | ZS023**0*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
3706373 | Ground Loop | GEOSTAR | ZS023**2*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
3706374 | Ground Loop | GEOSTAR | ZS023**3*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
3706375 | Ground Loop | GEOSTAR | ZS023**4*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
3706376 | Ground Loop | GEOSTAR | ZS024**0*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
3706377 | Ground Loop | GEOSTAR | ZS024**2*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
3706378 | Ground Loop | GEOSTAR | ZS024**3*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
3706379 | Ground Loop | GEOSTAR | ZS024**4*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
3706380 | Ground Loop | GEOSTAR | ZS030**0*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
3706381 | Ground Loop | GEOSTAR | ZS030**2*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
3706382 | Ground Loop | GEOSTAR | ZS030**3*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
3706383 | Ground Loop | GEOSTAR | ZS030**4*1 |  | 29000 | 18.3 | 22800 | 3.8 | 2.4167
3706391 | Ground Loop | GEOSTAR | ZS042**0*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
3706392 | Ground Loop | GEOSTAR | ZS042**3*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
3706393 | Ground Loop | GEOSTAR | ZS042**4*1 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
3706394 | Ground Loop | GEOSTAR | ZS048**0*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
3706395 | Ground Loop | GEOSTAR | ZS048**3*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
3706396 | Ground Loop | GEOSTAR | ZS048**4*1 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
3706397 | Ground Loop | GEOSTAR | ZS060**0*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
3706398 | Ground Loop | GEOSTAR | ZS060**3*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
3706399 | Ground Loop | GEOSTAR | ZS060**4*1 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
3811559 | Ground Loop | WaterFurnace | USV/USH024**0*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
3811671 | Ground Loop | WaterFurnace | USV/USH024**2*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
3811673 | Ground Loop | WaterFurnace | USV/USH024**3*1 |  | 24400 | 17.5 | 17500 | 3.8 | 2.0333
217351757 | Ground Loop | BRYANT | GZ024SA*C******1 | F(T,G,E)5(A,B)***36*** | 26000 | 18.5 | 18800 | 4.1 | 2.1667
217351758 | Ground Loop | BRYANT | GZ024SA*N******1 | F(T,G,E)5(A,B)***36*** | 25400 | 18.1 | 18400 | 4 | 2.1167
217351761 | Ground Loop | BRYANT | GZ036SA*C******1 | F(T,G,E)5(A,B)***48*** | 39000 | 18.5 | 27400 | 3.7 | 3.25
217351762 | Ground Loop | BRYANT | GZ036SA*N******1 | F(T,G,E)5(A,B)***48*** | 38000 | 18.1 | 26800 | 3.7 | 3.1667
217351763 | Ground Loop | BRYANT | GZ048SA*C******1 | F(T,G,E)5(A,B)***48*** | 48500 | 17.1 | 37800 | 4 | 4.0417
217351765 | Ground Loop | BRYANT | GZ060SA*C******1 | F(T,G,E)5(A,B)***60*** | 60500 | 17.6 | 47000 | 3.7 | 5.0417
217351766 | Ground Loop | BRYANT | GZ060SA*N******1 | F(T,G,E)5(A,B)***60*** | 59500 | 17.3 | 46000 | 3.7 | 4.9583
217351768 | Ground Loop | BRYANT | GZ024SA*C******1 | CAAMP2***AMA | 25900 | 17.5 | 18900 | 3.8 | 2.1583
217351769 | Ground Loop | BRYANT | GZ024SA*N******1 | CAAMP2***AMA | 25400 | 17.1 | 18500 | 3.7 | 2.1167
217351770 | Ground Loop | BRYANT | GZ036SA*C******1 | CAAMP3***AMA | 37400 | 17.7 | 27600 | 3.6 | 3.1167
217351771 | Ground Loop | BRYANT | GZ036SA*N******1 | CAAMP3***AMA | 36600 | 17.4 | 27100 | 3.6 | 3.05
217351772 | Ground Loop | BRYANT | GZ048SA*C******1 | CAAMP4***AMA | 49000 | 17.1 | 37900 | 3.9 | 4.0833
217351774 | Ground Loop | BRYANT | GZ060SA*C******1 | CAAMP6***AMA | 63900 | 17.7 | 48300 | 3.8 | 5.325
217351775 | Ground Loop | BRYANT | GZ060SA*N******1 | CAAMP6***AMA | 62600 | 17.3 | 47300 | 3.7 | 5.2167
217351776 | Ground Loop | BRYANT | GZ072SA*C******1 | CAAMP6***AMA | 70000 | 17.5 | 55200 | 3.6 | 5.8333
217351784 | Ground Loop | ARCOAIRE | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667
217351785 | Ground Loop | ARCOAIRE | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167
202147073 | Ground Loop | TETCO | TZS060*****1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75
202147074 | Ground Loop | TETCO | TZS060*2***1 |  | 57000 | 17.5 | 46200 | 3.6 | 4.75
202147690 | Ground Loop | GEOCOMFORT | GZT030*A |  | 31500 | 17.5 | 23300 | 3.7 | 2.625
202147691 | Ground Loop | HYDRON MODULE | HZT030*A |  | 31500 | 17.5 | 23300 | 3.7 | 2.625
202147692 | Ground Loop | TETCO | TZT030*A |  | 31500 | 17.5 | 23300 | 3.7 | 2.625
202147693 | Ground Loop | TETCO | TZT048*A |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583
202147697 | Ground Loop | GEOCOMFORT | GZS015*A***1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833
202147698 | Ground Loop | HYDRON MODULE | HZS015*A***1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833
202147699 | Ground Loop | TETCO | TZS015*A***1 |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833
202147700 | Ground Loop | GEOCOMFORT | GZS018*A***1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675
202147701 | Ground Loop | HYDRON MODULE | HZS018*A***1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675
202147702 | Ground Loop | TETCO | TZS018*A***1 |  | 20100 | 18.7 | 14100 | 3.7 | 1.675
202147703 | Ground Loop | GEOCOMFORT | GZS030*3***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167
202147704 | Ground Loop | GEOCOMFORT | GZS030*A***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167
202147705 | Ground Loop | HYDRON MODULE | HZS030*3***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167
202147706 | Ground Loop | HYDRON MODULE | HZS030*A***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167
202147707 | Ground Loop | TETCO | TZS030*3***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167
202147708 | Ground Loop | TETCO | TZS030*A***1 |  | 29000 | 18.8 | 21700 | 3.8 | 2.4167
202147709 | Ground Loop | GEOCOMFORT | GZS042*3***1 |  | 40700 | 19.2 | 30200 | 3.8 | 3.3917
206608717 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ048J1* | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417
206608718 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ048J1* | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417
206608719 | Ground Loop | GEOSTAR | 103J048**1* | SAH048* | 42500 | 18.7 | 33400 | 4 | 3.5417
206608720 | Ground Loop | GEOSTAR | 103J048**1* | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417
206608721 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ060J1* | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
206608722 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ060J1* | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
206608723 | Ground Loop | GEOSTAR | 103J060**1* | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
206608724 | Ground Loop | GEOSTAR | 103J060**1* | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
206611120 | Ground Loop | COMFORT-AIRE | HEH/V060C |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667
206611121 | Ground Loop | CENTURY | HEH/V060C |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667
9850201 | Ground Loop | DAIKIN | WVFW1030*K***01 |  | 30700 | 19.1 | 22300 | 3.9 | 2.5583
9910449 | Ground Loop | GEOCOMFORT | GZS018*****1B |  | 20800 | 20.5 | 14200 | 3.8 | 1.7333
205503116 | Ground Loop | BOSCH-GEO | SM024-1CS*******A | BMAC2430BNTD | 25500 | 18.1 | 18900 | 3.95 | 2.125
205503120 | Ground Loop | BOSCH-GEO | LM024-1CS*******A | BMAC2430BNTD | 25500 | 18.1 | 18900 | 3.95 | 2.125
205503124 | Ground Loop | BOSCH | SM024-1CS*******A | BMAC2430BNTD | 25500 | 18.1 | 18900 | 3.95 | 2.125
205503128 | Ground Loop | FHP | LM024-1CS*******A | BMAC2430BNTD | 25500 | 18.1 | 18900 | 3.95 | 2.125
205652453 | Ground Loop | BOSCH-GEO | SM048-1CS*-*****A | BVA-48WN1-M20 | 51700 | 18.1 | 38000 | 4 | 4.3083
205652454 | Ground Loop | BOSCH-GEO | SM060-1CS*-*****A | BVA-60WN1-M20 | 62900 | 17.7 | 50100 | 4 | 5.2417
205652455 | Ground Loop | BOSCH-GEO | SM048-1CS*-*****A | BMAC4248CNTF | 50300 | 17.5 | 37200 | 3.9 | 4.1917
205652457 | Ground Loop | BOSCH-GEO | LM048-1CS*-*****A | BVA-48WN1-M20 | 51700 | 18.1 | 38000 | 4 | 4.3083
205652458 | Ground Loop | BOSCH-GEO | LM060-1CS*-*****A | BVA-60WN1-M20 | 62900 | 17.7 | 50100 | 4 | 5.2417
205652459 | Ground Loop | BOSCH-GEO | LM048-1CS*-*****A | BMAC4248CNTF | 50300 | 17.5 | 37200 | 3.9 | 4.1917
205652461 | Ground Loop | BOSCH | SM048-1CS*-*****A | BVA-48WN1-M20 | 51700 | 18.1 | 38000 | 4 | 4.3083
205652462 | Ground Loop | BOSCH | SM060-1CS*-*****A | BVA-60WN1-M20 | 62900 | 17.7 | 50100 | 4 | 5.2417
205652463 | Ground Loop | BOSCH | SM048-1CS*-*****A | BMAC4248CNTF | 50300 | 17.5 | 37200 | 3.9 | 4.1917
205652465 | Ground Loop | FHP | LM048-1CS*-*****A | BVA-48WN1-M20 | 51700 | 18.1 | 38000 | 4 | 4.3083
205652466 | Ground Loop | FHP | LM060-1CS*-*****A | BVA-60WN1-M20 | 62900 | 17.7 | 50100 | 4 | 5.2417
205652467 | Ground Loop | FHP | LM048-1CS*-*****A | BMAC4248CNTF | 50300 | 17.5 | 37200 | 3.9 | 4.1917
4947178 | Ground Loop | TRANE | VSVE0241 |  | 25900 | 22.32 | 18400 | 4.17 | 2.1583
4947179 | Ground Loop | TRANE | VSVE0242 |  | 25900 | 22.32 | 18400 | 4.17 | 2.1583
4947180 | Ground Loop | TRANE | VSVE0244 |  | 25900 | 22.32 | 18400 | 4.17 | 2.1583
4947183 | Ground Loop | TRANE | VSVE0331 |  | 34300 | 18.08 | 24500 | 3.86 | 2.8583
4947184 | Ground Loop | TRANE | VSVE0332 |  | 34300 | 18.08 | 24500 | 3.86 | 2.8583
4947185 | Ground Loop | TRANE | VSVE0334 |  | 34300 | 18.08 | 24500 | 3.86 | 2.8583
4947240 | Ground Loop | TRANE | VSVE0501 |  | 54100 | 18.76 | 41400 | 3.75 | 4.5083
4947241 | Ground Loop | TRANE | VSVE0502 |  | 54100 | 18.76 | 41400 | 3.75 | 4.5083
4947242 | Ground Loop | TRANE | VSVE0504 |  | 54100 | 18.76 | 41400 | 3.75 | 4.5083
5211514 | Ground Loop | DAIKIN | WGSV/WGSH007B*A |  | 8400 | 18.1 | 6200 | 3.9 | 0.7
5211515 | Ground Loop | DAIKIN | WGSV/WGSH007B*E |  | 8400 | 18.1 | 6200 | 3.9 | 0.7
5211516 | Ground Loop | DAIKIN | WGSV/WGSH007B*J |  | 8400 | 18.1 | 6200 | 3.9 | 0.7
5220636 | Ground Loop | DAIKIN | WGSV/WGSH012B*A |  | 13300 | 18.1 | 10000 | 3.9 | 1.1083
5220637 | Ground Loop | DAIKIN | WGSV/WGSH012B*E |  | 13300 | 18.1 | 10000 | 3.9 | 1.1083
5220638 | Ground Loop | DAIKIN | WGSV/WGSH012B*J |  | 13300 | 17.2 | 10000 | 3.8 | 1.1083
5220663 | Ground Loop | DAIKIN | WGSV/WGSH015B*E |  | 16000 | 21.2 | 11700 | 4.1 | 1.3333
5220664 | Ground Loop | DAIKIN | WGSV/WGSH015B*J |  | 16000 | 19.1 | 11700 | 3.8 | 1.3333
5220666 | Ground Loop | DAIKIN | WGSV/WGSH019B*E |  | 18700 | 18.7 | 13800 | 4.1 | 1.5583
5220667 | Ground Loop | DAIKIN | WGSV/WGSH019B*J |  | 18700 | 18.7 | 13800 | 4.1 | 1.5583
5220670 | Ground Loop | DAIKIN | WGSV/WGSH024B*E |  | 27500 | 19.9 | 17700 | 4.1 | 2.2917
5220671 | Ground Loop | DAIKIN | WGSV/WGSH024B*F |  | 27500 | 19.9 | 17700 | 4.1 | 2.2917
6502003 | Ground Loop | GEOSTAR | GBV/GBH072**0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
6502004 | Ground Loop | GEOSTAR | GBV/GBH072**3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
6502005 | Ground Loop | GEOSTAR | GBV/GBH072**3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
6502006 | Ground Loop | GEOSTAR | GBV/GBH072**4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
6502007 | Ground Loop | GEOSTAR | GBV/GBH072**4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
6674620 | Ground Loop | BOSCH | LM024-1CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167
6674621 | Ground Loop | BOSCH | LM024-3CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167
6674622 | Ground Loop | BOSCH | LM024-2CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167
6674623 | Ground Loop | BOSCH | LM024-4CF/HZ/VT*-*****A |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167
6676515 | Ground Loop | BOSCH | LM036-1VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
6676516 | Ground Loop | BOSCH | LM036-3VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
6676518 | Ground Loop | BOSCH | LM036-2VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
6676519 | Ground Loop | BOSCH | LM036-4VT/CF/HZ*-*****A |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
6677645 | Ground Loop | BOSCH | LM048-1VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275
6677682 | Ground Loop | BOSCH | LM048-3VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275
6677754 | Ground Loop | BOSCH | LM048-4VT/CF/HZ*-*****A |  | 51300 | 18 | 36900 | 3.9 | 4.275
6677875 | Ground Loop | BOSCH | LM060-1VT/CF/HZ*-*****A |  | 65100 | 17.6 | 45500 | 3.7 | 5.425
6677876 | Ground Loop | BOSCH | LM060-3VT/CF/HZ*-*****A |  | 65100 | 17.6 | 45500 | 3.7 | 5.425
6677878 | Ground Loop | BOSCH | LM060-4VT/CF/HZ*-*****A |  | 65100 | 17.6 | 45500 | 3.7 | 5.425
216767332 | Ground Loop | TETCO | TYT072* |  | 70300 | 17.1 | 57800 | 3.8 | 5.8583
216767333 | Ground Loop | HYDRON MODULE | HVT024* |  | 25800 | 18.6 | 19400 | 4 | 2.15
216767334 | Ground Loop | HYDRON MODULE | HVT030* |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833
216767335 | Ground Loop | HYDRON MODULE | HVT036* |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167
216767336 | Ground Loop | HYDRON MODULE | HVT042* |  | 45900 | 18.5 | 32400 | 3.9 | 3.825
216767337 | Ground Loop | HYDRON MODULE | HVT048* |  | 50300 | 18.8 | 38500 | 4 | 4.1917
216767338 | Ground Loop | HYDRON MODULE | HYT024* |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583
216767339 | Ground Loop | HYDRON MODULE | HYT036* |  | 39700 | 21 | 27900 | 4.3 | 3.3083
216767340 | Ground Loop | HYDRON MODULE | HYT048* |  | 51900 | 19.2 | 36700 | 4.1 | 4.325
216767341 | Ground Loop | HYDRON MODULE | HVT060* |  | 60900 | 17.6 | 46300 | 3.8 | 5.075
216767342 | Ground Loop | HYDRON MODULE | HYT060* |  | 63100 | 18.7 | 49100 | 4 | 5.2583
216767344 | Ground Loop | HYDRON MODULE | HYT072* |  | 70300 | 17.1 | 57800 | 3.8 | 5.8583
216772562 | Ground Loop | Enertech | EBS018* | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167
216772563 | Ground Loop | Enertech | EBT024* | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917
216772564 | Ground Loop | Enertech | EBT036* | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075
216772565 | Ground Loop | Enertech | EBT048* | EAD048 | 47800 | 17.3 | 41000 | 3.6 | 3.9833
216772567 | Ground Loop | Enertech | EVS012* |  | 12625 | 18.2 | 9475 | 3.6 | 1.0521
216772568 | Ground Loop | Enertech | EVS018* |  | 22275 | 24.1 | 15400 | 4.24 | 1.8562
216772569 | Ground Loop | Enertech | EVT024* |  | 25775 | 20.5 | 19400 | 4.09 | 2.1479
216772570 | Ground Loop | Enertech | EVT030* |  | 32900 | 19.8 | 24425 | 3.98 | 2.7417
216772571 | Ground Loop | Enertech | EVT036* |  | 38450 | 18.8 | 29500 | 3.94 | 3.2042
216772572 | Ground Loop | Enertech | EVT042* |  | 45900 | 19.4 | 32975 | 4.14 | 3.825
216772573 | Ground Loop | Enertech | EVT048* |  | 50300 | 18.8 | 38500 | 4 | 4.1917
5339321 | Ground Loop | TTHERM GEO | TVA-036-1* |  | 38100 | 17.47 | 32700 | 3.66 | 3.175
5339322 | Ground Loop | TTHERM GEO | TVA-048-1* |  | 52600 | 17.1 | 45200 | 3.6 | 4.3833
5339323 | Ground Loop | TTHERM GEO | TVA-060-1* |  | 61800 | 17.1 | 50700 | 3.6 | 5.15
5440541 | Ground Loop | GEOCOMFORT | GXT060D |  | 63000 | 17.8 | 47700 | 3.7 | 5.25
5440542 | Ground Loop | HYDRON MODULE | HXT060D |  | 63000 | 17.8 | 47700 | 3.7 | 5.25
5440543 | Ground Loop | TETCO | TXT060D |  | 63000 | 17.8 | 47700 | 3.7 | 5.25
5440554 | Ground Loop | GEOCOMFORT | GXT072D |  | 71100 | 17.1 | 55900 | 3.6 | 5.925
5440555 | Ground Loop | HYDRON MODULE | HXT072D |  | 71100 | 17.1 | 55900 | 3.6 | 5.925
5440557 | Ground Loop | TETCO | TXT072D |  | 71100 | 17.1 | 55900 | 3.6 | 5.925
5440573 | Ground Loop | GEOCOMFORT | GXT060D2 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25
5440574 | Ground Loop | HYDRON MODULE | HXT060D2 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25
5440575 | Ground Loop | TETCO | TXT060D2 |  | 63000 | 17.8 | 47700 | 3.7 | 5.25
5440576 | Ground Loop | GEOCOMFORT | GXT072D2 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925
5440577 | Ground Loop | HYDRON MODULE | HXT072D2 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925
5440578 | Ground Loop | TETCO | TXT072D2 |  | 71100 | 17.1 | 55900 | 3.6 | 5.925
215400148 | Ground Loop | DAIKIN | WSMV048E1*G/J*C |  | 49800 | 19.09 | 36400 | 3.75 | 4.15
215400149 | Ground Loop | DAIKIN | WSMV048F3*G/J*C |  | 49800 | 19.09 | 36400 | 3.75 | 4.15
217735435 | Ground Loop | DAIKIN | WSTH024J1*H*C |  | 25100 | 19.52 | 17200 | 3.84 | 2.0917
217735437 | Ground Loop | DAIKIN | WSTH030J1*H*C |  | 32700 | 19.29 | 20600 | 3.68 | 2.725
217735439 | Ground Loop | DAIKIN | WSTH036J1*H*C |  | 38700 | 20.23 | 25900 | 3.67 | 3.225
217735441 | Ground Loop | DAIKIN | WSTV024J1*H*C |  | 22400 | 17.63 | 17200 | 3.9 | 1.8667
217735443 | Ground Loop | DAIKIN | WSTV030J1*H*C |  | 32200 | 19.09 | 20800 | 3.7 | 2.6833
217735445 | Ground Loop | DAIKIN | WSTV036J1*H*C |  | 39100 | 20.7 | 25600 | 3.61 | 3.2583
8738031 | Ground Loop | GEOCOMFORT | GVT060 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075
8738032 | Ground Loop | HYDRON MODULE | HVT060 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075
8738033 | Ground Loop | TETCO | TVT060 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075
8738034 | Ground Loop | GEOCOMFORT | GVT060*2 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075
8738035 | Ground Loop | HYDRON MODULE | HVT060*2 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075
8738036 | Ground Loop | TETCO | TVT060*2 |  | 60900 | 17.6 | 46300 | 3.8 | 5.075
203495474 | Ground Loop | GEOSTAR | 103J049**1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
203993050 | Ground Loop | GEOSTAR | 111H049**1*(1,2) |  | 47700 | 18.2 | 38000 | 3.8 | 3.975
203993052 | Ground Loop | GEOSTAR | 111H072**1*1 |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083
213087558 | Ground Loop | WaterFurnace | NDS049J1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
213087559 | Ground Loop | WaterFurnace | NDS049J1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
213087562 | Ground Loop | WaterFurnace | NDS064J1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
213087563 | Ground Loop | WaterFurnace | NDS064J1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
213154439 | Ground Loop | GeoSmart Energy | GTS026*1******K | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
213154440 | Ground Loop | GeoSmart Energy | GTS026*1******K | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
213154441 | Ground Loop | GeoSmart Energy | GTS049*1******K | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
213154442 | Ground Loop | GeoSmart Energy | GTS049*1******K | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
213154445 | Ground Loop | GeoSmart Energy | GTS064*1******K | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
216625816 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S4**2 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625817 | Ground Loop | GeoSmart Energy | S5A(V/H)036*S4**4 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
216625818 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D0**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625819 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D0**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625820 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D0**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625821 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D2**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625822 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D3**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625823 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D3**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625824 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D3**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625825 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D4**1 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625826 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D4**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625827 | Ground Loop | GeoSmart Energy | S5A(V/H)042*D4**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625828 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S0**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625829 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S0**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625830 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S0**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625831 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S2**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625832 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S3**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625833 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S3**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625834 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S3**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625835 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S4**1 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625836 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S4**2 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625837 | Ground Loop | GeoSmart Energy | S5A(V/H)042*S4**4 |  | 42000 | 21.2 | 32000 | 4.2 | 3.5
216625838 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D0**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
216625839 | Ground Loop | GeoSmart Energy | S5A(V/H)048*D0**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
3628407 | Ground Loop | WaterFurnace | USH023**0*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
3628408 | Ground Loop | WaterFurnace | USV/USH036**3*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
3628409 | Ground Loop | WaterFurnace | USV/USH036**0*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
3628410 | Ground Loop | WaterFurnace | USV/USH036**4*1 |  | 34500 | 17.3 | 26000 | 3.6 | 2.875
3628411 | Ground Loop | WaterFurnace | USH023**3*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
3628412 | Ground Loop | WaterFurnace | USH023**2*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
3628413 | Ground Loop | WaterFurnace | USH023**4*1 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
3628414 | Ground Loop | WaterFurnace | USV/USH018**0*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417
3628415 | Ground Loop | WaterFurnace | USV/USH018**2*1 |  | 18500 | 17.5 | 13700 | 3.7 | 1.5417
3628416 | Ground Loop | WaterFurnace | USV/USH015**0*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225
3628417 | Ground Loop | WaterFurnace | USV/USH015**2*1 |  | 14700 | 17.5 | 11500 | 3.7 | 1.225
207198443 | Ground Loop | BOSCH | QV036-2HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667
207198446 | Ground Loop | BOSCH | QV036-2VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625
207198447 | Ground Loop | BOSCH | QV036-2VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583
207198449 | Ground Loop | BOSCH | QV036-3HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667
207198452 | Ground Loop | BOSCH | QV036-3VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625
207198454 | Ground Loop | BOSCH | QV036-3VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583
207198455 | Ground Loop | BOSCH | QV036-4HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667
207198458 | Ground Loop | BOSCH | QV036-4VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625
207198460 | Ground Loop | BOSCH | QV036-4VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583
207198729 | Ground Loop | FHP | QV024-1HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083
207198730 | Ground Loop | FHP | QV024-1HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083
207198733 | Ground Loop | FHP | QV024-2HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083
207198734 | Ground Loop | FHP | QV024-2HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083
5220672 | Ground Loop | DAIKIN | WGSV/WGSH024B*J |  | 27500 | 19.9 | 17700 | 4.1 | 2.2917
5220673 | Ground Loop | DAIKIN | WGSV/WGSH024B*K |  | 27500 | 19.9 | 17700 | 4.1 | 2.2917
5220675 | Ground Loop | DAIKIN | WGSV/WGSH030B*E |  | 31300 | 20.1 | 21600 | 4.1 | 2.6083
5220676 | Ground Loop | DAIKIN | WGSV/WGSH030B*F |  | 31300 | 20.1 | 21600 | 4.1 | 2.6083
5220677 | Ground Loop | DAIKIN | WGSV/WGSH030B*J |  | 31300 | 20.1 | 21600 | 4.1 | 2.6083
5220678 | Ground Loop | DAIKIN | WGSV/WGSH030B*K |  | 31300 | 20.1 | 21600 | 4.1 | 2.6083
5220681 | Ground Loop | DAIKIN | WGSV/WGSH036B*E |  | 38500 | 22 | 26200 | 4.3 | 3.2083
5220682 | Ground Loop | DAIKIN | WGSV/WGSH036B*F |  | 38500 | 22 | 26200 | 4.3 | 3.2083
5220683 | Ground Loop | DAIKIN | WGSV/WGSH036B*J |  | 38500 | 22 | 26200 | 4.3 | 3.2083
5220684 | Ground Loop | DAIKIN | WGSV/WGSH036B*K |  | 38500 | 22 | 26200 | 4.3 | 3.2083
5220686 | Ground Loop | DAIKIN | WGSV/WGSH042B*E |  | 45500 | 20.2 | 31300 | 4 | 3.7917
5220687 | Ground Loop | DAIKIN | WGSV/WGSH042B*F |  | 45500 | 20.2 | 31300 | 4 | 3.7917
5220688 | Ground Loop | DAIKIN | WGSV/WGSH042B*K |  | 45500 | 20.2 | 31300 | 4 | 3.7917
5220690 | Ground Loop | DAIKIN | WGSV/WGSH048B*E |  | 52700 | 19.9 | 36900 | 4 | 4.3917
5220691 | Ground Loop | DAIKIN | WGSV/WGSH048B*F |  | 52700 | 19.9 | 36900 | 4 | 4.3917
5220693 | Ground Loop | DAIKIN | WGSV/WGSH048B*K |  | 52700 | 19.9 | 36900 | 4 | 4.3917
5220700 | Ground Loop | DAIKIN | WGSV/WGSH060B*E |  | 66300 | 20 | 46500 | 3.8 | 5.525
5220701 | Ground Loop | DAIKIN | WGSV/WGSH060B*F |  | 66300 | 20 | 46500 | 3.8 | 5.525
5220702 | Ground Loop | DAIKIN | WGSV/WGSH060B*K |  | 66300 | 20 | 46500 | 3.8 | 5.525
5220703 | Ground Loop | DAIKIN | WGSV/WGSH070B*E |  | 75700 | 18 | 55800 | 3.7 | 6.3083
5220704 | Ground Loop | DAIKIN | WGSV/WGSH070B*F |  | 75700 | 18 | 55800 | 3.7 | 6.3083
5220705 | Ground Loop | DAIKIN | WGSV/WGSH070B*K |  | 75700 | 18 | 55800 | 3.7 | 6.3083
5220707 | Ground Loop | DAIKIN | WGTV/WGTH026B*E |  | 27600 | 19.27 | 18100 | 4.1 | 2.3
5220708 | Ground Loop | DAIKIN | WGTV/WGTH026B*F |  | 27600 | 19.27 | 18100 | 4.1 | 2.3
5220709 | Ground Loop | DAIKIN | WGTV/WGTH026B*J |  | 27600 | 19.27 | 18100 | 4.1 | 2.3
206223145 | Ground Loop | ClimateMaster | TRT060D |  | 64500 | 17.9 | 46000 | 3.7 | 5.375
206223146 | Ground Loop | CENTURY | HZS024B | TAC026B***A* | 24000 | 17.4 | 18800 | 3.9 | 2
206223147 | Ground Loop | COMFORT-AIRE | HZS024B | TAC026B***A* | 24000 | 17.4 | 18800 | 3.9 | 2
206223148 | Ground Loop | CENTURY | HZS024B | TAC026B***B* | 26000 | 18 | 18600 | 3.8 | 2.1667
206223149 | Ground Loop | COMFORT-AIRE | HZS024B | TAC026B***B* | 26000 | 18 | 18600 | 3.8 | 2.1667
206223150 | Ground Loop | CENTURY | HZS036B | TAC038B | 38000 | 17.3 | 26600 | 3.7 | 3.1667
206223151 | Ground Loop | COMFORT-AIRE | HZS036B | TAC038B | 38000 | 17.3 | 26600 | 3.7 | 3.1667
206229666 | Ground Loop | BOSCH | EP024-1HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
206229667 | Ground Loop | BOSCH | EP024-2HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
206229668 | Ground Loop | BOSCH | EP024-3HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
206229669 | Ground Loop | BOSCH | EP024-4HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
206229674 | Ground Loop | FHP | EP024-1HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
206229675 | Ground Loop | FHP | EP024-2HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
206229676 | Ground Loop | FHP | EP024-3HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
206229677 | Ground Loop | FHP | EP024-4HZ/VTC-*****B |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
206229682 | Ground Loop | CARRIER | 50PSH/V024**C3/CA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
206229683 | Ground Loop | CARRIER | 50PSH/V024**C4/DA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
206229684 | Ground Loop | CARRIER | 50PSH/V024**C5/EA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
206229685 | Ground Loop | CARRIER | 50PSH/V024**C6/FA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
7415878 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
7416559 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
7416688 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
7416782 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
7416889 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**2*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
7416979 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
7417060 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
7417146 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
7417250 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
7417329 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
7417419 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH036**4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
7417586 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
7417698 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
7417776 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
7417867 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**2*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
7417918 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
7417992 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
7418047 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
7418154 | Ground Loop | YORK BY JOHNSON CONTROLS | YKTV/YKTH038**4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
7418360 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
7418435 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**0*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
7418635 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*1 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
7418715 | Ground Loop | YORK BY JOHNSON CONTROLS | YKSV/YKSH042**3*4 |  | 40700 | 21.7 | 28900 | 4 | 3.3917
207349404 | Ground Loop | WaterFurnace | NBV/NBH064**4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207349405 | Ground Loop | WaterFurnace | NBV/NBH064**3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207349406 | Ground Loop | WaterFurnace | NBV/NBH064**0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207349407 | Ground Loop | WaterFurnace | NBV/NBH072**0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207349408 | Ground Loop | WaterFurnace | NBV/NBH072**3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207349409 | Ground Loop | WaterFurnace | NBV/NBH072**4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207349410 | Ground Loop | WaterFurnace | NBV/NBH072**4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207349411 | Ground Loop | WaterFurnace | NBV/NBH072**0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207349412 | Ground Loop | WaterFurnace | NBV/NBH072**3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207657647 | Ground Loop | ClimateMaster | TSM15 D |  | 15500 | 18.8 | 11000 | 3.6 | 1.2917
207657653 | Ground Loop | ClimateMaster | TSM30 D |  | 29000 | 17.6 | 22200 | 3.6 | 2.4167
207657660 | Ground Loop | ClimateMaster | TSL15 A/C |  | 15400 | 17.7 | 11500 | 3.6 | 1.2833
207657661 | Ground Loop | ClimateMaster | TSL15 D |  | 15400 | 19.2 | 11000 | 3.7 | 1.2833
205767489 | Ground Loop | ClimateMaster | TSH/V/D018B |  | 19500 | 18.4 | 14500 | 3.6 | 1.625
205767490 | Ground Loop | ClimateMaster | TSH/V/D018B*K |  | 20200 | 19.4 | 14500 | 3.9 | 1.6833
214595688 | Ground Loop | AAON, Inc. | M2-007-2-H-GCAC-V0-10-000-A |  | 73700 | 17 | 52600 | 3.6 | 6.1417
214595689 | Ground Loop | AAON, Inc. | M2-007-2-H-GCBC-V0-10-000-A |  | 78000 | 17.8 | 51600 | 3.6 | 6.5
214595690 | Ground Loop | AAON, Inc. | M2-007-3-H-GCAC-V0-10-000-A |  | 73700 | 17 | 52600 | 3.6 | 6.1417
214595691 | Ground Loop | AAON, Inc. | M2-007-3-H-GCBC-V0-10-000-A |  | 78000 | 17.8 | 51600 | 3.6 | 6.5
214595692 | Ground Loop | AAON, Inc. | M2-007-4-H-GCAC-V0-10-000-A |  | 73700 | 17 | 52600 | 3.6 | 6.1417
214595693 | Ground Loop | AAON, Inc. | M2-007-4-H-GCBC-V0-10-000-A |  | 78000 | 17.8 | 51600 | 3.6 | 6.5
214606639 | Ground Loop | Dandelion Geo | DP1G072V3A1000S |  | 70000 | 17.5 | 61000 | 4.3 | 5.8333
214771921 | Ground Loop | TRANE | GEVK009A |  | 8800 | 19.6 | 6400 | 3.96 | 0.73333
214771923 | Ground Loop | TRANE | GEVK015A |  | 15900 | 18.2 | 12500 | 3.85 | 1.325
214771924 | Ground Loop | TRANE | GEVK018A |  | 18500 | 17.3 | 15300 | 3.76 | 1.5417
214771925 | Ground Loop | TRANE | GEVK024A |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167
214771926 | Ground Loop | TRANE | GEVK030A |  | 30000 | 18.2 | 23700 | 3.66 | 2.5
214771929 | Ground Loop | TRANE | GEVK048A |  | 50900 | 18.4 | 38900 | 3.6 | 4.2417
214771930 | Ground Loop | TRANE | GEVK060A |  | 60100 | 18.3 | 50200 | 3.65 | 5.0083
214771931 | Ground Loop | TRANE | EXVK009A |  | 9000 | 21.2 | 6100 | 3.91 | 0.75
214771932 | Ground Loop | TRANE | EXVK012A |  | 11900 | 19.8 | 8500 | 3.78 | 0.99167
214771933 | Ground Loop | TRANE | EXVK015A |  | 16200 | 18.7 | 11800 | 3.73 | 1.35
214771934 | Ground Loop | TRANE | EXVK018A |  | 19700 | 20.8 | 14400 | 3.93 | 1.6417
214771935 | Ground Loop | TRANE | EXVK024A |  | 26200 | 21.2 | 19400 | 3.8 | 2.1833
214771936 | Ground Loop | TRANE | EXVK030A |  | 31800 | 21.3 | 22900 | 4.17 | 2.65
217754758 | Ground Loop | DAIKIN | WSCH048F1*G/J*T |  | 49200 | 17.36 | 37500 | 3.6 | 4.1
217754759 | Ground Loop | DAIKIN | WSCH048K1*G/J*T |  | 49200 | 17.36 | 37500 | 3.6 | 4.1
217754762 | Ground Loop | DAIKIN | WSCH048F1*G/J*C |  | 49200 | 17.36 | 37500 | 3.6 | 4.1
217754763 | Ground Loop | DAIKIN | WSCH048K1*G/J*C |  | 49200 | 17.36 | 37500 | 3.6 | 4.1
9910683 | Ground Loop | TETCO | TZS042*4****B |  | 43400 | 19.8 | 32800 | 3.9 | 3.6167
9910696 | Ground Loop | GEOCOMFORT | GZS048*****1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2
9910697 | Ground Loop | HYDRON MODULE | HZS048*****1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2
9910698 | Ground Loop | TETCO | TZS048*****1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2
9910699 | Ground Loop | GEOCOMFORT | GZS048*2***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2
9910700 | Ground Loop | HYDRON MODULE | HZS048*2***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2
9910701 | Ground Loop | TETCO | TZS048*2***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2
9910702 | Ground Loop | GEOCOMFORT | GZS048*3***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2
9910703 | Ground Loop | HYDRON MODULE | HZS048*3***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2
9910704 | Ground Loop | TETCO | TZS048*3***1B |  | 50400 | 19.1 | 37800 | 3.8 | 4.2
9910708 | Ground Loop | GEOCOMFORT | GZS048******B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417
9910709 | Ground Loop | HYDRON MODULE | HZS048******B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417
9910710 | Ground Loop | TETCO | TZS048******B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417
9910711 | Ground Loop | GEOCOMFORT | GZS048*2****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417
9910712 | Ground Loop | HYDRON MODULE | HZS048*2****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417
9910713 | Ground Loop | TETCO | TZS048*2****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417
9910714 | Ground Loop | GEOCOMFORT | GZS048*3****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417
9910715 | Ground Loop | HYDRON MODULE | HZS048*3****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417
9910716 | Ground Loop | TETCO | TZS048*3****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417
9910717 | Ground Loop | GEOCOMFORT | GZS048*4****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417
9910718 | Ground Loop | HYDRON MODULE | HZS048*4****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417
9910719 | Ground Loop | TETCO | TZS048*4****B |  | 48500 | 17.8 | 38500 | 3.6 | 4.0417
9910752 | Ground Loop | GEOCOMFORT | GZS060*****1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583
9910753 | Ground Loop | HYDRON MODULE | HZS060*****1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583
9910754 | Ground Loop | TETCO | TZS060*****1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583
9910755 | Ground Loop | GEOCOMFORT | GZS060*2***1B |  | 60700 | 19.5 | 48200 | 4 | 5.0583
216625507 | Ground Loop | GEOSTAR | G5A(V/H)042*D4**2 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625508 | Ground Loop | GEOSTAR | G5A(V/H)042*D4**4 |  | 41700 | 19.2 | 33700 | 4.4 | 3.475
216625509 | Ground Loop | GEOSTAR | G5A(V/H)048*S3**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625510 | Ground Loop | GEOSTAR | G5A(V/H)048*S4**1 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625511 | Ground Loop | GEOSTAR | G5A(V/H)048*S0**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625512 | Ground Loop | GEOSTAR | G5A(V/H)048*S2**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625513 | Ground Loop | GEOSTAR | G5A(V/H)048*S3**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625514 | Ground Loop | GEOSTAR | G5A(V/H)048*S4**2 |  | 51000 | 19 | 38500 | 4.2 | 4.25
216625515 | Ground Loop | GEOSTAR | G5A(V/H)048*S0**4 |  | 51000 | 19 | 38500 | 4.2 | 4.25
202326797 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ038J1 | SAH036* | 36000 | 19 | 27900 | 4 | 3
202326829 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS038J1 | SAH036* | 36000 | 19 | 27900 | 4 | 3
202328436 | Ground Loop | BOSCH | BP018-1VT*******C |  | 20500 | 18.5 | 14800 | 3.7 | 1.7083
215268789 | Ground Loop | WaterFurnace | V5A(V/H)048*D4**1 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
215268790 | Ground Loop | WaterFurnace | V5A(V/H)048*D2**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
215268791 | Ground Loop | WaterFurnace | V5A(V/H)048*D4**2 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
215268792 | Ground Loop | WaterFurnace | V5A(V/H)048*D4**4 |  | 50500 | 18.9 | 40100 | 4.4 | 4.2083
215268793 | Ground Loop | WaterFurnace | V5A(V/H)060*D4**1 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
215268794 | Ground Loop | WaterFurnace | V5A(V/H)060*D4**4 |  | 66000 | 19.3 | 47600 | 4.1 | 5.5
215268795 | Ground Loop | WaterFurnace | V5A(V/H)072*D4**1 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
215268796 | Ground Loop | WaterFurnace | V5A(V/H)072*D4**4 |  | 73400 | 18.3 | 57900 | 4 | 6.1167
215285739 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)024A |  | 26300 | 19.9 | 17800 | 4.1 | 2.1917
215285740 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)036A |  | 39200 | 18.6 | 28400 | 4.2 | 3.2667
215285741 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)048A |  | 51700 | 19.4 | 38200 | 4 | 4.3083
215285742 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)060A |  | 62600 | 18.7 | 44300 | 3.9 | 5.2167
215285743 | Ground Loop | ClimateMaster | SE(L/R/B/P/D/N/T/K)072A |  | 74700 | 18.4 | 54000 | 3.8 | 6.225
217351788 | Ground Loop | ARCOAIRE | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25
217351789 | Ground Loop | ARCOAIRE | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667
217351790 | Ground Loop | ARCOAIRE | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417
217351792 | Ground Loop | ARCOAIRE | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417
217351793 | Ground Loop | ARCOAIRE | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583
217351795 | Ground Loop | ARCOAIRE | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583
217351796 | Ground Loop | ARCOAIRE | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167
217351797 | Ground Loop | ARCOAIRE | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167
217351798 | Ground Loop | ARCOAIRE | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05
211594253 | Ground Loop | TRANE | EXHG0364 |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917
211594254 | Ground Loop | TRANE | EXHG0367 |  | 37100 | 20.4 | 27200 | 4.1 | 3.0917
211594255 | Ground Loop | TRANE | EXHG042B |  | 40500 | 21.1 | 29400 | 4.3 | 3.375
211594256 | Ground Loop | TRANE | EXHG0424 |  | 40500 | 21.1 | 29400 | 4.3 | 3.375
211594257 | Ground Loop | TRANE | EXHG048B |  | 47100 | 20.3 | 34600 | 4.3 | 3.925
211594258 | Ground Loop | TRANE | EXHG0484 |  | 47100 | 20.3 | 34600 | 4.3 | 3.925
211594259 | Ground Loop | TRANE | EXHG060B |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083
211594260 | Ground Loop | TRANE | EXHG0604 |  | 57700 | 20.1 | 42900 | 4.1 | 4.8083
211594261 | Ground Loop | TRANE | EXHG070B |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083
211594262 | Ground Loop | TRANE | EXHG0704 |  | 66100 | 19.8 | 52000 | 4.1 | 5.5083
211594263 | Ground Loop | TRANE | DXHG024B |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583
211594264 | Ground Loop | TRANE | DXHG0244 |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583
211594265 | Ground Loop | TRANE | DXHG0247 |  | 25900 | 19.2 | 19400 | 3.9 | 2.1583
211594266 | Ground Loop | TRANE | DXHG036B |  | 34500 | 19.7 | 25500 | 4.1 | 2.875
211594267 | Ground Loop | TRANE | DXHG0364 |  | 34500 | 19.7 | 25500 | 4.1 | 2.875
211594268 | Ground Loop | TRANE | DXHG0367 |  | 34500 | 19.7 | 25500 | 4.1 | 2.875
211594269 | Ground Loop | TRANE | DXHG048B |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833
211594270 | Ground Loop | TRANE | DXHG0484 |  | 46600 | 20.6 | 34500 | 4.3 | 3.8833
211594271 | Ground Loop | TRANE | DXHG060B |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917
211594272 | Ground Loop | TRANE | DXHG0604 |  | 53900 | 19.9 | 39800 | 4.2 | 4.4917
211594273 | Ground Loop | TRANE | DXHG070B |  | 66800 | 19.6 | 52900 | 4 | 5.5667
211594274 | Ground Loop | TRANE | DXHG0704 |  | 66800 | 19.6 | 52900 | 4 | 5.5667
212428693 | Ground Loop | HYDROTECH | WSH6009A6* |  | 9500 | 18.9 | 6800 | 3.6 | 0.79167
212428694 | Ground Loop | HYDROTECH | WSH6012A6* |  | 12000 | 18.2 | 8500 | 3.8 | 1
212428695 | Ground Loop | HYDROTECH | WSH6018A6* |  | 19000 | 19 | 12000 | 3.6 | 1.5833
212428696 | Ground Loop | HYDROTECH | WSH6024A6* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083
212428697 | Ground Loop | HYDROTECH | WSH6030A6* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5
212428698 | Ground Loop | HYDROTECH | WSH6036A6* |  | 36500 | 18 | 27000 | 3.6 | 3.0417
212428699 | Ground Loop | HYDROTECH | WSH6042A6* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833
212428700 | Ground Loop | HYDROTECH | WSH6048A6* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125
212428701 | Ground Loop | AE Air | WSH6009A6* |  | 9500 | 18.9 | 6800 | 3.6 | 0.79167
212428702 | Ground Loop | AE Air | WSH6012A6* |  | 12000 | 18.2 | 8500 | 3.8 | 1
212428703 | Ground Loop | AE Air | WSH6018A6* |  | 19000 | 19 | 12000 | 3.6 | 1.5833
212428704 | Ground Loop | AE Air | WSH6024A6* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083
212428705 | Ground Loop | AE Air | WSH6030A6* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5
212428706 | Ground Loop | AE Air | WSH6036A6* |  | 36500 | 18 | 27000 | 3.6 | 3.0417
212428707 | Ground Loop | AE Air | WSH6042A6* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833
212428708 | Ground Loop | AE Air | WSH6048A6* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125
212505502 | Ground Loop | HYDROTECH | WSH6060A6* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083
212505503 | Ground Loop | HYDROTECH | WSH6072A6* |  | 72000 | 17.1 | 55000 | 3.6 | 6
212505504 | Ground Loop | AE Air | WSH6030AM* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5
212505505 | Ground Loop | AE Air | WSH6060A6* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083
212505506 | Ground Loop | AE Air | WSH6072A6* |  | 72000 | 17.1 | 55000 | 3.6 | 6
212505507 | Ground Loop | HYDROTECH | WSH6024AM* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083
212505508 | Ground Loop | HYDROTECH | WSH6030AM* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5
216625879 | Ground Loop | GeoSmart Energy | S5A(V/H)072*S3**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216625880 | Ground Loop | GeoSmart Energy | S5A(V/H)072*S4**1 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216625881 | Ground Loop | GeoSmart Energy | S5A(V/H)072*S4**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
216687113 | Ground Loop | WaterFurnace | W5SS024BD1 | W5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833
216687114 | Ground Loop | WaterFurnace | W5SS036BD1 | W5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833
216687115 | Ground Loop | WaterFurnace | W5SS048BD1 | W5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925
216687116 | Ground Loop | WaterFurnace | W5SS060BD1 | W5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917
216687118 | Ground Loop | WaterFurnace | W5SZ024BD1 | W5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833
216687119 | Ground Loop | WaterFurnace | W5SZ036BD1 | W5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833
216687120 | Ground Loop | WaterFurnace | W5SZ048BD1 | W5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925
216687121 | Ground Loop | WaterFurnace | W5SZ060BD1 | W5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917
216687731 | Ground Loop | GEOSTAR | G5SS024BD1 | G5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833
216687732 | Ground Loop | GEOSTAR | G5SS036BD1 | G5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833
216687733 | Ground Loop | GEOSTAR | G5SS048BD1 | G5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925
216687734 | Ground Loop | GEOSTAR | G5SS060BD1 | G5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917
216687736 | Ground Loop | GEOSTAR | G5SZ024BD1 | G5BM024BN1**2 | 23800 | 18.4 | 18800 | 3.9 | 1.9833
216687737 | Ground Loop | GEOSTAR | G5SZ036BD1 | G5BM036BN1**2 | 37000 | 19.8 | 28400 | 4.2 | 3.0833
216687738 | Ground Loop | GEOSTAR | G5SZ048BD1 | G5BM048BN1**2 | 47100 | 18.2 | 37900 | 4.2 | 3.925
216687739 | Ground Loop | GEOSTAR | G5SZ060BD1 | G5BM060BN1**2 | 59900 | 18.2 | 46700 | 3.9 | 4.9917
207198737 | Ground Loop | FHP | QV024-3HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083
207198738 | Ground Loop | FHP | QV024-3HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083
207198741 | Ground Loop | FHP | QV024-4HZC-***D*A-**T/G |  | 25300 | 17.65 | 17850 | 3.7 | 2.1083
207198742 | Ground Loop | FHP | QV024-4HZN-***D*A-**T/G |  | 25300 | 17.55 | 17550 | 3.7 | 2.1083
207198745 | Ground Loop | FHP | QV030-1HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958
207198746 | Ground Loop | FHP | QV030-1HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708
207198747 | Ground Loop | FHP | QV030-1VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958
207198748 | Ground Loop | FHP | QV030-1VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708
207198749 | Ground Loop | FHP | QV030-2HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958
207198750 | Ground Loop | FHP | QV030-2HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708
207198751 | Ground Loop | FHP | QV030-2VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958
207198752 | Ground Loop | FHP | QV030-2VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708
207198753 | Ground Loop | FHP | QV030-3HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958
207198754 | Ground Loop | FHP | QV030-3HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708
207198755 | Ground Loop | FHP | QV030-3VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958
207198756 | Ground Loop | FHP | QV030-3VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708
207198757 | Ground Loop | FHP | QV030-4HZC-***D*A-**T/G |  | 29950 | 17.1 | 21050 | 3.6 | 2.4958
207198758 | Ground Loop | FHP | QV030-4HZN-***D*A-**T/G |  | 29650 | 17.15 | 20650 | 3.6 | 2.4708
207198759 | Ground Loop | FHP | QV030-4VTC-***D*A-**T/G |  | 29950 | 17 | 21050 | 3.6 | 2.4958
207198760 | Ground Loop | FHP | QV030-4VTN-***D*A-**T/G |  | 29650 | 17.05 | 20650 | 3.6 | 2.4708
207198761 | Ground Loop | FHP | QV036-1HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667
207198763 | Ground Loop | FHP | QV036-1VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625
207198764 | Ground Loop | FHP | QV036-1VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583
207198765 | Ground Loop | FHP | QV036-2HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667
207198767 | Ground Loop | FHP | QV036-2VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625
207198768 | Ground Loop | FHP | QV036-2VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583
207198769 | Ground Loop | FHP | QV036-3HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667
207198771 | Ground Loop | FHP | QV036-3VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625
207198772 | Ground Loop | FHP | QV036-3VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583
207198773 | Ground Loop | FHP | QV036-4HZC-***D*A-**T/G |  | 38000 | 17.4 | 26750 | 3.65 | 3.1667
207198775 | Ground Loop | FHP | QV036-4VTC-***D*A-**T/G |  | 37950 | 17.55 | 26700 | 3.7 | 3.1625
207198776 | Ground Loop | FHP | QV036-4VTN-***D*A-**T/G |  | 37900 | 17.3 | 26400 | 3.6 | 3.1583
7167375 | Ground Loop | BRYANT | GB024H/V******1*X1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
7167376 | Ground Loop | CARRIER | GB024H/V******1**1 |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
7167377 | Ground Loop | BRYANT | GB030H/V******1*X1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
7167378 | Ground Loop | CARRIER | GB030H/V******1**1 |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
7167538 | Ground Loop | CARRIER | 50PTD/H/V024***3/CA |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167
7167539 | Ground Loop | CARRIER | 50PTD/H/V024***5/EA |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167
7167540 | Ground Loop | CARRIER | 50PTD/H/V024***4/DA |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167
7167541 | Ground Loop | CARRIER | 50PTD/H/V024***6/FA |  | 26600 | 19.9 | 18000 | 3.78 | 2.2167
7167542 | Ground Loop | CARRIER | 50PTD/H/V036***3/CA |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
7167543 | Ground Loop | CARRIER | 50PTD/H/V036***5/EA |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
7167544 | Ground Loop | CARRIER | 50PTD/H/V036***4/DA |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
7167545 | Ground Loop | CARRIER | 50PTD/H/V036***6/FA |  | 39900 | 20.2 | 28400 | 3.95 | 3.325
7167546 | Ground Loop | CARRIER | 50PTD/H/V048***3/CA |  | 51300 | 18 | 36900 | 3.9 | 4.275
7167547 | Ground Loop | CARRIER | 50PTD/H/V048***5/EA |  | 51300 | 18 | 36900 | 3.9 | 4.275
7167548 | Ground Loop | CARRIER | 50PTD/H/V048***6/FA |  | 51300 | 18 | 36900 | 3.9 | 4.275
7167549 | Ground Loop | CARRIER | 50PTD/H/V060***3/CA |  | 65100 | 17.65 | 45500 | 3.7 | 5.425
7167550 | Ground Loop | CARRIER | 50PTD/H/V060***5/EA |  | 65100 | 17.65 | 45500 | 3.7 | 5.425
217642928 | Ground Loop | GeoSmart Energy | S3A(V/H)060*S0**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
217642929 | Ground Loop | GeoSmart Energy | S3A(V/H)060*S3**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
217642930 | Ground Loop | GeoSmart Energy | S3A(V/H)060*S3**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
217642931 | Ground Loop | GeoSmart Energy | S3A(V/H)060*S4**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
217642932 | Ground Loop | GeoSmart Energy | S3A(V/H)060*S4**4 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
217642943 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S0**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
217642945 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S0**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642946 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S0**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
217642948 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)060*S0**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
217642959 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S0**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
217642960 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S2**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
217642961 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S2**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
217642962 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S3**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
217642963 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S3**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
217642964 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S4**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
217642965 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)024*S4**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
217642973 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S0**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642974 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S2**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642975 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S2**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642976 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S3**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642977 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S3**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642978 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S4**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642979 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)036*S4**4 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642980 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S0**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
217642981 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S3**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
217642982 | Ground Loop | YORK BY JOHNSON CONTROLS | Y3A(V/H)042*S3**4 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
207177441 | Ground Loop | TRANE | GEVG0244 |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667
207177442 | Ground Loop | TRANE | GEVG0247 |  | 24800 | 18.5 | 19600 | 3.8 | 2.0667
207177443 | Ground Loop | TRANE | GEVG030A |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167
207177444 | Ground Loop | TRANE | GEVG030B |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167
207177445 | Ground Loop | TRANE | GEVG0304 |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167
207177446 | Ground Loop | TRANE | GEVG0307 |  | 30200 | 17.7 | 23300 | 3.7 | 2.5167
207177447 | Ground Loop | TRANE | GEVG036A |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083
207177448 | Ground Loop | TRANE | GEVG036B |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083
207177449 | Ground Loop | TRANE | GEVG0364 |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083
207177450 | Ground Loop | TRANE | GEVG0367 |  | 37300 | 17.6 | 28700 | 3.6 | 3.1083
207177460 | Ground Loop | TRANE | EXVG009A |  | 8300 | 18.8 | 6100 | 3.7 | 0.69167
207177461 | Ground Loop | TRANE | EXVG0097 |  | 8300 | 18.8 | 6100 | 3.7 | 0.69167
207177462 | Ground Loop | TRANE | EXVG012A |  | 12300 | 19.5 | 9300 | 4 | 1.025
215224683 | Ground Loop | BOSCH | RF012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224684 | Ground Loop | BOSCH | RF012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224685 | Ground Loop | BOSCH | RF015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083
215224686 | Ground Loop | BOSCH | RF015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917
215224687 | Ground Loop | BOSCH | RF018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224688 | Ground Loop | BOSCH | RF018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224691 | Ground Loop | BOSCH | RF024-1VT/HZC-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224692 | Ground Loop | BOSCH | RF024-1VT/HZN-*****A |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224782 | Ground Loop | CARRIER | GBA18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224783 | Ground Loop | BRYANT | GBA18V/H**C******1 |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224784 | Ground Loop | CARRIER | GBA18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224785 | Ground Loop | BRYANT | GBA18V/H**N******1 |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224786 | Ground Loop | CARRIER | GBA24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224787 | Ground Loop | BRYANT | GBA24V/H**C******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224788 | Ground Loop | CARRIER | GBA24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224789 | Ground Loop | BRYANT | GBA24V/H**N******1 |  | 25000 | 17 | 18000 | 3.7 | 2.0833
205767559 | Ground Loop | ClimateMaster | TZV/H060C |  | 63200 | 17.3 | 43700 | 3.6 | 5.2667
215893693 | Ground Loop | DUAL AIR | CFF024 |  | 25000 | 17.1 | 16000 | 3.6 | 2.0833
215893695 | Ground Loop | DUAL AIR | CFF031 |  | 31200 | 17.1 | 19500 | 3.6 | 2.6
215893697 | Ground Loop | DUAL AIR | CFF036 |  | 35500 | 17.1 | 25500 | 3.6 | 2.9583
215893699 | Ground Loop | DUAL AIR | CFF041 |  | 40500 | 17.1 | 26000 | 3.6 | 3.375
215893703 | Ground Loop | MIAMI HEAT PUMP | HPF024 |  | 25000 | 17.1 | 16000 | 3.6 | 2.0833
215893704 | Ground Loop | MIAMI HEAT PUMP | HPF031 |  | 31200 | 17.1 | 19500 | 3.6 | 2.6
215893706 | Ground Loop | MIAMI HEAT PUMP | HPF036 |  | 35500 | 17.1 | 25500 | 3.6 | 2.9583
215893707 | Ground Loop | MIAMI HEAT PUMP | HPF041 |  | 40500 | 17.1 | 26000 | 3.6 | 3.375
215893711 | Ground Loop | DUAL AIR | CFF049 |  | 49000 | 17.1 | 31000 | 3.6 | 4.0833
215893713 | Ground Loop | MIAMI HEAT PUMP | HPF049 |  | 49000 | 17.1 | 31000 | 3.6 | 4.0833
216014181 | Ground Loop | RHEEM | RPVV/H/D036D |  | 39000 | 20.3 | 29700 | 4.4 | 3.25
216054107 | Ground Loop | WaterFurnace | W5TV036BD1**2 |  | 38000 | 20.1 | 29300 | 4.3 | 3.1667
216054108 | Ground Loop | WaterFurnace | W5TV048BD1**2 |  | 49100 | 18.5 | 38400 | 4.1 | 4.0917
216054109 | Ground Loop | WaterFurnace | W5TV060BD1**2 |  | 63700 | 17.9 | 47300 | 4 | 5.3083
216054110 | Ground Loop | WaterFurnace | W5TV072BD1**2 |  | 71500 | 17.8 | 56100 | 3.9 | 5.9583
216054475 | Ground Loop | GEOCOMFORT | GBS018* | EAD018 | 21800 | 21.1 | 14400 | 3.9 | 1.8167
216054476 | Ground Loop | GEOCOMFORT | GBT024* | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917
216054477 | Ground Loop | GEOCOMFORT | GBT036* | EAD036 | 36900 | 19.2 | 27800 | 3.8 | 3.075
216054478 | Ground Loop | GEOCOMFORT | GBT048* | EAD048 | 47800 | 17.3 | 41000 | 3.6 | 3.9833
216054479 | Ground Loop | GEOCOMFORT | GVS009* |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833
216054480 | Ground Loop | GEOCOMFORT | GVS012* |  | 11900 | 18.1 | 9400 | 3.6 | 0.99167
216054481 | Ground Loop | GEOCOMFORT | GVS018* |  | 21700 | 22.2 | 15400 | 4 | 1.8083
216054482 | Ground Loop | GEOCOMFORT | GVT024* |  | 25800 | 18.6 | 19400 | 4 | 2.15
216054483 | Ground Loop | GEOCOMFORT | GVT030* |  | 32200 | 18.4 | 24300 | 3.8 | 2.6833
216054484 | Ground Loop | GEOCOMFORT | GVT036* |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167
216054485 | Ground Loop | GEOCOMFORT | GVT042* |  | 45900 | 18.5 | 32400 | 3.9 | 3.825
216054486 | Ground Loop | GEOCOMFORT | GVT048* |  | 50300 | 18.8 | 38500 | 4 | 4.1917
216054487 | Ground Loop | GEOCOMFORT | GYT024* |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583
216054488 | Ground Loop | GEOCOMFORT | GYT036* |  | 39700 | 21 | 27900 | 4.3 | 3.3083
216054489 | Ground Loop | GEOCOMFORT | GYT048* |  | 51900 | 19.2 | 36700 | 4.1 | 4.325
216054492 | Ground Loop | GEOCOMFORT | GZT024* |  | 26400 | 18.3 | 18300 | 3.9 | 2.2
216054493 | Ground Loop | GEOCOMFORT | GZT030* |  | 31500 | 17.5 | 23300 | 3.7 | 2.625
216054494 | Ground Loop | GEOCOMFORT | GZT036* |  | 36700 | 17.9 | 27100 | 3.8 | 3.0583
216054495 | Ground Loop | GEOCOMFORT | GZT042* |  | 43000 | 18 | 32900 | 3.6 | 3.5833
216054496 | Ground Loop | GEOCOMFORT | GZT048* |  | 48700 | 17.3 | 36900 | 3.6 | 4.0583
216054499 | Ground Loop | GEOCOMFORT | GVS015* |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333
216057509 | Ground Loop | GEOCOMFORT | GBT060* | EAD060 | 61100 | 17.6 | 46800 | 3.8 | 5.0917
216057511 | Ground Loop | GEOCOMFORT | GVT060* |  | 60900 | 17.6 | 46300 | 3.8 | 5.075
216057512 | Ground Loop | GEOCOMFORT | GYT060* |  | 63100 | 18.7 | 49100 | 4 | 5.2583
216057513 | Ground Loop | GEOCOMFORT | GZS015* |  | 14200 | 17.6 | 11200 | 3.9 | 1.1833
216057515 | Ground Loop | GEOCOMFORT | GZS018* |  | 20100 | 18.7 | 14100 | 3.7 | 1.675
201926738 | Ground Loop | WaterFurnace | URS070*4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
201926741 | Ground Loop | WaterFurnace | URS070*4*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
201926779 | Ground Loop | WaterFurnace | URD064*4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
201926783 | Ground Loop | WaterFurnace | URD064*4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
201926787 | Ground Loop | WaterFurnace | URD064*4*5 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
201926799 | Ground Loop | WaterFurnace | URD072*4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
201926802 | Ground Loop | WaterFurnace | URD072*4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
201926804 | Ground Loop | WaterFurnace | URD072*4*5 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
201926809 | Ground Loop | WaterFurnace | URT096*4*5 |  | 91800 | 18.8 | 72800 | 4 | 7.65
201930362 | Ground Loop | GEOCOMFORT | GZT024 |  | 26400 | 18.3 | 18300 | 3.9 | 2.2
217967018 | Ground Loop | TRANE | VSHK024A |  | 25400 | 22.4 | 19200 | 4.4 | 2.1167
217967019 | Ground Loop | TRANE | VSVK024A |  | 26300 | 24.7 | 18800 | 4.6 | 2.1917
217967020 | Ground Loop | TRANE | VSHK033A |  | 33300 | 18.1 | 27700 | 4.1 | 2.775
217967021 | Ground Loop | TRANE | VSVK033A |  | 35300 | 20.3 | 25500 | 4.3 | 2.9417
217967022 | Ground Loop | TRANE | VSHK042A |  | 42200 | 21.3 | 32500 | 4.4 | 3.5167
217967023 | Ground Loop | TRANE | VSVK042A |  | 44900 | 22.7 | 34400 | 4.4 | 3.7417
200083804 | Ground Loop | NORTHERN HEAT PUMP | RA-VE-061-* |  | 61800 | 17.1 | 50700 | 3.6 | 5.15
200083805 | Ground Loop | NORTHSTAR SERIES | RA-VE-061-* |  | 61800 | 17.1 | 50700 | 3.6 | 5.15
201756620 | Ground Loop | NORTHERN HEAT PUMP | RA-VE-041-* |  | 38100 | 17.47 | 32700 | 3.66 | 3.175
201756621 | Ground Loop | NORTHSTAR SERIES | RA-VE-041-* |  | 38100 | 17.47 | 32700 | 3.66 | 3.175
201756622 | Ground Loop | NORTHERN HEAT PUMP | RA-VE-053-* |  | 52600 | 17.1 | 45200 | 3.6 | 4.3833
201756623 | Ground Loop | NORTHSTAR SERIES | RA-VE-053-* |  | 52600 | 17.1 | 45200 | 3.6 | 4.3833
6501891 | Ground Loop | GEOSTAR | GBV/GBH015**2*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25
6501892 | Ground Loop | GEOSTAR | GBV/GBH015**2*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25
6501894 | Ground Loop | GEOSTAR | GBV/GBH018**0*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
6501895 | Ground Loop | GEOSTAR | GBV/GBH018**0*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
6501897 | Ground Loop | GEOSTAR | GBV/GBH018**2*1 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
6501898 | Ground Loop | GEOSTAR | GBV/GBH018**2*4 |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
6501899 | Ground Loop | GEOSTAR | GBV/GBH024**0*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
6501900 | Ground Loop | GEOSTAR | GBV/GBH024**0*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
6501901 | Ground Loop | GEOSTAR | GBV/GBH024**0*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
6501902 | Ground Loop | GEOSTAR | GBV/GBH024**2*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
6501903 | Ground Loop | GEOSTAR | GBV/GBH024**2*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
6501904 | Ground Loop | GEOSTAR | GBV/GBH024**2*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
6501905 | Ground Loop | GEOSTAR | GBV/GBH024**3*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
6501906 | Ground Loop | GEOSTAR | GBV/GBH024**3*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
6501907 | Ground Loop | GEOSTAR | GBV/GBH024**3*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
6501908 | Ground Loop | GEOSTAR | GBV/GBH024**4*0 |  | 26000 | 19.2 | 18900 | 3.7 | 2.1667
6501909 | Ground Loop | GEOSTAR | GBV/GBH024**4*1 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
6501910 | Ground Loop | GEOSTAR | GBV/GBH024**4*4 |  | 26000 | 19.6 | 19000 | 3.8 | 2.1667
6501911 | Ground Loop | GEOSTAR | GBV/GBH026**0*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
6501912 | Ground Loop | GEOSTAR | GBV/GBH026**0*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
6501913 | Ground Loop | GEOSTAR | GBV/GBH026**2*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
6501914 | Ground Loop | GEOSTAR | GBV/GBH026**2*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
6501915 | Ground Loop | GEOSTAR | GBV/GBH026**3*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
6501916 | Ground Loop | GEOSTAR | GBV/GBH026**3*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
6501917 | Ground Loop | GEOSTAR | GBV/GBH026**4*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
6501918 | Ground Loop | GEOSTAR | GBV/GBH030**0*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
6501919 | Ground Loop | GEOSTAR | GBV/GBH030**0*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
6501920 | Ground Loop | GEOSTAR | GBV/GBH030**0*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
6501921 | Ground Loop | GEOSTAR | GBV/GBH030**2*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
6501922 | Ground Loop | GEOSTAR | GBV/GBH030**2*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
6501923 | Ground Loop | GEOSTAR | GBV/GBH030**2*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
6501924 | Ground Loop | GEOSTAR | GBV/GBH030**3*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
6501925 | Ground Loop | GEOSTAR | GBV/GBH030**3*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
6501926 | Ground Loop | GEOSTAR | GBV/GBH030**3*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
6501927 | Ground Loop | GEOSTAR | GBV/GBH030**4*0 |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
6501928 | Ground Loop | GEOSTAR | GBV/GBH030**4*1 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
6501929 | Ground Loop | GEOSTAR | GBV/GBH030**4*4 |  | 28100 | 22 | 20500 | 3.9 | 2.3417
6501930 | Ground Loop | GEOSTAR | GBV/GBH036**0*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
6501931 | Ground Loop | GEOSTAR | GBV/GBH036**0*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
6501932 | Ground Loop | GEOSTAR | GBV/GBH036**0*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
6501933 | Ground Loop | GEOSTAR | GBV/GBH036**2*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
6501934 | Ground Loop | GEOSTAR | GBV/GBH036**2*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
6501935 | Ground Loop | GEOSTAR | GBV/GBH036**2*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
6501936 | Ground Loop | GEOSTAR | GBV/GBH036**3*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
6501937 | Ground Loop | GEOSTAR | GBV/GBH036**3*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
6501938 | Ground Loop | GEOSTAR | GBV/GBH036**3*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
6501939 | Ground Loop | GEOSTAR | GBV/GBH036**4*0 |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
6501940 | Ground Loop | GEOSTAR | GBV/GBH036**4*1 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
6501941 | Ground Loop | GEOSTAR | GBV/GBH036**4*4 |  | 33700 | 22 | 24400 | 4.2 | 2.8083
6501942 | Ground Loop | GEOSTAR | GBV/GBH038**0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
6501943 | Ground Loop | GEOSTAR | GBV/GBH038**0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
6501944 | Ground Loop | GEOSTAR | GBV/GBH038**2*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
6501945 | Ground Loop | GEOSTAR | GBV/GBH038**2*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
6501946 | Ground Loop | GEOSTAR | GBV/GBH038**3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
206726849 | Ground Loop | HYDRON MODULE | HBT060 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833
206726850 | Ground Loop | TETCO | TBT060 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833
206726851 | Ground Loop | GEOCOMFORT | GBT060*2 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833
206726852 | Ground Loop | HYDRON MODULE | HBT060*2 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833
206726853 | Ground Loop | TETCO | TBT060*2 | EED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833
206726854 | Ground Loop | GEOCOMFORT | GBT024 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333
206726855 | Ground Loop | GEOCOMFORT | GBT024 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917
206726856 | Ground Loop | HYDRON MODULE | HBT024 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333
206726857 | Ground Loop | HYDRON MODULE | HBT024 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917
206726858 | Ground Loop | TETCO | TBT024 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333
206726859 | Ground Loop | TETCO | TBT024 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917
206726860 | Ground Loop | GEOCOMFORT | GBT024*2 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333
206726861 | Ground Loop | GEOCOMFORT | GBT024*2 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917
206726862 | Ground Loop | HYDRON MODULE | HBT024*2 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333
206726863 | Ground Loop | HYDRON MODULE | HBT024*2 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917
206726864 | Ground Loop | TETCO | TBT024*2 | EED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333
206726865 | Ground Loop | TETCO | TBT024*2 | EAD024 | 26300 | 19.5 | 18800 | 3.9 | 2.1917
214841676 | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667
214841678 | Ground Loop | ClimateMaster | SC(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167
214841679 | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333
214841680 | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15
214841682 | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417
214841684 | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333
214841698 | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)015A*V |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667
214841700 | Ground Loop | ClimateMaster | SR(L/R/B/P/T/K/F)018A*V |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167
214841701 | Ground Loop | ClimateMaster | SZ(L/R/B/P/T/K)024A |  | 25000 | 18 | 18400 | 3.9 | 2.0833
214841705 | Ground Loop | ClimateMaster | SZ(L/R/B/P/T/K)048A |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833
214841706 | Ground Loop | ClimateMaster | SZ(L/R/B/P/T/K)060A |  | 61500 | 17.8 | 44600 | 3.7 | 5.125
214841707 | Ground Loop | ClimateMaster | SY(L/R/B/P/T/K)024A |  | 25000 | 18 | 18400 | 3.9 | 2.0833
214841711 | Ground Loop | ClimateMaster | SY(L/R/B/P/T/K)048A |  | 49000 | 17.7 | 36000 | 3.7 | 4.0833
214841712 | Ground Loop | ClimateMaster | SY(L/R/B/P/T/K)060A |  | 61500 | 17.8 | 44600 | 3.7 | 5.125
214844588 | Ground Loop | WaterFurnace | W7A(V/H)024BV1**2 |  | 24100 | 23.6 | 24800 | 4.1 | 2.0083
214844645 | Ground Loop | WaterFurnace | W7A(V/H)036BV1**2 |  | 35800 | 18.1 | 32900 | 3.8 | 2.9833
214844646 | Ground Loop | WaterFurnace | W7A(V/H)048BV1**2 |  | 45000 | 18.9 | 42000 | 3.6 | 3.75
207348679 | Ground Loop | WaterFurnace | URS070*4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
207348680 | Ground Loop | WaterFurnace | URS070*4*5 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
207348681 | Ground Loop | WaterFurnace | URS060*0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
215399850 | Ground Loop | DAIKIN | WSMV060K3*G/J*C |  | 63500 | 17.62 | 46100 | 3.66 | 5.2917
215399858 | Ground Loop | DAIKIN | WSSV015A1*H*T |  | 17000 | 23.75 | 10400 | 3.77 | 1.4167
215399859 | Ground Loop | DAIKIN | WSSV015J1*H*T |  | 17000 | 22.25 | 10500 | 3.77 | 1.4167
215399862 | Ground Loop | DAIKIN | WSSV015A1*H*C |  | 17000 | 23.75 | 10400 | 3.77 | 1.4167
215399863 | Ground Loop | DAIKIN | WSSV015J1*H*C |  | 17000 | 22.25 | 10500 | 3.77 | 1.4167
215399865 | Ground Loop | DAIKIN | WSSV019J1*H*T |  | 20600 | 20.96 | 14100 | 3.63 | 1.7167
215399867 | Ground Loop | DAIKIN | WSSV019J1*H*C |  | 20600 | 20.96 | 14100 | 3.63 | 1.7167
215399870 | Ground Loop | DAIKIN | WSSV042J1*H*T |  | 44352 | 21.08 | 28710 | 3.88 | 3.696
215399871 | Ground Loop | DAIKIN | WSSV042K3*H*T |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587
215399874 | Ground Loop | DAIKIN | WSSV042J1*H*C |  | 44352 | 21.08 | 28710 | 3.88 | 3.696
215399875 | Ground Loop | DAIKIN | WSSV042K3*H*C |  | 43904 | 20.87 | 28420 | 3.84 | 3.6587
215399878 | Ground Loop | DAIKIN | WSSV048K3*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35
215399879 | Ground Loop | DAIKIN | WSSV048L3*H*T |  | 52200 | 20.14 | 36400 | 4.04 | 4.35
215399882 | Ground Loop | DAIKIN | WSSV048K3*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35
215399883 | Ground Loop | DAIKIN | WSSV048L3*H*C |  | 52200 | 20.14 | 36400 | 4.04 | 4.35
217642881 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S0**1 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
217642883 | Ground Loop | GeoSmart Energy | S3A(V/H)036*S0**1 |  | 36000 | 17.5 | 27000 | 3.7 | 3
217642884 | Ground Loop | GeoSmart Energy | S3A(V/H)042*S0**1 |  | 42000 | 17.5 | 32000 | 3.7 | 3.5
217642886 | Ground Loop | GeoSmart Energy | S3A(V/H)060*S0**1 |  | 62000 | 17 | 47000 | 3.6 | 5.1667
217642897 | Ground Loop | GeoSmart Energy | S3A(V/H)024*S0**4 |  | 24800 | 17.8 | 18500 | 3.7 | 2.0667
209180330 | Ground Loop | HYDROTECH | WSV6018B* |  | 18000 | 17.2 | 13500 | 3.6 | 1.5
215415772 | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)015A*VB |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667
215415773 | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)015A*VC |  | 15200 | 17.3 | 10700 | 3.6 | 1.2667
215415776 | Ground Loop | Johnson Controls | BC(L/R/B/P/T/K/F)018A*VB |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167
215415777 | Ground Loop | SKYMARK | BC(L/R/B/P/T/K/F)018A*VC |  | 19400 | 17.3 | 13800 | 3.6 | 1.6167
215415778 | Ground Loop | Johnson Controls | BR(L/R/B/P/T/K/F)024A*B |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333
215415779 | Ground Loop | SKYMARK | BR(L/R/B/P/T/K/F)024A*C |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333
215224621 | Ground Loop | CARRIER | 50WD*024***4*(A-H)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224622 | Ground Loop | CARRIER | 50WD*024***4*(J-R)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224623 | Ground Loop | CARRIER | 50WD*024***5*(A-H)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224624 | Ground Loop | CARRIER | 50WD*024***5*(J-R)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224625 | Ground Loop | CARRIER | 50WD*024***6*(A-H)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224626 | Ground Loop | CARRIER | 50WD*024***6*(J-R)** |  | 25000 | 17 | 18000 | 3.7 | 2.0833
215224679 | Ground Loop | BOSCH | RF007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224680 | Ground Loop | BOSCH | RF007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224681 | Ground Loop | BOSCH | RF009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
215224682 | Ground Loop | BOSCH | RF009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
217014536 | Ground Loop | COMFORTMAKER | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
217014537 | Ground Loop | DAY & NIGHT | HCR72V**C******1 |  | 70000 | 17 | 55000 | 3.8 | 5.8333
10318048 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS048**1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417
10318049 | Ground Loop | GeoSmart Energy | GSZ048*1 | SRAA048* | 42500 | 18.7 | 33400 | 4 | 3.5417
205767623 | Ground Loop | ClimateMaster | TCH/V015A*W/K |  | 14800 | 18 | 11000 | 3.6 | 1.2333
205767624 | Ground Loop | ClimateMaster | TRH/V015A*W/K |  | 14800 | 18 | 11000 | 3.6 | 1.2333
205767626 | Ground Loop | ClimateMaster | TES/P038B | TAC038B | 38000 | 17.3 | 26600 | 3.7 | 3.1667
205780261 | Ground Loop | GEOSTAR | 111J038**1*(1,2)* |  | 36000 | 18.7 | 27400 | 3.9 | 3
205782086 | Ground Loop | 5 SERIES INDOOR SPLITS | NSZ042J1 | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15
205782087 | Ground Loop | GEOSTAR | 103J042**1 | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15
205782239 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS036**1*J | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55
205782240 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZS042**1*J | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15
205782241 | Ground Loop | YORK BY JOHNSON CONTROLS | YAZT038**1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3
205782242 | Ground Loop | YORK BY JOHNSON CONTROLS | YAST038**1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3
205782243 | Ground Loop | GeoSmart Energy | GSZ036*1*J | SRAA036* | 30600 | 20.4 | 23100 | 4 | 2.55
205782244 | Ground Loop | GeoSmart Energy | GSZ042*1*J | SRAA048* | 37800 | 19.5 | 27400 | 3.9 | 3.15
205782245 | Ground Loop | GeoSmart Energy | GTZ038*1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3
205782246 | Ground Loop | GeoSmart Energy | GTS038*1*J | SAH036* | 36000 | 19 | 27900 | 4 | 3
205782247 | Ground Loop | GeoSmart Energy | GTS038*1*J | SRAA036* | 36000 | 19 | 27900 | 4 | 3
205782567 | Ground Loop | YORK BY JOHNSON CONTROLS | YACT038**1*(1,2)* |  | 36000 | 18.7 | 27400 | 3.9 | 3
205782571 | Ground Loop | GeoSmart Energy | QT038**1*(1,2)* |  | 36000 | 18.7 | 27400 | 3.9 | 3
205788273 | Ground Loop | Johnson Controls | JSH/V/D018B B |  | 19500 | 18.4 | 14500 | 3.6 | 1.625
205788274 | Ground Loop | SKYMARK | JSH/V/D018B C |  | 19500 | 18.4 | 14500 | 3.6 | 1.625
205788275 | Ground Loop | Johnson Controls | JSH/V/D018B*K B |  | 20200 | 19.4 | 14500 | 3.9 | 1.6833
205788276 | Ground Loop | SKYMARK | JSH/V/D018B*K C |  | 20200 | 19.4 | 14500 | 3.9 | 1.6833
205788277 | Ground Loop | Johnson Controls | JSH/V/D024C B |  | 25300 | 18.9 | 19200 | 4 | 2.1083
205788278 | Ground Loop | SKYMARK | JSH/V/D024C C |  | 25300 | 18.9 | 19200 | 4 | 2.1083
205788279 | Ground Loop | Johnson Controls | JSH/V/D024C*K B |  | 25500 | 20.9 | 19100 | 4.2 | 2.125
205788280 | Ground Loop | SKYMARK | JSH/V/D024C*K C |  | 25500 | 20.9 | 19100 | 4.2 | 2.125
205788281 | Ground Loop | Johnson Controls | JSH/V/D030C B |  | 29200 | 18.5 | 22200 | 3.9 | 2.4333
205788282 | Ground Loop | SKYMARK | JSH/V/D030C C |  | 29200 | 18.5 | 22200 | 3.9 | 2.4333
205788283 | Ground Loop | Johnson Controls | JSH/V/D036C B |  | 34300 | 19.2 | 25900 | 4.1 | 2.8583
205788284 | Ground Loop | SKYMARK | JSH/V/D036C C |  | 34300 | 19.2 | 25900 | 4.1 | 2.8583
205788285 | Ground Loop | Johnson Controls | JSH/V/D036C*K B |  | 34600 | 20.4 | 25600 | 4.3 | 2.8833
205788286 | Ground Loop | SKYMARK | JSH/V/D036C*K C |  | 34600 | 20.4 | 25600 | 4.3 | 2.8833
205788287 | Ground Loop | Johnson Controls | JSH/V/D042C B |  | 40100 | 19.4 | 28700 | 3.8 | 3.3417
205788288 | Ground Loop | SKYMARK | JSH/V/D042C C |  | 40100 | 19.4 | 28700 | 3.8 | 3.3417
205788289 | Ground Loop | Johnson Controls | JSH/V/D042C*K B |  | 40700 | 21.9 | 27400 | 4.1 | 3.3917
205788290 | Ground Loop | SKYMARK | JSH/V/D042C*K C |  | 40700 | 21.9 | 27400 | 4.1 | 3.3917
205788293 | Ground Loop | Johnson Controls | JSH/V/D060C B |  | 63900 | 17.2 | 46900 | 3.7 | 5.325
205788294 | Ground Loop | SKYMARK | JSH/V/D060C C |  | 63900 | 17.2 | 46900 | 3.7 | 5.325
205823049 | Ground Loop | OMEGA HEAT PUMP | VSHP050G |  | 15000 | 18.5 | 10600 | 3.7 | 1.25
205823050 | Ground Loop | OMEGA HEAT PUMP | VSHP060G |  | 18200 | 17.3 | 14000 | 3.6 | 1.5167
214772087 | Ground Loop | TRANE | EXVK042B |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083
214772088 | Ground Loop | TRANE | EXVK0424 |  | 43300 | 20.9 | 30800 | 4.1 | 3.6083
214772089 | Ground Loop | TRANE | EXVK048B |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083
214772090 | Ground Loop | TRANE | EXVK0484 |  | 46900 | 20.3 | 33900 | 3.99 | 3.9083
214772091 | Ground Loop | TRANE | EXVK060B |  | 62700 | 19.7 | 45200 | 3.82 | 5.225
214772092 | Ground Loop | TRANE | EXVK0604 |  | 62700 | 19.7 | 45200 | 3.82 | 5.225
214772093 | Ground Loop | TRANE | EXVK070B |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917
214772094 | Ground Loop | TRANE | EXVK0704 |  | 65900 | 20.1 | 48800 | 3.9 | 5.4917
214772095 | Ground Loop | TRANE | DXVK024A |  | 25700 | 21.4 | 18900 | 4.2 | 2.1417
214772096 | Ground Loop | TRANE | DXVK036A |  | 33800 | 20.9 | 25400 | 4.3 | 2.8167
214772097 | Ground Loop | TRANE | DXVK048A |  | 46300 | 20.2 | 32300 | 4.3 | 3.8583
214772098 | Ground Loop | TRANE | DXVK060A |  | 56500 | 21.1 | 41000 | 4.3 | 4.7083
214772099 | Ground Loop | TRANE | DXVK070A |  | 65100 | 18.9 | 51700 | 4.1 | 5.425
214772101 | Ground Loop | TRANE | GEHK0097 |  | 8800 | 19.6 | 6400 | 3.96 | 0.73333
214772103 | Ground Loop | TRANE | GEHK0157 |  | 15900 | 18.2 | 12500 | 3.85 | 1.325
214772104 | Ground Loop | TRANE | GEHK0187 |  | 18500 | 17.3 | 15300 | 3.76 | 1.5417
214772105 | Ground Loop | TRANE | GEHK024B |  | 25400 | 18.9 | 19700 | 3.65 | 2.1167
213710616 | Ground Loop | DAIKIN | WSSH012J1*H*T |  | 12200 | 19 | 9100 | 3.8 | 1.0167
213710620 | Ground Loop | DAIKIN | WSSH015A1*H*T |  | 17100 | 23.7 | 11000 | 3.9 | 1.425
213710622 | Ground Loop | DAIKIN | WSSH015A1*H*C |  | 17100 | 23.7 | 11000 | 3.9 | 1.425
213710624 | Ground Loop | DAIKIN | WSSH015E1*H*T |  | 17100 | 23.69 | 11000 | 3.9 | 1.425
213710625 | Ground Loop | DAIKIN | WSSH015E1*H*C |  | 17100 | 23.69 | 11000 | 3.9 | 1.425
213710629 | Ground Loop | DAIKIN | WSSH015J1*H*T |  | 17000 | 22 | 10900 | 3.9 | 1.4167
213710630 | Ground Loop | DAIKIN | WSSH015J1*H*C |  | 17000 | 22 | 10900 | 3.9 | 1.4167
213710633 | Ground Loop | DAIKIN | WSSH019E1*H*T |  | 20700 | 21.1 | 14100 | 3.8 | 1.725
213710634 | Ground Loop | DAIKIN | WSSH019E1*H*C |  | 20700 | 21.1 | 14100 | 3.8 | 1.725
213710638 | Ground Loop | DAIKIN | WSSH019J1*H*T |  | 20700 | 21.1 | 14100 | 3.8 | 1.725
213710639 | Ground Loop | DAIKIN | WSSH019J1*H*C |  | 20700 | 21.1 | 14100 | 3.8 | 1.725
213710641 | Ground Loop | DAIKIN | WSSH024E1*H*T |  | 25700 | 21.7 | 16900 | 4 | 2.1417
213710643 | Ground Loop | DAIKIN | WSSH024E1*H*C |  | 25700 | 21.7 | 16900 | 4 | 2.1417
213710645 | Ground Loop | DAIKIN | WSSH030E1*H*T |  | 30600 | 22.5 | 21200 | 4.2 | 2.55
213710646 | Ground Loop | DAIKIN | WSSH030E1*H*C |  | 30600 | 22.5 | 21200 | 4.2 | 2.55
213710648 | Ground Loop | DAIKIN | WSSH036E1*H*T |  | 40300 | 22 | 27600 | 3.7 | 3.3583
213710650 | Ground Loop | DAIKIN | WSSH036E1*H*C |  | 40300 | 22 | 27600 | 3.7 | 3.3583
213710652 | Ground Loop | DAIKIN | WSSH042E1*H*T |  | 44000 | 21.7 | 29000 | 3.9 | 3.6667
213710653 | Ground Loop | DAIKIN | WSSH042E1*H*C |  | 44000 | 21.7 | 29000 | 3.9 | 3.6667
213710655 | Ground Loop | DAIKIN | WSSH048E1*H*T |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667
213710657 | Ground Loop | DAIKIN | WSSH048E1*H*C |  | 51200 | 20.1 | 35100 | 3.6 | 4.2667
213714597 | Ground Loop | DAIKIN | WSSH070E1*H*T |  | 73300 | 19.73 | 53600 | 3.64 | 6.1083
213714598 | Ground Loop | DAIKIN | WSSH070E1*H*C |  | 73300 | 19.73 | 53600 | 3.64 | 6.1083
5646381 | Ground Loop | GEOCOMFORT | GCT036D |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167
5646382 | Ground Loop | HYDRON MODULE | HCT036D |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167
5646383 | Ground Loop | TETCO | TCT036D |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167
5646384 | Ground Loop | GEOCOMFORT | GCT036D2 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167
5646385 | Ground Loop | HYDRON MODULE | HCT036D2 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167
5646386 | Ground Loop | TETCO | TCT036D2 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167
5646387 | Ground Loop | GEOCOMFORT | GCT036D3 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167
5646388 | Ground Loop | HYDRON MODULE | HCT036D3 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167
5646389 | Ground Loop | TETCO | TCT036D3 |  | 38600 | 18.3 | 28600 | 4.1 | 3.2167
5646391 | Ground Loop | GEOCOMFORT | GXT048D |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833
5646392 | Ground Loop | HYDRON MODULE | HXT048D |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833
5646393 | Ground Loop | TETCO | TXT048D |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833
5646394 | Ground Loop | GEOCOMFORT | GXT048D2 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833
5646395 | Ground Loop | HYDRON MODULE | HXT048D2 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833
5646396 | Ground Loop | TETCO | TXT048D2 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833
5646397 | Ground Loop | GEOCOMFORT | GXT048D3 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833
5646398 | Ground Loop | HYDRON MODULE | HXT048D3 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833
5646399 | Ground Loop | TETCO | TXT048D3 |  | 49000 | 17.1 | 38200 | 3.9 | 4.0833
5646765 | Ground Loop | GEOCOMFORT | GCT048D |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833
5646766 | Ground Loop | HYDRON MODULE | HCT048D |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833
5646767 | Ground Loop | TETCO | TCT048D |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833
5646768 | Ground Loop | GEOCOMFORT | GCT048D2 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833
5646769 | Ground Loop | HYDRON MODULE | HCT048D2 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833
5646770 | Ground Loop | TETCO | TCT048D2 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833
5646771 | Ground Loop | GEOCOMFORT | GCT048D3 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833
5646772 | Ground Loop | HYDRON MODULE | HCT048D3 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833
5646773 | Ground Loop | TETCO | TCT048D3 |  | 49000 | 17.1 | 38000 | 3.9 | 4.0833
5699505 | Ground Loop | TRANE | VSVE0421 |  | 46200 | 22.03 | 31900 | 3.98 | 3.85
5699525 | Ground Loop | TRANE | VSVE0422 |  | 46200 | 22.03 | 31900 | 3.98 | 3.85
5699526 | Ground Loop | TRANE | VSVE0424 |  | 46200 | 22.03 | 31900 | 3.98 | 3.85
5699527 | Ground Loop | TRANE | VSVE0601 |  | 64600 | 18.3 | 50000 | 4 | 5.3833
5699534 | Ground Loop | TRANE | VSVE0602 |  | 64600 | 18.3 | 50000 | 4 | 5.3833
5699535 | Ground Loop | TRANE | VSVE0604 |  | 64600 | 18.3 | 50000 | 4 | 5.3833
5699628 | Ground Loop | TRANE | VSHE0241 |  | 26200 | 21.82 | 18500 | 4.35 | 2.1833
5699631 | Ground Loop | TRANE | VSHE0242 |  | 26200 | 21.82 | 18500 | 4.35 | 2.1833
5699633 | Ground Loop | TRANE | VSHE0244 |  | 26200 | 21.82 | 18500 | 4.35 | 2.1833
5699634 | Ground Loop | TRANE | VSHE0331 |  | 35300 | 18.51 | 24700 | 4.1 | 2.9417
5699635 | Ground Loop | TRANE | VSHE0332 |  | 35300 | 18.51 | 24700 | 4.1 | 2.9417
5699637 | Ground Loop | TRANE | VSHE0334 |  | 35300 | 18.51 | 24700 | 4.1 | 2.9417
5699639 | Ground Loop | TRANE | VSHE0421 |  | 44600 | 22 | 31500 | 4.5 | 3.7167
5699644 | Ground Loop | TRANE | VSHE0422 |  | 44600 | 22 | 31500 | 4.5 | 3.7167
5699650 | Ground Loop | TRANE | VSHE0424 |  | 44600 | 22 | 31500 | 4.5 | 3.7167
5699652 | Ground Loop | TRANE | VSHE0501 |  | 52400 | 19.3 | 40100 | 4.2 | 4.3667
5699653 | Ground Loop | TRANE | VSHE0502 |  | 52400 | 19.3 | 40100 | 4.2 | 4.3667
5699654 | Ground Loop | TRANE | VSHE0504 |  | 52400 | 19.3 | 40100 | 4.2 | 4.3667
5699655 | Ground Loop | TRANE | VSHE0601 |  | 63200 | 17 | 50400 | 3.8 | 5.2667
5699656 | Ground Loop | TRANE | VSHE0602 |  | 63200 | 17 | 50400 | 3.8 | 5.2667
5699657 | Ground Loop | TRANE | VSHE0604 |  | 63200 | 17 | 50400 | 3.8 | 5.2667
6501887 | Ground Loop | GEOSTAR | GBV/GBH015**0*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25
6501888 | Ground Loop | GEOSTAR | GBV/GBH015**0*1 |  | 15000 | 18.8 | 12000 | 4 | 1.25
6501889 | Ground Loop | GEOSTAR | GBV/GBH015**0*4 |  | 15000 | 18.8 | 12000 | 4 | 1.25
6501890 | Ground Loop | GEOSTAR | GBV/GBH015**2*0 |  | 15000 | 18 | 12000 | 3.8 | 1.25
7795945 | Ground Loop | TETCO | TVT036 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167
7795946 | Ground Loop | GEOCOMFORT | GVT036*2 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167
7795947 | Ground Loop | HYDRON MODULE | HVT036*2 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167
7795948 | Ground Loop | TETCO | TVT036*2 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167
7795949 | Ground Loop | GEOCOMFORT | GVT036*3 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167
7795950 | Ground Loop | HYDRON MODULE | HVT036*3 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167
7795951 | Ground Loop | TETCO | TVT036*3 |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167
7795952 | Ground Loop | GEOCOMFORT | GVT036*A |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167
7795953 | Ground Loop | HYDRON MODULE | HVT036*A |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167
7795954 | Ground Loop | TETCO | TVT036*A |  | 37400 | 17.7 | 29500 | 3.9 | 3.1167
8000290 | Ground Loop | GEOCOOL | GCHP01024 |  | 25000 | 17.1 | 16000 | 3.6 | 2.0833
8000291 | Ground Loop | GEOCOOL | GCHP01031 |  | 31200 | 17.1 | 19500 | 3.6 | 2.6
8000292 | Ground Loop | GEOCOOL | GCHP01036 |  | 35500 | 17.1 | 25500 | 3.6 | 2.9583
8000293 | Ground Loop | GEOCOOL | GCHP01041 |  | 40500 | 17.1 | 26000 | 3.6 | 3.375
8077723 | Ground Loop | GEOCOMFORT | GYT060 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583
8077724 | Ground Loop | HYDRON MODULE | HYT060 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583
8077725 | Ground Loop | TETCO | TYT060 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583
8077726 | Ground Loop | GEOCOMFORT | GYT060*2 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583
8077727 | Ground Loop | HYDRON MODULE | HYT060*2 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583
8077728 | Ground Loop | TETCO | TYT060*2 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583
8077729 | Ground Loop | GEOCOMFORT | GYT060*3 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583
8077730 | Ground Loop | HYDRON MODULE | HYT060*3 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583
8077731 | Ground Loop | TETCO | TYT060*3 |  | 64300 | 19.3 | 49200 | 4.1 | 5.3583
8077735 | Ground Loop | GEOCOMFORT | GYT072 |  | 71900 | 18 | 56200 | 3.8 | 5.9917
8077736 | Ground Loop | HYDRON MODULE | HYT072 |  | 71900 | 18 | 56200 | 3.8 | 5.9917
8077737 | Ground Loop | TETCO | TYT072 |  | 71900 | 18 | 56200 | 3.8 | 5.9917
8077738 | Ground Loop | GEOCOMFORT | GYT072*2 |  | 71900 | 18 | 56200 | 3.8 | 5.9917
8077739 | Ground Loop | HYDRON MODULE | HYT072*2 |  | 71900 | 18 | 56200 | 3.8 | 5.9917
8077740 | Ground Loop | TETCO | TYT072*2 |  | 71900 | 18 | 56200 | 3.8 | 5.9917
8077741 | Ground Loop | GEOCOMFORT | GYT072*3 |  | 71900 | 18 | 56200 | 3.8 | 5.9917
8077742 | Ground Loop | HYDRON MODULE | HYT072*3 |  | 71900 | 18 | 56200 | 3.8 | 5.9917
8077743 | Ground Loop | TETCO | TYT072*3 |  | 71900 | 18 | 56200 | 3.8 | 5.9917
8233354 | Ground Loop | DAIKIN | W.CCW.2.072*F |  | 80100 | 17.1 | 58700 | 3.75 | 6.675
8233365 | Ground Loop | DAIKIN | W.CCW.2.072*K |  | 80100 | 17.1 | 58700 | 3.75 | 6.675
215415835 | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)024A |  | 25600 | 17.3 | 19000 | 3.6 | 2.1333
215415836 | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15
215415837 | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)024A*V |  | 25800 | 18 | 19000 | 3.7 | 2.15
215415840 | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417
215415841 | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)030A*V |  | 30500 | 17.3 | 23000 | 3.6 | 2.5417
215415844 | Ground Loop | CENTURY | MC(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333
215415845 | Ground Loop | COMFORT-AIRE | MC(L/R/B/P/T/K/F)036A*V |  | 36400 | 17.4 | 27900 | 3.6 | 3.0333
217754507 | Ground Loop | DAIKIN | WSTV030E1*H*C |  | 32200 | 19.48 | 20800 | 3.78 | 2.6833
217754508 | Ground Loop | DAIKIN | WSTV030F1*H*C |  | 32200 | 19.09 | 20800 | 3.7 | 2.6833
217754511 | Ground Loop | DAIKIN | WSTV036E1*H*C |  | 39100 | 21.12 | 25600 | 3.68 | 3.2583
217754512 | Ground Loop | DAIKIN | WSTV036F1*H*C |  | 39100 | 20.7 | 25600 | 3.61 | 3.2583
217754515 | Ground Loop | DAIKIN | WSTV042E1*H*C |  | 44800 | 19.54 | 27600 | 3.74 | 3.7333
217754516 | Ground Loop | DAIKIN | WSTV042F1*H*C |  | 44800 | 19.15 | 27600 | 3.66 | 3.7333
217754519 | Ground Loop | DAIKIN | WSTV048E1*H*C |  | 52400 | 20.17 | 35200 | 3.9 | 4.3667
217754520 | Ground Loop | DAIKIN | WSTV048F1*H*C |  | 52400 | 19.76 | 35200 | 3.82 | 4.3667
217754523 | Ground Loop | DAIKIN | WSTV060E1*H*C |  | 63100 | 19.6 | 46800 | 4.1 | 5.2583
217754524 | Ground Loop | DAIKIN | WSTV060F1*H*C |  | 63100 | 19.21 | 46800 | 4.02 | 5.2583
217754527 | Ground Loop | DAIKIN | WSTV070E1*H*C |  | 74600 | 19 | 56000 | 4 | 6.2167
217754528 | Ground Loop | DAIKIN | WSTV070F1*H*C |  | 74600 | 18.62 | 56000 | 3.92 | 6.2167
217754535 | Ground Loop | DAIKIN | WSMH024F1*G/J*P |  | 25600 | 18.72 | 18400 | 3.8 | 2.1333
217754536 | Ground Loop | DAIKIN | WSMH024K1*G/J*P |  | 25600 | 18.72 | 18400 | 3.8 | 2.1333
217754539 | Ground Loop | DAIKIN | WSMH024F1*G/J*T |  | 25800 | 19.99 | 18200 | 3.8 | 2.15
217754540 | Ground Loop | DAIKIN | WSMH024K1*G/J*T |  | 25800 | 19.99 | 18200 | 3.8 | 2.15
217754543 | Ground Loop | DAIKIN | WSMH024F1*G/J*C |  | 25800 | 19.99 | 18200 | 3.8 | 2.15
217754544 | Ground Loop | DAIKIN | WSMH024K1*G/J*C |  | 25800 | 19.99 | 18200 | 3.8 | 2.15
217754547 | Ground Loop | DAIKIN | WSMH030F1*G/J*P |  | 29200 | 18.62 | 22200 | 3.72 | 2.4333
217754548 | Ground Loop | DAIKIN | WSMH030K1*G/J*P |  | 29200 | 18.62 | 22200 | 3.72 | 2.4333
217754551 | Ground Loop | DAIKIN | WSMH030F1*G/J*T |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583
217754552 | Ground Loop | DAIKIN | WSMH030K1*G/J*T |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583
217754555 | Ground Loop | DAIKIN | WSMH030F1*G/J*C |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583
217754556 | Ground Loop | DAIKIN | WSMH030K1*G/J*C |  | 29500 | 20.19 | 21900 | 3.92 | 2.4583
217754559 | Ground Loop | DAIKIN | WSMH036F1*G/J*P |  | 37800 | 18.18 | 30700 | 3.79 | 3.15
217754560 | Ground Loop | DAIKIN | WSMH036K1*G/J*P |  | 37800 | 18.1 | 30700 | 3.79 | 3.15
217754563 | Ground Loop | DAIKIN | WSMH036F1*G/J*T |  | 38000 | 19.24 | 30000 | 3.89 | 3.1667
204100658 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ064J1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
204100659 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ064J1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
204100660 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS064J1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
204100661 | Ground Loop | 5 SERIES OUTDOOR SPLITS | NDS064J1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
204101161 | Ground Loop | 5 SERIES | NDV/NDH064J1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
204117015 | Ground Loop | GEOSTAR | 101/102J064**1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
204117016 | Ground Loop | GEOSTAR | 103J064**1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
204117017 | Ground Loop | GEOSTAR | 103J064**1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
213502525 | Ground Loop | DAIKIN | WSMH015A1*G/J*P |  | 16000 | 20.1 | 12100 | 4 | 1.3333
213502526 | Ground Loop | DAIKIN | WSMH015A1*G/J*T |  | 16300 | 21.1 | 11800 | 4.1 | 1.3583
213502527 | Ground Loop | DAIKIN | WSMH015A1*G/J*C |  | 16300 | 21.1 | 11800 | 4.1 | 1.3583
213502531 | Ground Loop | DAIKIN | WSMH015E1*G/J*P |  | 16000 | 20.1 | 12300 | 4 | 1.3333
213502532 | Ground Loop | DAIKIN | WSMH015E1*G/J*T |  | 16300 | 21.1 | 12000 | 4.1 | 1.3583
213502533 | Ground Loop | DAIKIN | WSMH015E1*G/J*C |  | 16300 | 21.1 | 12000 | 4.1 | 1.3583
213502537 | Ground Loop | DAIKIN | WSMH015J1*G/J*P |  | 16000 | 18.9 | 12300 | 3.9 | 1.3333
213502538 | Ground Loop | DAIKIN | WSMH015J1*G/J*T |  | 16300 | 19.9 | 12000 | 4 | 1.3583
213502539 | Ground Loop | DAIKIN | WSMH015J1*G/J*C |  | 16300 | 19.9 | 12000 | 4 | 1.3583
213502543 | Ground Loop | DAIKIN | WSMH019E1*G/J*P |  | 20500 | 18.8 | 15600 | 3.8 | 1.7083
213502544 | Ground Loop | DAIKIN | WSMH019E1*G/J*T |  | 20700 | 19.5 | 15300 | 3.9 | 1.725
213502545 | Ground Loop | DAIKIN | WSMH019E1*G/J*C |  | 20700 | 19.5 | 15300 | 3.9 | 1.725
213502549 | Ground Loop | DAIKIN | WSMH019J1*G/J*P |  | 20500 | 18.8 | 15600 | 3.7 | 1.7083
213502550 | Ground Loop | DAIKIN | WSMH019J1*G/J*T |  | 20700 | 19.5 | 15300 | 3.8 | 1.725
213502551 | Ground Loop | DAIKIN | WSMH019J1*G/J*C |  | 20700 | 19.5 | 15300 | 3.8 | 1.725
213502555 | Ground Loop | DAIKIN | WSMH024E1*G/J*P |  | 25600 | 19.2 | 18400 | 3.9 | 2.1333
213502556 | Ground Loop | DAIKIN | WSMH024E1*G/J*T |  | 25800 | 20.5 | 18200 | 3.9 | 2.15
213502557 | Ground Loop | DAIKIN | WSMH024E1*G/J*C |  | 25800 | 20.5 | 18200 | 3.9 | 2.15
213502561 | Ground Loop | DAIKIN | WSMH030E1*G/J*P |  | 29200 | 19 | 22200 | 3.8 | 2.4333
213502562 | Ground Loop | DAIKIN | WSMH030E1*G/J*T |  | 29500 | 20.6 | 21900 | 4 | 2.4583
213502563 | Ground Loop | DAIKIN | WSMH030E1*G/J*C |  | 29500 | 20.6 | 21900 | 4 | 2.4583
213502567 | Ground Loop | DAIKIN | WSMH036E1*G/J*P |  | 37800 | 18.8 | 30700 | 3.9 | 3.15
213502568 | Ground Loop | DAIKIN | WSMH036E1*G/J*T |  | 38000 | 19.9 | 30000 | 4 | 3.1667
213502569 | Ground Loop | DAIKIN | WSMH036E1*G/J*C |  | 38000 | 19.9 | 30000 | 4 | 3.1667
213502573 | Ground Loop | DAIKIN | WSCH042E1*G/J*P |  | 39900 | 17.5 | 32500 | 3.7 | 3.325
213502574 | Ground Loop | DAIKIN | WSCH042E1*G/J*T |  | 40800 | 19.4 | 31600 | 3.8 | 3.4
213502575 | Ground Loop | DAIKIN | WSCH042E1*G/J*C |  | 40800 | 19.4 | 31600 | 3.8 | 3.4
214839009 | Ground Loop | FHP | EC072-1VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167
214839010 | Ground Loop | FHP | EC072-3VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167
214839011 | Ground Loop | FHP | EC072-4VT/HZ*-*****C |  | 80600 | 18.85 | 55900 | 3.85 | 6.7167
214839012 | Ground Loop | FHP | EC096-1VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667
214839013 | Ground Loop | FHP | EC096-3VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667
214839014 | Ground Loop | FHP | EC096-4VT/HZ*-*****C |  | 104000 | 18.9 | 82000 | 4 | 8.6667
216625648 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D3**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625649 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D3**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625650 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D4**1 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625651 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*D4**4 |  | 32300 | 20.3 | 24600 | 4 | 2.6917
216625652 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S0**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625653 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S0**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625654 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S2**1 |  | 30000 | 21 | 23000 | 3.9 | 2.5
216625655 | Ground Loop | YORK BY JOHNSON CONTROLS | Y5A(V/H)030*S2**4 |  | 30000 | 21 | 23000 | 3.9 | 2.5
207178493 | Ground Loop | GEOSTAR | 164J038**1 | SAH036* | 36000 | 19 | 27900 | 4 | 3
4651865 | Ground Loop | GEOSTAR | ZS023**2*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
4651866 | Ground Loop | GeoSmart Energy | ZS023**2*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
4651869 | Ground Loop | GEOSTAR | ZS023**3*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
4651870 | Ground Loop | GeoSmart Energy | ZS023**3*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
4651873 | Ground Loop | GEOSTAR | ZS023**4*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
4651874 | Ground Loop | GeoSmart Energy | ZS023**4*4 |  | 23900 | 17 | 17000 | 3.6 | 1.9917
4651882 | Ground Loop | GEOSTAR | ZS042**0*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
4651883 | Ground Loop | GeoSmart Energy | ZS042**0*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
4651888 | Ground Loop | GEOSTAR | ZS042**3*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
4651889 | Ground Loop | GeoSmart Energy | ZS042**3*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
4651894 | Ground Loop | GEOSTAR | ZS042**4*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
4651895 | Ground Loop | GeoSmart Energy | ZS042**4*4 |  | 42300 | 18.5 | 29900 | 3.7 | 3.525
4651936 | Ground Loop | GEOSTAR | ZS048**0*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
4651937 | Ground Loop | GeoSmart Energy | ZS048**0*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
4651942 | Ground Loop | GeoSmart Energy | ZS048**3*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
4651943 | Ground Loop | GEOSTAR | ZS048**3*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
4651948 | Ground Loop | GEOSTAR | ZS048**4*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
4651949 | Ground Loop | GeoSmart Energy | ZS048**4*4 |  | 49500 | 18.1 | 36900 | 3.6 | 4.125
4651954 | Ground Loop | GEOSTAR | ZS060**0*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
4651955 | Ground Loop | GeoSmart Energy | ZS060**0*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
4651966 | Ground Loop | GEOSTAR | ZS060**4*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
4651967 | Ground Loop | GeoSmart Energy | ZS060**4*4 |  | 60900 | 17.9 | 47100 | 3.6 | 5.075
4651972 | Ground Loop | GEOSTAR | ZS070**0*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
4651973 | Ground Loop | GeoSmart Energy | ZS070**0*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
4651978 | Ground Loop | GEOSTAR | ZS070**3*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
4651979 | Ground Loop | GeoSmart Energy | ZS070**3*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
4651984 | Ground Loop | GEOSTAR | ZS070**4*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
4651985 | Ground Loop | GeoSmart Energy | ZS070**4*4 |  | 68500 | 17.1 | 51600 | 3.6 | 5.7083
207200558 | Ground Loop | GeoSmart Energy | GT064**1*(1,4)*J |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207200565 | Ground Loop | GeoSmart Energy | GS060**1*(1,4)*H |  | 62200 | 18.4 | 47900 | 4 | 5.1833
207200566 | Ground Loop | GeoSmart Energy | GS060**1*0*H |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
207200576 | Ground Loop | GeoSmart Energy | GTZ026*1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207200577 | Ground Loop | GeoSmart Energy | GTZ026*1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207200578 | Ground Loop | GeoSmart Energy | GTS026*1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
5315761 | Ground Loop | WaterFurnace | NBV/NBH048**0*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
5315762 | Ground Loop | WaterFurnace | NBV/NBH048**3*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
5315763 | Ground Loop | WaterFurnace | NBV/NBH048**4*4 |  | 45900 | 18.8 | 36400 | 4 | 3.825
5315774 | Ground Loop | WaterFurnace | NBV/NBH060**0*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
5315776 | Ground Loop | WaterFurnace | NBV/NBH060**3*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
5315777 | Ground Loop | WaterFurnace | NBV/NBH060**4*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
5315778 | Ground Loop | WaterFurnace | NBV/NBH060**5*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
5315780 | Ground Loop | WaterFurnace | NBV/NBH060**0*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
5315781 | Ground Loop | WaterFurnace | NBV/NBH060**3*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
5315782 | Ground Loop | WaterFurnace | NBV/NBH060**4*1 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
5315783 | Ground Loop | WaterFurnace | NBV/NBH060**0*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
5315784 | Ground Loop | WaterFurnace | NBV/NBH060**3*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
5315785 | Ground Loop | WaterFurnace | NBV/NBH060**4*4 |  | 62200 | 18.4 | 47900 | 4 | 5.1833
5316500 | Ground Loop | WaterFurnace | NBV/NBH070**0*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
5316501 | Ground Loop | WaterFurnace | NBV/NBH070**3*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
5316502 | Ground Loop | WaterFurnace | NBV/NBH070**4*1 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
5316503 | Ground Loop | WaterFurnace | NBV/NBH070**0*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
5316504 | Ground Loop | WaterFurnace | NBV/NBH070**3*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
5316505 | Ground Loop | WaterFurnace | NBV/NBH070**4*4 |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
5316510 | Ground Loop | WaterFurnace | NBV/NBH026**0*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
5316511 | Ground Loop | WaterFurnace | NBV/NBH026**3*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
5316512 | Ground Loop | WaterFurnace | NBV/NBH026**2*1 |  | 26400 | 19.6 | 19500 | 4 | 2.2
5316513 | Ground Loop | WaterFurnace | NBV/NBH026**0*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
5316514 | Ground Loop | WaterFurnace | NBV/NBH026**3*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
5316515 | Ground Loop | WaterFurnace | NBV/NBH026**4*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
5316516 | Ground Loop | WaterFurnace | NBV/NBH026**2*4 |  | 26400 | 19.6 | 19500 | 4 | 2.2
5317193 | Ground Loop | WaterFurnace | NBV/NBH038**0*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
5317194 | Ground Loop | WaterFurnace | NBV/NBH038**3*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
5317195 | Ground Loop | WaterFurnace | NBV/NBH038**2*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
5317196 | Ground Loop | WaterFurnace | NBV/NBH038**4*1 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
5317197 | Ground Loop | WaterFurnace | NBV/NBH038**0*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
5317198 | Ground Loop | WaterFurnace | NBV/NBH038**3*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
5317199 | Ground Loop | WaterFurnace | NBV/NBH038**4*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
5317200 | Ground Loop | WaterFurnace | NBV/NBH038**2*4 |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
5317201 | Ground Loop | WaterFurnace | NBV/NBH049**0*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
5317202 | Ground Loop | WaterFurnace | NBV/NBH049**3*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
5317203 | Ground Loop | WaterFurnace | NBV/NBH049**4*4 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
5317205 | Ground Loop | WaterFurnace | NBV/NBH049**0*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
5317206 | Ground Loop | WaterFurnace | NBV/NBH049**3*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
5317207 | Ground Loop | WaterFurnace | NBV/NBH049**4*1 |  | 50800 | 19.3 | 38200 | 4 | 4.2333
5317209 | Ground Loop | WaterFurnace | NBV/NBH064**0*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
5317210 | Ground Loop | WaterFurnace | NBV/NBH064**3*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
5317211 | Ground Loop | WaterFurnace | NBV/NBH064**4*1 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
5317270 | Ground Loop | WaterFurnace | NBV/NBH064**4*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
5317328 | Ground Loop | WaterFurnace | NBV/NBH064**3*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
5317329 | Ground Loop | WaterFurnace | NBV/NBH064**0*4 |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
5317330 | Ground Loop | WaterFurnace | NBV/NBH072**0*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
5317331 | Ground Loop | WaterFurnace | NBV/NBH072**3*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
5317332 | Ground Loop | WaterFurnace | NBV/NBH072**4*1 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
5317333 | Ground Loop | WaterFurnace | NBV/NBH072**4*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
5317334 | Ground Loop | WaterFurnace | NBV/NBH072**3*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
5317335 | Ground Loop | WaterFurnace | NBV/NBH072**0*4 |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
215268733 | Ground Loop | WaterFurnace | V5A(V/H)072*S4**4 |  | 70000 | 17.8 | 54000 | 3.7 | 5.8333
215268734 | Ground Loop | WaterFurnace | V5A(V/H)036*S2**1 |  | 37500 | 21.5 | 26000 | 4.2 | 3.125
215268735 | Ground Loop | WaterFurnace | V5A(V/H)018*D0**1 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583
215268736 | Ground Loop | WaterFurnace | V5A(V/H)018*D0**4 |  | 18700 | 19.8 | 14700 | 4.2 | 1.5583
215268737 | Ground Loop | WaterFurnace | V5A(V/H)024*D0**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
215268738 | Ground Loop | WaterFurnace | V5A(V/H)024*D2**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
215268739 | Ground Loop | WaterFurnace | V5A(V/H)024*D3**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
215268740 | Ground Loop | WaterFurnace | V5A(V/H)024*D4**1 |  | 25000 | 19.2 | 19400 | 4.1 | 2.0833
5646375 | Ground Loop | HYDRON MODULE | HXT036D2 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417
5646376 | Ground Loop | TETCO | TXT036D2 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417
5646377 | Ground Loop | GEOCOMFORT | GXT036D3 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417
5646378 | Ground Loop | HYDRON MODULE | HXT036D3 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417
5646379 | Ground Loop | TETCO | TXT036D3 |  | 38900 | 18.3 | 29200 | 4.2 | 3.2417
207312016 | Ground Loop | WaterFurnace | SDV049J1*(1,2) |  | 47700 | 18.2 | 38000 | 3.8 | 3.975
207312018 | Ground Loop | WaterFurnace | SDV072J1*1 |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083
207312019 | Ground Loop | WaterFurnace | SDV038K1*(1,2) |  | 36000 | 18.7 | 27400 | 3.9 | 3
207312171 | Ground Loop | WaterFurnace | NDV/NDH026J1*(1,4) |  | 26400 | 19.6 | 19500 | 4 | 2.2
207312172 | Ground Loop | WaterFurnace | NDV/NDH038K1*(1,2,4) |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207312173 | Ground Loop | WaterFurnace | NDV/NDH049K1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207312174 | Ground Loop | WaterFurnace | NDV/NDH072J1*(1,4) |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207312176 | Ground Loop | WaterFurnace | NDV/NDH064K1*(1,4) |  | 65500 | 19.3 | 47300 | 3.8 | 5.4583
207312224 | Ground Loop | WaterFurnace | NSV/NSH018J1*(1,4) |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
207312225 | Ground Loop | WaterFurnace | NSV/NSH030J1*(1,4) |  | 28100 | 22 | 20500 | 3.9 | 2.3417
207312226 | Ground Loop | WaterFurnace | NSV/NSH036K1*(1,2,4) |  | 33700 | 22 | 24400 | 4.2 | 2.8083
207312227 | Ground Loop | WaterFurnace | NSV/NSH042K1*(1,2,4) |  | 40700 | 21.7 | 28900 | 4 | 3.3917
207312228 | Ground Loop | WaterFurnace | NSV/NSH048K1*(1,2,4) |  | 45900 | 18.8 | 36400 | 4 | 3.825
207312229 | Ground Loop | WaterFurnace | NSV/NSH060K1*(1,4)* |  | 62200 | 18.4 | 47900 | 4 | 5.1833
207312230 | Ground Loop | WaterFurnace | NSV/NSH070J1*(1,4) |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
207312265 | Ground Loop | WaterFurnace | NSV/NSH030J1*(0,3) |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
207312266 | Ground Loop | WaterFurnace | NSV/NSH036K1*(0,3) |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
207312269 | Ground Loop | WaterFurnace | NSV/NSH060K1*0* |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
207312271 | Ground Loop | WaterFurnace | NSV/NSH022J1*(1,4) |  | 19200 | 18.7 | 15000 | 4 | 1.6
207323881 | Ground Loop | WaterFurnace | NDZ026H1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207323882 | Ground Loop | WaterFurnace | NDZ026H1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207323883 | Ground Loop | WaterFurnace | NDS026H1 | SAH026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207323884 | Ground Loop | WaterFurnace | NDS026H1 | SRAA026* | 23400 | 17.5 | 18400 | 3.7 | 1.95
207323885 | Ground Loop | WaterFurnace | NDZ038J1 | SAH036* | 36000 | 19 | 27900 | 4 | 3
207323886 | Ground Loop | WaterFurnace | NDZ038J1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3
207323887 | Ground Loop | WaterFurnace | NDS038J1 | SRAA036* | 36000 | 19 | 27900 | 4 | 3
207323888 | Ground Loop | WaterFurnace | NDZ049J1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207323889 | Ground Loop | WaterFurnace | NDZ049J1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207323890 | Ground Loop | WaterFurnace | NDS049H1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207323891 | Ground Loop | WaterFurnace | NDS049H1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
207323892 | Ground Loop | WaterFurnace | NDZ064J1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207323893 | Ground Loop | WaterFurnace | NDZ064J1 | SRAA060* | 57400 | 17 | 45200 | 3.7 | 4.7833
207323894 | Ground Loop | WaterFurnace | NDS064H1 | SAH060* | 57400 | 17 | 45200 | 3.7 | 4.7833
215310891 | Ground Loop | GEOSTAR | G7A(V/H)024BV1**2 |  | 24100 | 23.6 | 24800 | 4.1 | 2.0083
215310892 | Ground Loop | GEOSTAR | G7A(V/H)036BV1**2 |  | 35800 | 18.1 | 32900 | 3.8 | 2.9833
215310893 | Ground Loop | GEOSTAR | G7A(V/H)048BV1**2 |  | 45000 | 18.9 | 42000 | 3.6 | 3.75
215310990 | Ground Loop | GeoSmart Energy | S7A(V/H)024BV1**2 |  | 24100 | 23.6 | 24800 | 4.1 | 2.0083
215224477 | Ground Loop | FHP | CF007-1VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224478 | Ground Loop | FHP | CF007-1VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224479 | Ground Loop | FHP | CF009-1VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
215224480 | Ground Loop | FHP | CF009-1VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
215224481 | Ground Loop | FHP | CF012-1VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224482 | Ground Loop | FHP | CF012-1VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224483 | Ground Loop | FHP | CF015-1VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083
215224484 | Ground Loop | FHP | CF015-1VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917
215224485 | Ground Loop | FHP | CF018-1VT/HZC-*****A |  | 20000 | 18 | 14200 | 3.6 | 1.6667
215224486 | Ground Loop | FHP | CF018-1VT/HZN-*****A |  | 19700 | 18 | 14200 | 3.6 | 1.6417
215224487 | Ground Loop | FHP | CF007-2VT/HZC-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224488 | Ground Loop | FHP | CF007-2VT/HZN-*****A |  | 7400 | 18.5 | 5000 | 3.6 | 0.61667
215224489 | Ground Loop | FHP | CF009-2VT/HZC-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
215224490 | Ground Loop | FHP | CF009-2VT/HZN-*****A |  | 9200 | 17.5 | 6500 | 3.6 | 0.76667
215224491 | Ground Loop | FHP | CF012-2VT/HZC-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224492 | Ground Loop | FHP | CF012-2VT/HZN-*****A |  | 12500 | 17.5 | 9000 | 3.6 | 1.0417
215224493 | Ground Loop | FHP | CF015-2VT/HZC-*****A |  | 15700 | 18 | 11000 | 3.6 | 1.3083
215224494 | Ground Loop | FHP | CF015-2VT/HZN-*****A |  | 15500 | 17.5 | 11000 | 3.6 | 1.2917
203383902 | Ground Loop | FHP | EP048-1VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
203383903 | Ground Loop | FHP | EP048-3VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
203383904 | Ground Loop | FHP | EP048-4VT*******B |  | 46800 | 17.75 | 33400 | 3.7 | 3.9
203383905 | Ground Loop | FHP | EP048-1HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203383906 | Ground Loop | FHP | EP048-3HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203383907 | Ground Loop | FHP | EP048-4HZ*******B |  | 46800 | 17.8 | 33400 | 3.7 | 3.9
203459712 | Ground Loop | BOSCH-GEO | LM036-1CSC-*****B | LM036-1AH*-*****B | 37900 | 17.15 | 27400 | 3.8 | 3.1583
203459725 | Ground Loop | FHP | LM036-1CSC-*****B | LM036-1AH*-*****B | 37900 | 17.15 | 27400 | 3.8 | 3.1583
203459750 | Ground Loop | BOSCH | LM024-1CS*-*****A | LM024-1AV/AH*****A*A | 26200 | 17 | 17700 | 3.75 | 2.1833
203459757 | Ground Loop | FHP | LM024-1CS*-*****A | LM024-1AV/AH*****A*A | 26200 | 17 | 17700 | 3.75 | 2.1833
203466717 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ049J1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
203471325 | Ground Loop | 5 SERIES INDOOR SPLITS | NDZ049J1 | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
203490411 | Ground Loop | GeoSmart Energy | GTZ049*1*J | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
203490420 | Ground Loop | GeoSmart Energy | GTZ049*1*J | SRAA048* | 46300 | 18 | 37700 | 3.9 | 3.8583
203495469 | Ground Loop | GEOSTAR | 101/102J049**1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333
203495470 | Ground Loop | GEOSTAR | 103J049**1 | SAH048* | 46300 | 18 | 37700 | 3.9 | 3.8583
212505509 | Ground Loop | HYDROTECH | WSH6036AM* |  | 36500 | 18 | 27000 | 3.6 | 3.0417
212505510 | Ground Loop | HYDROTECH | WSH6042AM* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833
212505511 | Ground Loop | HYDROTECH | WSH6048AM* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125
212505512 | Ground Loop | AE Air | WSH6024AM* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083
212505513 | Ground Loop | AE Air | WSH6036AM* |  | 36500 | 18 | 27000 | 3.6 | 3.0417
212505514 | Ground Loop | AE Air | WSH6042AM* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833
212505515 | Ground Loop | AE Air | WSH6048AM* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125
212508378 | Ground Loop | HYDROTECH | WSH6024AN* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083
212508380 | Ground Loop | HYDROTECH | WSH6030AN* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5
212508382 | Ground Loop | HYDROTECH | WSH6036AN* |  | 36500 | 18 | 27000 | 3.6 | 3.0417
212508384 | Ground Loop | HYDROTECH | WSH6042AN* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833
212508386 | Ground Loop | HYDROTECH | WSH6048AN* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125
212508387 | Ground Loop | HYDROTECH | WSH6060AM* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083
212508388 | Ground Loop | HYDROTECH | WSH6060AN* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083
212508389 | Ground Loop | HYDROTECH | WSH6072AM* |  | 72000 | 17.1 | 55000 | 3.6 | 6
212508390 | Ground Loop | HYDROTECH | WSH6072AN* |  | 72000 | 17.1 | 55000 | 3.6 | 6
212508395 | Ground Loop | AE Air | WSH6024AN* |  | 26500 | 18.4 | 18500 | 3.6 | 2.2083
212508397 | Ground Loop | AE Air | WSH6030AN* |  | 30000 | 18.4 | 21000 | 3.6 | 2.5
212508399 | Ground Loop | AE Air | WSH6036AN* |  | 36500 | 18 | 27000 | 3.6 | 3.0417
212508401 | Ground Loop | AE Air | WSH6042AN* |  | 43000 | 18.5 | 31500 | 3.8 | 3.5833
212508403 | Ground Loop | AE Air | WSH6048AN* |  | 49500 | 18.1 | 36000 | 3.6 | 4.125
212508404 | Ground Loop | AE Air | WSH6072AM* |  | 72000 | 17.1 | 55000 | 3.6 | 6
212508405 | Ground Loop | AE Air | WSH6072AN* |  | 72000 | 17.1 | 55000 | 3.6 | 6
212509300 | Ground Loop | AE Air | WSH6060AM* |  | 62500 | 18.1 | 45000 | 3.6 | 5.2083
206438813 | Ground Loop | FHP | EP012-1VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438814 | Ground Loop | FHP | EP012-1HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438817 | Ground Loop | FHP | EP012-0VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438818 | Ground Loop | FHP | EP012-2VTC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438819 | Ground Loop | FHP | EP012-0HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
206438820 | Ground Loop | FHP | EP012-2HZC-*****B |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
216726189 | Ground Loop | DAIKIN | WSRC007*E*G/J |  | 7100 | 19.4 | 4700 | 3.6 | 0.59167
217351919 | Ground Loop | TEMPSTAR | HS024SR*C******1 | F(C,T)MA5*36**** | 26000 | 18.5 | 18800 | 4.1 | 2.1667
217351920 | Ground Loop | TEMPSTAR | HS024SR*N******1 | F(C,T)MA5*36**** | 25400 | 18.1 | 18400 | 4 | 2.1167
217351923 | Ground Loop | TEMPSTAR | HS036SR*C******1 | F(C,T)MA5*48**** | 39000 | 18.5 | 27400 | 3.7 | 3.25
217351924 | Ground Loop | TEMPSTAR | HS036SR*N******1 | F(C,T)MA5*48**** | 38000 | 18.1 | 26800 | 3.7 | 3.1667
217351925 | Ground Loop | TEMPSTAR | HS048SR*C******1 | F(C,T)MA5*48**** | 48500 | 17.1 | 37800 | 4 | 4.0417
217351927 | Ground Loop | TEMPSTAR | HS060SR*C******1 | F(C,T)MA5*60**** | 60500 | 17.6 | 47000 | 3.7 | 5.0417
217351928 | Ground Loop | TEMPSTAR | HS060SR*N******1 | F(C,T)MA5*60**** | 59500 | 17.3 | 46000 | 3.7 | 4.9583
217351930 | Ground Loop | TEMPSTAR | HS024SR*C******1 | EAM5*2*M*** | 25900 | 17.5 | 18900 | 3.8 | 2.1583
217351931 | Ground Loop | TEMPSTAR | HS024SR*N******1 | EAM5*2*M*** | 25400 | 17.1 | 18500 | 3.7 | 2.1167
217351932 | Ground Loop | TEMPSTAR | HS036SR*C******1 | EAM5*3*M*** | 37400 | 17.7 | 27600 | 3.6 | 3.1167
217351933 | Ground Loop | TEMPSTAR | HS036SR*N******1 | EAM5*3*M*** | 36600 | 17.4 | 27100 | 3.6 | 3.05
217351934 | Ground Loop | TEMPSTAR | HS048SR*C******1 | EAM5*4*M*** | 49000 | 17.1 | 37900 | 3.9 | 4.0833
217351936 | Ground Loop | TEMPSTAR | HS060SR*C******1 | EAM5*6*M*** | 63900 | 17.7 | 48300 | 3.8 | 5.325
217351937 | Ground Loop | TEMPSTAR | HS060SR*N******1 | EAM5*6*M*** | 62600 | 17.3 | 47300 | 3.7 | 5.2167
217351938 | Ground Loop | TEMPSTAR | HS072SR*C******1 | EAM5*6*M*** | 70000 | 17.5 | 55200 | 3.6 | 5.8333
8332268 | Ground Loop | GEOCOMFORT | GYT024 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583
8332358 | Ground Loop | HYDRON MODULE | HYT024 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583
8332380 | Ground Loop | TETCO | TYT024 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583
8332431 | Ground Loop | GEOCOMFORT | GYT024*2 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583
8332452 | Ground Loop | HYDRON MODULE | HYT024*2 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583
8332472 | Ground Loop | TETCO | TYT024*2 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583
8332525 | Ground Loop | GEOCOMFORT | GYT024*3 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583
8332545 | Ground Loop | HYDRON MODULE | HYT024*3 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583
8332563 | Ground Loop | TETCO | TYT024*3 |  | 27100 | 19.9 | 19000 | 4.3 | 2.2583
8560797 | Ground Loop | 5 SERIES | NSV/NSH060H1*0 |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
8560805 | Ground Loop | 5 SERIES | NSV/NSH060H1*(1,4) |  | 62200 | 18.4 | 47900 | 4 | 5.1833
8560913 | Ground Loop | GEOCOMFORT | GVS009 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833
8560914 | Ground Loop | HYDRON MODULE | HVS009 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833
8560915 | Ground Loop | TETCO | TVS009 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833
8560916 | Ground Loop | GEOCOMFORT | GVS009*A |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833
8560917 | Ground Loop | HYDRON MODULE | HVS009*A |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833
8560918 | Ground Loop | TETCO | TVS009*A |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833
8560919 | Ground Loop | GEOCOMFORT | GVS009*9 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833
8560920 | Ground Loop | HYDRON MODULE | HVS009*9 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833
8560921 | Ground Loop | TETCO | TVS009*9 |  | 10900 | 17.4 | 8500 | 3.6 | 0.90833
8560930 | Ground Loop | GEOCOMFORT | GVS012 |  | 11900 | 18.1 | 9400 | 3.6 | 0.99167
8560931 | Ground Loop | HYDRON MODULE | HVS012 |  | 11900 | 18.1 | 9400 | 3.6 | 0.99167
8560932 | Ground Loop | TETCO | TVS012 |  | 11900 | 18.1 | 9400 | 3.6 | 0.99167
8560938 | Ground Loop | GEOCOMFORT | GVS015 |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333
8560939 | Ground Loop | HYDRON MODULE | HVS015 |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333
8560940 | Ground Loop | TETCO | TVS015 |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333
8560941 | Ground Loop | GEOCOMFORT | GVS015*A |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333
8560942 | Ground Loop | HYDRON MODULE | HVS015*A |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333
8560943 | Ground Loop | TETCO | TVS015*A |  | 16000 | 19.8 | 11600 | 4.1 | 1.3333
8560946 | Ground Loop | GEOCOMFORT | GVS015*****1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333
8560947 | Ground Loop | HYDRON MODULE | HVS015*****1 |  | 16000 | 22.3 | 11500 | 4.3 | 1.3333
205993181 | Ground Loop | TETCO | TBT060 | TAD060 | 61100 | 18.2 | 46800 | 3.8 | 5.0917
205993182 | Ground Loop | GEOCOMFORT | GBT060*2 | GAD060 | 61100 | 18.2 | 46800 | 3.8 | 5.0917
205993183 | Ground Loop | HYDRON MODULE | HBT060*2 | HAD060 | 61100 | 18.2 | 46800 | 3.8 | 5.0917
10447650 | Ground Loop | RHEEM | RPVS/EC025 | RCFL-HM2621 | 26000 | 18 | 18600 | 3.8 | 2.1667
10447662 | Ground Loop | RHEEM | RPVS/EC036 | RCFL-HM38** | 38000 | 17.3 | 26600 | 3.7 | 3.1667
10581108 | Ground Loop | 5 SERIES | NDP026H1*1 |  | 24800 | 17.9 | 19300 | 3.9 | 2.0667
10581109 | Ground Loop | 5 SERIES | NDP038H1*(1,2) |  | 38200 | 19.7 | 28300 | 4.1 | 3.1833
10581110 | Ground Loop | 5 SERIES | NDP049H1*1 |  | 50400 | 19 | 38000 | 4 | 4.2
204031802 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT049**1*(1,2,4)*J |  | 50800 | 19.3 | 38200 | 4 | 4.2333
204031808 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS048**1*(1,2,4)*J |  | 45900 | 18.8 | 36400 | 4 | 3.825
4219442 | Ground Loop | NORDIC | RS25HACW-P-1T-* | AH-25-P-1-***** | 24800 | 17 | 18300 | 3.6 | 2.0667
4230439 | Ground Loop | DAIKIN | WCCW4015*E*04* |  | 17200 | 20.8 | 11500 | 4 | 1.4333
203363320 | Ground Loop | WILLIAMS | EW009H1D*A |  | 24000 | 17.1 | 17000 | 3.8 | 2
202391445 | Ground Loop | CARRIER | 50PSV012**C3/CA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
202391446 | Ground Loop | CARRIER | 50PSH012**C3/CA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
202391449 | Ground Loop | CARRIER | 50PSV012**C0/BA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
202391450 | Ground Loop | CARRIER | 50PSV012**C4/DA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
202391451 | Ground Loop | CARRIER | 50PSH012**C0/BA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
7499460 | Ground Loop | FHP | EP024-1HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
7499461 | Ground Loop | FHP | EP024-2HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
7499463 | Ground Loop | FHP | EP024-3HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
7499464 | Ground Loop | FHP | EP024-4HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
7499465 | Ground Loop | FHP | EP030-1HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
7499466 | Ground Loop | FHP | EP030-2HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
7499467 | Ground Loop | FHP | EP030-3HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
202330327 | Ground Loop | AAON, Inc. | WH-048-2-H-ACAC-C0-10-200-A |  | 54100 | 18.7 | 43100 | 4 | 4.5083
202330328 | Ground Loop | AAON, Inc. | WH-048-3-H-ACAC-C0-10-200-A |  | 54100 | 18.7 | 43100 | 4 | 4.5083
202330339 | Ground Loop | AAON, Inc. | WH-036-A-H-DCAC-C0-10-200-A |  | 36800 | 17.3 | 27600 | 3.7 | 3.0667
5615038 | Ground Loop | DAIKIN | WCCW5030*E*04* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333
5615039 | Ground Loop | DAIKIN | WCCW5030*F*04* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333
5615040 | Ground Loop | DAIKIN | WCCW5030*J*04* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333
5615041 | Ground Loop | DAIKIN | WCCW5030*K*04* |  | 31600 | 18.4 | 23000 | 3.8 | 2.6333
5615046 | Ground Loop | DAIKIN | WCCW5036*E*04* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667
5615047 | Ground Loop | DAIKIN | WCCW5036*F*04* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667
5615048 | Ground Loop | DAIKIN | WCCW5036*J*04* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667
207178494 | Ground Loop | GEOSTAR | 161/162J049**1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207178526 | Ground Loop | GEOSTAR | 161/162H026**1*(1,4)***** |  | 26400 | 19.6 | 19500 | 4 | 2.2
207178527 | Ground Loop | GEOSTAR | 161/162J038**1*(1,2,4)***** |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
5317927 | Ground Loop | GEOCOMFORT | GRT048A | MPD060 | 50700 | 18 | 34200 | 3.7 | 4.225
205288519 | Ground Loop | BARD | QW2S3DA |  | 25000 | 17.2 | 19800 | 3.7 | 2.0833
5296250 | Ground Loop | TRANE | EXVF0301 |  | 29200 | 19.3 | 20900 | 3.9 | 2.4333
5296251 | Ground Loop | TRANE | EXVF0302 |  | 29200 | 19.3 | 20900 | 3.9 | 2.4333
5296252 | Ground Loop | TRANE | EXVF0307 |  | 29200 | 19.3 | 20900 | 3.9 | 2.4333
10268252 | Ground Loop | TETCO | TBT048 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333
10268253 | Ground Loop | GEOCOMFORT | GBT048*2 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333
10268254 | Ground Loop | HYDRON MODULE | HBT048*2 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333
10268255 | Ground Loop | TETCO | TBT048*2 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333
10268260 | Ground Loop | GEOCOMFORT | GBT060 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917
10268261 | Ground Loop | HYDRON MODULE | HBT060 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917
10268262 | Ground Loop | TETCO | TBT060 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917
202443468 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS036**1*(1,2,4)*J |  | 33700 | 22 | 24400 | 4.2 | 2.8083
202443469 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS042**1*(1,2,4)*J |  | 40700 | 21.7 | 28900 | 4 | 3.3917
8786547 | Ground Loop | GEOSTAR | 101/102H072**1*(1,4)***** |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
8786548 | Ground Loop | GeoSmart Energy | GT072**1*(1,4)********H |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
8786549 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT072**1*(1,4)****H |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
8786557 | Ground Loop | GEOSTAR | 101/102H018**1*(1,4)***** |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
8103479 | Ground Loop | TRANE | DXHF0241 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578
8105907 | Ground Loop | TRANE | DXHF0242 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578
8105909 | Ground Loop | TRANE | DXHF0243 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578
8105911 | Ground Loop | TRANE | DXHF0244 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578
8105912 | Ground Loop | TRANE | DXHF0247 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578
202350414 | Ground Loop | AAON, Inc. | RN-009-2-0-ACAY-C0-10-000-A |  | 105100 | 19.4 | 75000 | 3.9 | 8.7583
202350415 | Ground Loop | AAON, Inc. | RN-009-3-0-ACAY-C0-10-000-A |  | 105100 | 19.4 | 75000 | 3.9 | 8.7583
202350416 | Ground Loop | AAON, Inc. | RN-009-4-0-ACAY-C0-10-000-A |  | 105100 | 19.4 | 75000 | 3.9 | 8.7583
202330407 | Ground Loop | AAON, Inc. | WV-048-2-H-ACAC-C0-10-200-A |  | 50500 | 19 | 40100 | 3.7 | 4.2083
202330408 | Ground Loop | AAON, Inc. | WV-048-3-H-ACAC-C0-10-200-A |  | 50500 | 19 | 40100 | 3.7 | 4.2083
202330418 | Ground Loop | AAON, Inc. | WV-024-A-H-DCAC-C0-10-D00-A |  | 26900 | 18.1 | 16700 | 3.82 | 2.2417
202330284 | Ground Loop | AAON, Inc. | WH-018-A-H-ACAC-C0-10-200-A |  | 17300 | 19.2 | 13300 | 4.7 | 1.4417
6581203 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS022**1*(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917
202330271 | Ground Loop | AAON, Inc. | WH-009-B-H-ACAC-C0-10-200-A |  | 9300 | 17.3 | 7750 | 3.8 | 0.775
202330272 | Ground Loop | AAON, Inc. | WH-009-1-H-ACAC-C0-10-200-A |  | 9300 | 17.3 | 7750 | 3.8 | 0.775
202330273 | Ground Loop | AAON, Inc. | WH-009-A-H-ACAC-C0-10-200-A |  | 9300 | 17.3 | 7750 | 3.8 | 0.775
4230441 | Ground Loop | DAIKIN | WCCW4015*J*04* |  | 16800 | 20.8 | 11500 | 3.8 | 1.4
4230746 | Ground Loop | DAIKIN | WCCW4019*E*04* |  | 22600 | 18.4 | 14800 | 3.8 | 1.8833
4230748 | Ground Loop | DAIKIN | WCCW4019*J*04* |  | 22600 | 18.4 | 14800 | 3.8 | 1.8833
4230750 | Ground Loop | DAIKIN | WCCW4024*E*04* |  | 25200 | 17 | 17200 | 3.7 | 2.1
4230752 | Ground Loop | DAIKIN | WCCW4024*F*04* |  | 25200 | 17 | 17200 | 3.7 | 2.1
4230754 | Ground Loop | DAIKIN | WCCW4024*J*04* |  | 25200 | 17 | 17200 | 3.7 | 2.1
4231098 | Ground Loop | DAIKIN | WCCW4024*K*04* |  | 25200 | 17 | 17200 | 3.7 | 2.1
202391437 | Ground Loop | FHP | EP012-2HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
8105979 | Ground Loop | TRANE | DXVF0602 |  | 62100 | 18.2 | 51100 | 4 | 5.175
8105980 | Ground Loop | TRANE | DXVF0603 |  | 62100 | 18.2 | 51100 | 4 | 5.175
8105981 | Ground Loop | TRANE | DXVF0604 |  | 62100 | 18.2 | 51100 | 4 | 5.175
8105982 | Ground Loop | TRANE | DXVF0608 |  | 62100 | 18.2 | 51100 | 4 | 5.175
8105983 | Ground Loop | TRANE | DXVF0701 |  | 70700 | 17.8 | 58500 | 3.9 | 5.8917
8105984 | Ground Loop | TRANE | DXVF0702 |  | 70700 | 17.8 | 58500 | 3.9 | 5.8917
8105985 | Ground Loop | TRANE | DXVF0703 |  | 70700 | 17.8 | 58500 | 3.9 | 5.8917
202350506 | Ground Loop | AAON, Inc. | WH-036-1-H-DCAC-C0-10-200-A |  | 36800 | 17.3 | 27600 | 3.7 | 3.0667
202350507 | Ground Loop | AAON, Inc. | WH-036-2-H-DCAC-C0-10-200-A |  | 36800 | 17.3 | 27600 | 3.7 | 3.0667
202350510 | Ground Loop | AAON, Inc. | WH-048-1-H-DCAC-C0-10-200-A |  | 50000 | 18.4 | 40100 | 3.9 | 4.1667
202350511 | Ground Loop | AAON, Inc. | WH-048-2-H-DCAC-C0-10-200-A |  | 50000 | 18.4 | 40100 | 3.9 | 4.1667
5696567 | Ground Loop | 5 SERIES | NSV/NSH022G1*(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917
5708463 | Ground Loop | AMERICAN STANDARD | A1GX022***1**(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917
5708493 | Ground Loop | TRANE/AMERICAN STANDARD | T1GX022***1**(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917
5708550 | Ground Loop | GEOSTAR | 101/102A022**1*(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917
5708623 | Ground Loop | GeoSmart Energy | GS022**1*(0,3) |  | 21500 | 20.5 | 14200 | 3.7 | 1.7917
5731224 | Ground Loop | BARD | GTC36S2-A | GTA3600UD1AA+GTB1-A | 38400 | 17.3 | 29600 | 4 | 3.2
5343160 | Ground Loop | DAIKIN | WVFW1042*E***04 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417
5343161 | Ground Loop | DAIKIN | WVFW1042*F***04 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417
5343172 | Ground Loop | DAIKIN | WVFW1048*F***04 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833
5343173 | Ground Loop | DAIKIN | WVFW1048*K***04 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833
5296259 | Ground Loop | TRANE | EXVF0421 |  | 43200 | 18.5 | 31700 | 3.89 | 3.6
5296260 | Ground Loop | TRANE | EXVF0422 |  | 43200 | 18.5 | 31700 | 3.89 | 3.6
5296261 | Ground Loop | TRANE | EXVF0423 |  | 43200 | 18.5 | 31700 | 3.89 | 3.6
5296262 | Ground Loop | TRANE | EXVF0424 |  | 43200 | 18.5 | 31700 | 3.89 | 3.6
5296263 | Ground Loop | TRANE | EXVF0488 |  | 47900 | 18.5 | 36200 | 3.96 | 3.9917
5295943 | Ground Loop | TRANE | EXHF0241 |  | 24700 | 18 | 17900 | 3.6 | 2.0583
5295946 | Ground Loop | TRANE | EXHF0242 |  | 24700 | 18 | 17900 | 3.6 | 2.0583
5295949 | Ground Loop | TRANE | EXHF0247 |  | 24700 | 18 | 17900 | 3.6 | 2.0583
203363069 | Ground Loop | WILLIAMS | EW010A1D*A |  | 31000 | 18.2 | 20800 | 3.8 | 2.5833
202391438 | Ground Loop | FHP | EP012-0HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
202391439 | Ground Loop | FHP | EP012-2VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
202391440 | Ground Loop | FHP | EP012-0VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
202391443 | Ground Loop | FHP | EP012-1HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
202391444 | Ground Loop | FHP | EP012-1VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
8106144 | Ground Loop | TRANE | DXVF0704 |  | 70700 | 17.8 | 58500 | 3.9 | 5.8917
8106145 | Ground Loop | TRANE | DXVF0708 |  | 70700 | 17.8 | 58500 | 3.9 | 5.8917
8247563 | Ground Loop | TRANE | DXHF0601 |  | 60500 | 17.2 | 50300 | 3.7 | 5.0417
8247564 | Ground Loop | TRANE | DXHF0602 |  | 60500 | 17.2 | 50300 | 3.7 | 5.0417
8247571 | Ground Loop | TRANE | DXHF0603 |  | 60500 | 17.2 | 50300 | 3.7 | 5.0417
8247572 | Ground Loop | TRANE | DXHF0604 |  | 60500 | 17.2 | 50300 | 3.7 | 5.0417
8247573 | Ground Loop | TRANE | DXHF0608 |  | 60500 | 17.2 | 50300 | 3.7 | 5.0417
214813290 | Ground Loop | ARCADIAN | AVHP-10-G |  | 31947 | 17.27 | 21202 | 3.62 | 2.6622
202330573 | Ground Loop | AAON, Inc. | WH-006-B-H-ACAC-C0-10-200-A |  | 6400 | 17.2 | 4600 | 3.6 | 0.53333
202330574 | Ground Loop | AAON, Inc. | WH-006-1-H-ACAC-C0-10-200-A |  | 6400 | 17.2 | 4600 | 3.6 | 0.53333
202330575 | Ground Loop | AAON, Inc. | WH-006-A-H-ACAC-C0-10-200-A |  | 6400 | 17.2 | 4600 | 3.6 | 0.53333
202330576 | Ground Loop | AAON, Inc. | WV-006-B-H-ACAC-C0-10-200-A |  | 6300 | 18.2 | 5200 | 4.1 | 0.525
202330391 | Ground Loop | AAON, Inc. | WV-036-2-H-ACAC-C0-10-200-A |  | 36600 | 17.3 | 27400 | 3.6 | 3.05
202330392 | Ground Loop | AAON, Inc. | WV-036-3-H-ACAC-C0-10-200-A |  | 36600 | 17.3 | 27400 | 3.6 | 3.05
9951968 | Ground Loop | BARD | GV27S3AA |  | 26600 | 18.1 | 20200 | 4.1 | 2.2167
9951969 | Ground Loop | BARD | GV38S3AA |  | 38500 | 17.1 | 31400 | 4.05 | 3.2083
9951970 | Ground Loop | BARD | GV51S3AA |  | 49500 | 17.1 | 39500 | 3.75 | 4.125
202901193 | Ground Loop | WHALEN | VD-A-0801-*DA |  | 24500 | 17.5 | 17000 | 4 | 2.0417
8789586 | Ground Loop | GEOSTAR | 101/102H022**1*(1,4)***** |  | 19200 | 18.7 | 15500 | 4 | 1.6
8789591 | Ground Loop | GEOSTAR | 101/102H030**1*(0,3)***** |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
8789592 | Ground Loop | GeoSmart Energy | GS030**1*(0,3)********H |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
8789593 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(0,3)****H |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
8789596 | Ground Loop | GEOSTAR | 101/102H030**1*(1,4)***** |  | 28100 | 22 | 20500 | 3.9 | 2.3417
8789597 | Ground Loop | GeoSmart Energy | GS030**1*(1,4)********H |  | 28100 | 22 | 20500 | 3.9 | 2.3417
8105913 | Ground Loop | TRANE | DXHF0248 |  | 25893 | 17.58 | 18700 | 3.8 | 2.1578
202350426 | Ground Loop | AAON, Inc. | RN-011-2-0-ACAY-C0-10-000-A |  | 129300 | 17.5 | 95400 | 3.6 | 10.775
202350427 | Ground Loop | AAON, Inc. | RN-011-3-0-ACAY-C0-10-000-A |  | 129300 | 17.5 | 95400 | 3.6 | 10.775
202350428 | Ground Loop | AAON, Inc. | RN-011-4-0-ACAY-C0-10-000-A |  | 129300 | 17.5 | 95400 | 3.6 | 10.775
202330422 | Ground Loop | AAON, Inc. | WV-036-A-H-DCAC-C0-10-200-A |  | 38400 | 18.3 | 25600 | 3.6 | 3.2
202330424 | Ground Loop | AAON, Inc. | WV-036-3-H-DCAC-C0-10-200-A |  | 38400 | 18.3 | 25600 | 3.6 | 3.2
202330387 | Ground Loop | AAON, Inc. | WV-036-1-H-ACAC-C0-10-200-A |  | 36600 | 17.3 | 27400 | 3.6 | 3.05
202330388 | Ground Loop | AAON, Inc. | WV-036-A-H-ACAC-C0-10-200-A |  | 36600 | 17.3 | 27400 | 3.6 | 3.05
202330305 | Ground Loop | AAON, Inc. | WH-036-1-H-ACAC-C0-10-100-A |  | 37000 | 17 | 27600 | 3.7 | 3.0833
202330306 | Ground Loop | AAON, Inc. | WH-036-A-H-ACAC-C0-10-100-A |  | 37000 | 17 | 27600 | 3.7 | 3.0833
202330307 | Ground Loop | AAON, Inc. | WH-036-1-H-ACAC-C0-10-200-A |  | 38000 | 18.5 | 29800 | 4.1 | 3.1667
202330308 | Ground Loop | AAON, Inc. | WH-036-A-H-ACAC-C0-10-200-A |  | 38000 | 18.5 | 29800 | 4.1 | 3.1667
202330309 | Ground Loop | AAON, Inc. | WH-036-2-H-ACAC-C0-10-100-A |  | 37000 | 17 | 27600 | 3.7 | 3.0833
202330310 | Ground Loop | AAON, Inc. | WH-036-3-H-ACAC-C0-10-100-A |  | 37000 | 17 | 27600 | 3.7 | 3.0833
202330311 | Ground Loop | AAON, Inc. | WH-036-2-H-ACAC-C0-10-200-A |  | 38000 | 18.5 | 29800 | 4.1 | 3.1667
5615068 | Ground Loop | DAIKIN | WCCW5060*E*04* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417
5615069 | Ground Loop | DAIKIN | WCCW5060*F*04* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417
5615070 | Ground Loop | DAIKIN | WCCW5060*K*04* |  | 61700 | 17.9 | 48000 | 3.9 | 5.1417
5341546 | Ground Loop | DAIKIN | WVFW1019*E***04 |  | 19700 | 19 | 13400 | 3.7 | 1.6417
5341628 | Ground Loop | DAIKIN | WVFW1019*J***04 |  | 19700 | 19 | 13400 | 3.7 | 1.6417
205993156 | Ground Loop | GEOCOMFORT | GBT024 | GAD024 | 26300 | 20.4 | 18800 | 3.9 | 2.1917
205993157 | Ground Loop | HYDRON MODULE | HBT024 | HED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333
205993158 | Ground Loop | HYDRON MODULE | HBT024 | HAD024 | 26300 | 20.4 | 18800 | 3.9 | 2.1917
9850157 | Ground Loop | DAIKIN | WVFW1024*K***04 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917
9850202 | Ground Loop | DAIKIN | WVFW1030*K***04 |  | 30600 | 19.3 | 22300 | 4 | 2.55
203363090 | Ground Loop | WILLIAMS | EW010H1D*A |  | 31000 | 18.2 | 20800 | 3.8 | 2.5833
214855068 | Ground Loop | WHALEN | CASH*036AD**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
214855069 | Ground Loop | WHALEN | CASH*036AJ**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
214855070 | Ground Loop | WHALEN | CASH*036AM**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
214855071 | Ground Loop | WHALEN | CASV*036AB**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
214855072 | Ground Loop | WHALEN | CASV*036AD**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
214855073 | Ground Loop | WHALEN | CASV*036AJ**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
214855074 | Ground Loop | WHALEN | CASV*036AM**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
7499468 | Ground Loop | FHP | EP030-4HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
7499480 | Ground Loop | FHP | EP060-1HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
7499482 | Ground Loop | FHP | EP060-3HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
7499483 | Ground Loop | FHP | EP060-4HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
7499484 | Ground Loop | FHP | EP070-1HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
7499485 | Ground Loop | FHP | EP070-3HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
7499487 | Ground Loop | FHP | EP070-4HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
214855061 | Ground Loop | WHALEN | CASH*030AJ**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
214855062 | Ground Loop | WHALEN | CASH*030AM**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
214855063 | Ground Loop | WHALEN | CASV*030AB**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
214855064 | Ground Loop | WHALEN | CASV*030AD**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
214855065 | Ground Loop | WHALEN | CASV*030AJ**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
214855066 | Ground Loop | WHALEN | CASV*030AM**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
214855067 | Ground Loop | WHALEN | CASH*036AB**B**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
207699056 | Ground Loop | UNILUX VHP | UVHP-05-G |  | 15724 | 17.2 | 11705 | 3.61 | 1.3103
207699057 | Ground Loop | UNILUX VHP | UVHP-06-G |  | 19621 | 17.3 | 15106 | 3.62 | 1.6351
207699058 | Ground Loop | UNILUX VHP | UVHP-08-G |  | 26613 | 17.38 | 18707 | 3.61 | 2.2178
207699059 | Ground Loop | UNILUX VHP | UVHP-10-G |  | 31947 | 17.27 | 21202 | 3.62 | 2.6622
207200555 | Ground Loop | GeoSmart Energy | GT072**1*(1,4)*H |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207200556 | Ground Loop | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
207200557 | Ground Loop | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 50800 | 19.3 | 38200 | 4 | 4.2333
207200560 | Ground Loop | GeoSmart Energy | GS018**1*(1,4)*H |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
206599757 | Ground Loop | 5 SERIES | NSV/NSH060J1*0* |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
205993121 | Ground Loop | HYDRON MODULE | HBS018*2 | HED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417
205993122 | Ground Loop | HYDRON MODULE | HBS018*2 | HAD018 | 22200 | 22.2 | 14400 | 3.9 | 1.85
205993123 | Ground Loop | TETCO | TBS018*2 | TED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417
205993124 | Ground Loop | TETCO | TBS018*2 | TAD018 | 22200 | 22.2 | 14400 | 3.9 | 1.85
205993125 | Ground Loop | GEOCOMFORT | GBT036 | GED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333
205993126 | Ground Loop | GEOCOMFORT | GBT036 | GAD036 | 36900 | 19.3 | 29000 | 3.9 | 3.075
205993127 | Ground Loop | HYDRON MODULE | HBT036 | HED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333
205993139 | Ground Loop | HYDRON MODULE | HBT048 | HED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275
205993140 | Ground Loop | HYDRON MODULE | HBT048 | HAD048 | 50300 | 19.5 | 41000 | 3.9 | 4.1917
205993141 | Ground Loop | TETCO | TBT048 | TED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275
10268263 | Ground Loop | GEOCOMFORT | GBT060*2 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917
10268264 | Ground Loop | HYDRON MODULE | HBT060*2 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917
10268265 | Ground Loop | TETCO | TBT060*2 | MPD060 | 62300 | 17.6 | 45900 | 3.7 | 5.1917
10268268 | Ground Loop | GEOCOMFORT | GBT060 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833
10268269 | Ground Loop | HYDRON MODULE | HBT060 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833
10268270 | Ground Loop | TETCO | TBT060 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833
10268271 | Ground Loop | GEOCOMFORT | GBT060*2 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833
203363068 | Ground Loop | WILLIAMS | EW009A1D*A |  | 24000 | 17.1 | 17000 | 3.8 | 2
202358917 | Ground Loop | DAIKIN | WCCW5024*E*04* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417
202358919 | Ground Loop | DAIKIN | WCCW5024*F*04* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417
202358921 | Ground Loop | DAIKIN | WCCW5024*J*04* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417
202358923 | Ground Loop | DAIKIN | WCCW5024*K*04* |  | 24500 | 17.4 | 17200 | 3.7 | 2.0417
202391369 | Ground Loop | AQUARIUS | EP012-1VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
202391370 | Ground Loop | AQUARIUS | EP012-1HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
8105973 | Ground Loop | TRANE | DXVF0481 |  | 51100 | 19.4 | 39300 | 4.1 | 4.2583
8105974 | Ground Loop | TRANE | DXVF0482 |  | 51100 | 19.4 | 39300 | 4.1 | 4.2583
8105975 | Ground Loop | TRANE | DXVF0483 |  | 51100 | 19.4 | 39300 | 4.1 | 4.2583
8105976 | Ground Loop | TRANE | DXVF0484 |  | 51100 | 19.4 | 39300 | 4.1 | 4.2583
8105977 | Ground Loop | TRANE | DXVF0488 |  | 51100 | 19.4 | 39300 | 4.1 | 4.2583
8105978 | Ground Loop | TRANE | DXVF0601 |  | 62100 | 18.2 | 51100 | 4 | 5.175
202330577 | Ground Loop | AAON, Inc. | WV-006-1-H-ACAC-C0-10-200-A |  | 6300 | 18.2 | 5200 | 4.1 | 0.525
202330578 | Ground Loop | AAON, Inc. | WV-006-A-H-ACAC-C0-10-200-A |  | 6300 | 18.2 | 5200 | 4.1 | 0.525
202330738 | Ground Loop | WHALEN | CASH*024AB**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
202330739 | Ground Loop | WHALEN | CASV*024AB**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
202330740 | Ground Loop | WHALEN | CASH*024AD**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
202330741 | Ground Loop | WHALEN | CASV*024AD**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
202330742 | Ground Loop | WHALEN | CASH*030AB**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
207348743 | Ground Loop | WaterFurnace | URT096*3*5 |  | 91800 | 18.8 | 72800 | 4 | 7.65
207348744 | Ground Loop | WaterFurnace | URT096*4*5 |  | 91800 | 18.8 | 72800 | 4 | 7.65
5677855 | Ground Loop | BARD | QW2S2-A |  | 25600 | 18.2 | 19600 | 3.95 | 2.1333
5677856 | Ground Loop | BARD | QW2S2-B |  | 25600 | 18.2 | 19600 | 3.95 | 2.1333
5677857 | Ground Loop | BARD | QW2S2-C |  | 25600 | 18.2 | 19600 | 3.95 | 2.1333
5343140 | Ground Loop | DAIKIN | WVFW1024*E***04 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917
5343141 | Ground Loop | DAIKIN | WVFW1024*F***04 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917
5343142 | Ground Loop | DAIKIN | WVFW1024*J***04 |  | 25100 | 19.2 | 17500 | 3.8 | 2.0917
8560787 | Ground Loop | 5 SERIES | NSV/NSH030H1*(0,3) |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
8560799 | Ground Loop | 5 SERIES | NSV/NSH018H1*(1,4) |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
8560800 | Ground Loop | 5 SERIES | NSV/NSH022H1*(1,4) |  | 19200 | 18.7 | 15000 | 4 | 1.6
202330277 | Ground Loop | AAON, Inc. | WH-015-1-H-ACAC-C0-10-100-A |  | 14700 | 18.2 | 11100 | 4.8 | 1.225
202330278 | Ground Loop | AAON, Inc. | WH-015-A-H-ACAC-C0-10-100-A |  | 14700 | 18.2 | 11100 | 4.8 | 1.225
202330279 | Ground Loop | AAON, Inc. | WH-015-1-H-ACAC-C0-10-200-A |  | 14700 | 19.9 | 10900 | 5.2 | 1.225
202330280 | Ground Loop | AAON, Inc. | WH-015-A-H-ACAC-C0-10-200-A |  | 14700 | 19.9 | 10900 | 5.2 | 1.225
202330281 | Ground Loop | AAON, Inc. | WH-018-1-H-ACAC-C0-10-100-A |  | 17600 | 17.6 | 13500 | 4.4 | 1.4667
202330282 | Ground Loop | AAON, Inc. | WH-018-A-H-ACAC-C0-10-100-A |  | 17600 | 17.6 | 13500 | 4.4 | 1.4667
202330283 | Ground Loop | AAON, Inc. | WH-018-1-H-ACAC-C0-10-200-A |  | 17300 | 19.2 | 13300 | 4.7 | 1.4417
5932336 | Ground Loop | GEOCOMFORT | GRT048A | MCD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083
5932337 | Ground Loop | HYDRON MODULE | HRT048A | MCD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083
5932338 | Ground Loop | TETCO | TRT048A | MCD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083
5932368 | Ground Loop | GEOCOMFORT | GRT060A | MCD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083
5932380 | Ground Loop | HYDRON MODULE | HRT060A | MCD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083
5932381 | Ground Loop | TETCO | TRT060A | MCD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083
5343215 | Ground Loop | DAIKIN | WVFW1060*E***04 |  | 66000 | 18 | 46000 | 3.8 | 5.5
5343216 | Ground Loop | DAIKIN | WVFW1060*F***04 |  | 66000 | 18 | 46000 | 3.8 | 5.5
5343217 | Ground Loop | DAIKIN | WVFW1060*K***04 |  | 66000 | 18 | 46000 | 3.8 | 5.5
5613676 | Ground Loop | GEOSTAR | 141/142A048**1*1 |  | 46000 | 21.7 | 43000 | 3.6 | 3.8333
5317928 | Ground Loop | HYDRON MODULE | HRT048A | MPD060 | 50700 | 18 | 34200 | 3.7 | 4.225
5317929 | Ground Loop | TETCO | TRT048A | MPD060 | 50700 | 18 | 34200 | 3.7 | 4.225
5317930 | Ground Loop | GEOCOMFORT | GRT048A | ACD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083
5317931 | Ground Loop | HYDRON MODULE | HRT048A | ACD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083
5317932 | Ground Loop | TETCO | TRT048A | ACD060 | 50500 | 17.3 | 36600 | 3.8 | 4.2083
205288520 | Ground Loop | BARD | QW2S3DB |  | 25000 | 17.2 | 19800 | 3.7 | 2.0833
205288643 | Ground Loop | BARD | QW2S3DC |  | 25000 | 17.2 | 19800 | 3.7 | 2.0833
202350515 | Ground Loop | AAON, Inc. | WV-024-1-H-DCAC-C0-10-D00-A |  | 26900 | 18.1 | 16700 | 3.82 | 2.2417
202350519 | Ground Loop | AAON, Inc. | WV-036-1-H-DCAC-C0-10-200-A |  | 38400 | 18.3 | 25600 | 3.6 | 3.2
202350521 | Ground Loop | AAON, Inc. | WV-036-2-H-DCAC-C0-10-200-A |  | 38400 | 18.3 | 25600 | 3.6 | 3.2
7167334 | Ground Loop | CARRIER | 50PSH/V009***3/CA |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167
7167335 | Ground Loop | CARRIER | 50PSH/V009***4/DA |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167
7167337 | Ground Loop | CARRIER | 50PSH/V012***3/CA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
7167338 | Ground Loop | CARRIER | 50PSH/V015***3/CA |  | 16200 | 19.8 | 11000 | 3.63 | 1.35
7167339 | Ground Loop | CARRIER | 50PSH/V015***4/DA |  | 16200 | 19.8 | 11000 | 3.63 | 1.35
7167342 | Ground Loop | CARRIER | 50PSH/V024***3/CA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
5343147 | Ground Loop | DAIKIN | WVFW1030*F***04 |  | 30600 | 19.3 | 22300 | 4 | 2.55
5343148 | Ground Loop | DAIKIN | WVFW1030*J***04 |  | 30600 | 19.3 | 22300 | 4 | 2.55
205993179 | Ground Loop | GEOCOMFORT | GBT060 | GAD060 | 61100 | 18.2 | 46800 | 3.8 | 5.0917
205993180 | Ground Loop | HYDRON MODULE | HBT060 | HAD060 | 61100 | 18.2 | 46800 | 3.8 | 5.0917
202607207 | Ground Loop | WHALEN | VP-A-0814-*DD |  | 24000 | 17.1 | 17000 | 3.8 | 2
202607208 | Ground Loop | WHALEN | VP-A-1004-*DD |  | 31000 | 18.2 | 20800 | 3.8 | 2.5833
8786558 | Ground Loop | GeoSmart Energy | GS018**1*(1,4)********H |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
8786559 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS018**1*(1,4)****H |  | 18500 | 18.3 | 14500 | 3.8 | 1.5417
202330765 | Ground Loop | WHALEN | CASH*024AM**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
202330766 | Ground Loop | WHALEN | CASV*024AM**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
202330767 | Ground Loop | WHALEN | CASH*030AJ**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
202330768 | Ground Loop | WHALEN | CASV*030AJ**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
202330769 | Ground Loop | WHALEN | CASH*030AM**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
202330770 | Ground Loop | WHALEN | CASV*030AM**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
202330771 | Ground Loop | WHALEN | CASH*036AJ**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
7167555 | Ground Loop | CARRIER | 50PSH/V024***5/EA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
7167556 | Ground Loop | CARRIER | 50PSH/V024***6/FA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
202330340 | Ground Loop | AAON, Inc. | WH-036-3-H-DCAC-C0-10-200-A |  | 36800 | 17.3 | 27600 | 3.7 | 3.0667
202330343 | Ground Loop | AAON, Inc. | WH-048-A-H-DCAC-C0-10-200-A |  | 50000 | 18.4 | 40100 | 3.9 | 4.1667
202330344 | Ground Loop | AAON, Inc. | WH-048-3-H-DCAC-C0-10-200-A |  | 50000 | 18.4 | 40100 | 3.9 | 4.1667
202330347 | Ground Loop | AAON, Inc. | WV-009-B-H-ACAC-C0-10-200-A |  | 9800 | 18 | 7800 | 3.9 | 0.81667
202330348 | Ground Loop | AAON, Inc. | WV-009-1-H-ACAC-C0-10-200-A |  | 9800 | 18 | 7800 | 3.9 | 0.81667
6965885 | Ground Loop | TRANE | EXVF0062 |  | 8100 | 17.33 | 6100 | 3.63 | 0.675
6965888 | Ground Loop | TRANE | EXVF0067 |  | 8100 | 17.33 | 6100 | 3.63 | 0.675
6966727 | Ground Loop | TRANE | EXVF0121 |  | 13100 | 18.2 | 9400 | 3.74 | 1.0917
6966753 | Ground Loop | TRANE | EXVF0122 |  | 13100 | 18.2 | 9400 | 3.74 | 1.0917
6580833 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFV048**1*1 |  | 46000 | 21.7 | 43000 | 3.6 | 3.8333
201846902 | Ground Loop | GEOSTAR | 111H038**1*(1,2) |  | 36000 | 18.7 | 27400 | 3.9 | 3
10268279 | Ground Loop | TETCO | TBT060*2 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833
10318053 | Ground Loop | GEOSTAR | 103H060**1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
10443493 | Ground Loop | GEOCOMFORT | GBS018 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675
10443494 | Ground Loop | HYDRON MODULE | HBS018 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675
10443495 | Ground Loop | TETCO | TBS018 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675
10443496 | Ground Loop | GEOCOMFORT | GBS018*2 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675
3920297 | Ground Loop | AQUARIUS | EP030-2HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
3920298 | Ground Loop | AQUARIUS | EP030-4HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
3920299 | Ground Loop | AQUARIUS | EP030-3HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
3920300 | Ground Loop | AQUARIUS | EP030-1HZ/VT |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
3920500 | Ground Loop | AQUARIUS | EP060-4HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
3920501 | Ground Loop | AQUARIUS | EP060-3HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
3920502 | Ground Loop | AQUARIUS | EP060-1HZ/VT |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
203362373 | Ground Loop | WHALEN | VP-H-0814-*DD |  | 24000 | 17.1 | 17000 | 3.8 | 2
203362374 | Ground Loop | WHALEN | VP-H-1004-*DD |  | 31000 | 18.2 | 20800 | 3.8 | 2.5833
8789598 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS030**1*(1,4)****H |  | 28100 | 22 | 20500 | 3.9 | 2.3417
8791888 | Ground Loop | GEOSTAR | 101/102H070**1*(1,4)***** |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
8791889 | Ground Loop | GeoSmart Energy | GS070**1*(1,4)********H |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
8791890 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS070**1*(1,4)****H |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
8105926 | Ground Loop | TRANE | DXHF0481 |  | 53000 | 19.5 | 38800 | 3.9 | 4.4167
8105927 | Ground Loop | TRANE | DXHF0482 |  | 53000 | 19.5 | 38800 | 3.9 | 4.4167
8105928 | Ground Loop | TRANE | DXHF0483 |  | 53000 | 19.5 | 38800 | 3.9 | 4.4167
8105929 | Ground Loop | TRANE | DXHF0484 |  | 53000 | 19.5 | 38800 | 3.9 | 4.4167
8105930 | Ground Loop | TRANE | DXHF0488 |  | 53000 | 19.5 | 38800 | 3.9 | 4.4167
8105931 | Ground Loop | TRANE | DXHF0701 |  | 70400 | 17.6 | 56800 | 3.8 | 5.8667
8105932 | Ground Loop | TRANE | DXHF0702 |  | 70400 | 17.6 | 56800 | 3.8 | 5.8667
202391373 | Ground Loop | AQUARIUS | EP012-0VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
202391374 | Ground Loop | AQUARIUS | EP012-2VTC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
202391375 | Ground Loop | AQUARIUS | EP012-0HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
202391376 | Ground Loop | AQUARIUS | EP012-2HZC |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
8105965 | Ground Loop | TRANE | DXVF0247 |  | 24948 | 17.41 | 19300 | 4 | 2.079
8105966 | Ground Loop | TRANE | DXVF0248 |  | 24948 | 17.41 | 19300 | 4 | 2.079
214855043 | Ground Loop | WHALEN | CASH*015AB**B**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25
214855044 | Ground Loop | WHALEN | CASH*015AD**B**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25
214855045 | Ground Loop | WHALEN | CASV*015AB**B**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25
214855046 | Ground Loop | WHALEN | CASV*015AD**B**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25
207699054 | Ground Loop | UNILUX VHP | UVHP-03-G |  | 9900 | 17.22 | 7452 | 3.65 | 0.825
207699055 | Ground Loop | UNILUX VHP | UVHP-04-G |  | 13040 | 17.32 | 10273 | 3.62 | 1.0867
202330312 | Ground Loop | AAON, Inc. | WH-036-3-H-ACAC-C0-10-200-A |  | 38000 | 18.5 | 29800 | 4.1 | 3.1667
206599760 | Ground Loop | 5 SERIES | NSV/NSH060J1*(1,4)* |  | 62200 | 18.4 | 47900 | 4 | 5.1833
206599762 | Ground Loop | GEOSTAR | 101/102J060**1*0****** |  | 62300 | 17.4 | 46100 | 3.7 | 5.1917
206599765 | Ground Loop | GEOSTAR | 101/102J060**1*(1,4)****** |  | 62200 | 18.4 | 47900 | 4 | 5.1833
205993135 | Ground Loop | TETCO | TBT036*2 | TED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333
205993136 | Ground Loop | TETCO | TBT036*2 | TAD036 | 36900 | 19.3 | 29000 | 3.9 | 3.075
205993137 | Ground Loop | GEOCOMFORT | GBT048 | GED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275
205993138 | Ground Loop | GEOCOMFORT | GBT048 | GAD048 | 50300 | 19.5 | 41000 | 3.9 | 4.1917
205782568 | Ground Loop | YORK BY JOHNSON CONTROLS | YACT049**1*(1,2)* |  | 47700 | 18.2 | 38000 | 3.8 | 3.975
205782570 | Ground Loop | YORK BY JOHNSON CONTROLS | YACT072**1*1* |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083
205782572 | Ground Loop | GeoSmart Energy | QT049**1*(1,2)* |  | 47700 | 18.2 | 38000 | 3.8 | 3.975
205782574 | Ground Loop | GeoSmart Energy | QT072**1*1* |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083
205993113 | Ground Loop | GEOCOMFORT | GBS018 | GED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417
10268203 | Ground Loop | TETCO | TBT036*2 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825
10268204 | Ground Loop | GEOCOMFORT | GBT036 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825
10268205 | Ground Loop | HYDRON MODULE | HBT036 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825
10268206 | Ground Loop | TETCO | TBT036 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825
10268207 | Ground Loop | GEOCOMFORT | GBT036*2 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825
10268208 | Ground Loop | HYDRON MODULE | HBT036*2 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825
10268209 | Ground Loop | TETCO | TBT036*2 | ACD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825
202443457 | Ground Loop | GeoSmart Energy | GT038**1*(1,2,4)*J |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
202443458 | Ground Loop | GeoSmart Energy | GS036**1*(0,3)*J |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
202443459 | Ground Loop | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 33700 | 22 | 24400 | 4.2 | 2.8083
202443460 | Ground Loop | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 40700 | 21.7 | 28900 | 4 | 3.3917
202443465 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT038**1*(1,2,4)*J |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
202443466 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFS036**1*(0,3)*J |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
8786527 | Ground Loop | GEOSTAR | 101/102H026**1*(1,4)***** |  | 26400 | 19.6 | 19500 | 4 | 2.2
8786528 | Ground Loop | GeoSmart Energy | GT026**1*(1,4)********H |  | 26400 | 19.6 | 19500 | 4 | 2.2
8786529 | Ground Loop | YORK BY JOHNSON CONTROLS | YAFT026**1*(1,4)****H |  | 26400 | 19.6 | 19500 | 4 | 2.2
202330772 | Ground Loop | WHALEN | CASV*036AJ**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
202330773 | Ground Loop | WHALEN | CASH*036AM**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
202330774 | Ground Loop | WHALEN | CASV*036AM**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
7167343 | Ground Loop | CARRIER | 50PSH/V024***4/DA |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
7167344 | Ground Loop | CARRIER | 50PSH/V030***4/DA |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
7167345 | Ground Loop | CARRIER | 50PSH/V030***6/FA |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
7167346 | Ground Loop | CARRIER | 50PSH/V030***5/EA |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
7167347 | Ground Loop | CARRIER | 50PSH/V030***3/CA |  | 28500 | 19.4 | 20300 | 3.95 | 2.375
7167357 | Ground Loop | CARRIER | 50PSH/V060***6/FA |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
7167358 | Ground Loop | CARRIER | 50PSH/V060***5/EA |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
6936993 | Ground Loop | BARD | GTC60S2-A | HE49948D210B2705AW | 63000 | 18.8 | 48000 | 4.05 | 5.25
5343170 | Ground Loop | DAIKIN | WVFW1048*E***04 |  | 50200 | 18.2 | 37600 | 3.8 | 4.1833
5295957 | Ground Loop | TRANE | EXHF0368 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333
5295958 | Ground Loop | TRANE | EXHF0364 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333
5295959 | Ground Loop | TRANE | EXHF0421 |  | 43500 | 18.5 | 32500 | 3.89 | 3.625
5295961 | Ground Loop | TRANE | EXHF0422 |  | 43500 | 18.5 | 32500 | 3.89 | 3.625
5295963 | Ground Loop | TRANE | EXHF0423 |  | 43500 | 18.5 | 32500 | 3.89 | 3.625
5295965 | Ground Loop | TRANE | EXHF0424 |  | 43500 | 18.5 | 32500 | 3.89 | 3.625
5295967 | Ground Loop | TRANE | EXHF0428 |  | 43500 | 18.5 | 32500 | 3.89 | 3.625
10443497 | Ground Loop | HYDRON MODULE | HBS018*2 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675
10443498 | Ground Loop | TETCO | TBS018*2 | MCD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675
10443499 | Ground Loop | GEOCOMFORT | GBS018 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675
10443500 | Ground Loop | HYDRON MODULE | HBS018 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675
10443501 | Ground Loop | TETCO | TBS018 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675
10443502 | Ground Loop | GEOCOMFORT | GBS018*2 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675
10443503 | Ground Loop | HYDRON MODULE | HBS018*2 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675
10206404 | Ground Loop | BARD | GTC36S2-A | HE37942D210B2505AW | 39500 | 18.3 | 29000 | 4.2 | 3.2917
10206405 | Ground Loop | BARD | GTC36S2-A | HE37942D175B2505AW | 39500 | 18.3 | 29000 | 4.2 | 3.2917
10268136 | Ground Loop | GEOCOMFORT | GBT036 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333
10268137 | Ground Loop | HYDRON MODULE | HBT036 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333
10268138 | Ground Loop | TETCO | TBT036 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333
10268139 | Ground Loop | GEOCOMFORT | GBT036*2 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333
202330763 | Ground Loop | WHALEN | CASH*024AJ**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
202330764 | Ground Loop | WHALEN | CASV*024AJ**A**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
214855047 | Ground Loop | WHALEN | CASH*018AB**B**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417
214855048 | Ground Loop | WHALEN | CASH*018AD**B**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417
214855049 | Ground Loop | WHALEN | CASV*018AB**B**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417
214855050 | Ground Loop | WHALEN | CASV*018AD**B**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417
214855051 | Ground Loop | WHALEN | CASH*024AB**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
214855052 | Ground Loop | WHALEN | CASH*024AD**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
214855053 | Ground Loop | WHALEN | CASH*024AJ**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
202330743 | Ground Loop | WHALEN | CASV*030AB**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
202330744 | Ground Loop | WHALEN | CASH*030AD**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
202330745 | Ground Loop | WHALEN | CASV*030AD**A**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
202330746 | Ground Loop | WHALEN | CASH*036AB**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
202330747 | Ground Loop | WHALEN | CASV*036AB**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
202330748 | Ground Loop | WHALEN | CASH*036AD**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
202330749 | Ground Loop | WHALEN | CASV*036AD**A**(D,E) |  | 36000 | 19 | 28000 | 3.6 | 3
202330323 | Ground Loop | AAON, Inc. | WH-048-1-H-ACAC-C0-10-200-A |  | 54100 | 18.7 | 43100 | 4 | 4.5083
202330324 | Ground Loop | AAON, Inc. | WH-048-A-H-ACAC-C0-10-200-A |  | 54100 | 18.7 | 43100 | 4 | 4.5083
206315253 | Ground Loop | WHALEN | CASH*018AB**A**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417
206315254 | Ground Loop | WHALEN | CASV*018AB**A**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417
206315255 | Ground Loop | WHALEN | CASH*018AD**A**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417
206315256 | Ground Loop | WHALEN | CASV*018AD**A**(G,E) |  | 18500 | 19 | 13500 | 4 | 1.5417
207178547 | Ground Loop | GEOSTAR | 161/162H072**1*(1,4)***** |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
207200554 | Ground Loop | GeoSmart Energy | GT026**1*(1,4)*H |  | 26400 | 19.6 | 19500 | 4 | 2.2
205993163 | Ground Loop | HYDRON MODULE | HBT024*2 | HED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333
205993164 | Ground Loop | HYDRON MODULE | HBT024*2 | HAD024 | 26300 | 20.4 | 18800 | 3.9 | 2.1917
205993165 | Ground Loop | TETCO | TBT024*2 | TED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333
205993166 | Ground Loop | TETCO | TBT024*2 | TAD024 | 26300 | 20.4 | 18800 | 3.9 | 2.1917
10443584 | Ground Loop | HYDRON MODULE | HBT024 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417
10443585 | Ground Loop | TETCO | TBT024 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417
10443586 | Ground Loop | GEOCOMFORT | GBT024*2 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417
10443587 | Ground Loop | HYDRON MODULE | HBT024*2 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417
10443588 | Ground Loop | TETCO | TBT024*2 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417
8560801 | Ground Loop | 5 SERIES | NSV/NSH030H1*(1,4) |  | 28100 | 22 | 20500 | 3.9 | 2.3417
8560806 | Ground Loop | 5 SERIES | NSV/NSH070H1*(1,4) |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
8570181 | Ground Loop | 5 SERIES | NDV/NDH072H1*(1,4) |  | 73800 | 18.2 | 55400 | 3.7 | 6.15
7167359 | Ground Loop | CARRIER | 50PSH/V060***3/CA |  | 61500 | 17.45 | 46900 | 4.05 | 5.125
7167360 | Ground Loop | CARRIER | 50PSH/V070***3/CA |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
7167361 | Ground Loop | CARRIER | 50PSH/V070***5/EA |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
7167362 | Ground Loop | CARRIER | 50PSH/V070***6/FA |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
202330349 | Ground Loop | AAON, Inc. | WV-009-A-H-ACAC-C0-10-200-A |  | 9800 | 18 | 7800 | 3.9 | 0.81667
202330350 | Ground Loop | AAON, Inc. | WV-012-B-H-ACAC-C0-10-200-A |  | 13500 | 17.1 | 11200 | 3.7 | 1.125
202330351 | Ground Loop | AAON, Inc. | WV-012-1-H-ACAC-C0-10-200-A |  | 13500 | 17.1 | 11200 | 3.7 | 1.125
202330352 | Ground Loop | AAON, Inc. | WV-012-A-H-ACAC-C0-10-200-A |  | 13500 | 17.1 | 11200 | 3.7 | 1.125
6965882 | Ground Loop | TRANE | EXVF0061 |  | 8100 | 17.33 | 6100 | 3.63 | 0.675
5360714 | Ground Loop | BARD | GTC36S2-A | GTADP-3642-* | 39500 | 18.3 | 29000 | 4.2 | 3.2917
5360715 | Ground Loop | BARD | GTC48S2-A | GTADP-4860-C | 51500 | 18.6 | 37000 | 3.9 | 4.2917
5360791 | Ground Loop | BARD | GTC60S2-A | GTADP-4860-C | 63000 | 18.8 | 48000 | 4.05 | 5.25
5440741 | Ground Loop | 7 SERIES | NVV/NVH048A1*1 |  | 46000 | 21.7 | 43000 | 3.6 | 3.8333
202923075 | Ground Loop | GEOSTAR | 101/102J038**1*(1,2,4)***** |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
203113881 | Ground Loop | GEOSTAR | 101/102J036**1*(0,3)***** |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
203113882 | Ground Loop | GEOSTAR | 101/102J036**1*(1,2,4)***** |  | 33700 | 22 | 24400 | 4.2 | 2.8083
8849312 | Ground Loop | 5 SERIES | NDV/NDH026H1*(1,4) |  | 26400 | 19.6 | 19500 | 4 | 2.2
202350093 | Ground Loop | 5 SERIES | NSV/NSH036J1*(0,3) |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
202350095 | Ground Loop | 5 SERIES | NSV/NSH036J1*(1,2,4) |  | 33700 | 22 | 24400 | 4.2 | 2.8083
202350096 | Ground Loop | 5 SERIES | NSV/NSH042J1*(1,2,4) |  | 40700 | 21.7 | 28900 | 4 | 3.3917
202350098 | Ground Loop | 5 SERIES | NDV/NDH038J1*(1,2,4) |  | 38200 | 19.7 | 28500 | 4.2 | 3.1833
202330403 | Ground Loop | AAON, Inc. | WV-048-1-H-ACAC-C0-10-200-A |  | 50500 | 19 | 40100 | 3.7 | 4.2083
202330404 | Ground Loop | AAON, Inc. | WV-048-A-H-ACAC-C0-10-200-A |  | 50500 | 19 | 40100 | 3.7 | 4.2083
206315249 | Ground Loop | WHALEN | CASH*015AB**A**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25
206315250 | Ground Loop | WHALEN | CASV*015AB**A**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25
206315251 | Ground Loop | WHALEN | CASH*015AD**A**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25
206315252 | Ground Loop | WHALEN | CASV*015AD**A**(G,E) |  | 15000 | 19 | 12000 | 4 | 1.25
5343162 | Ground Loop | DAIKIN | WVFW1042*K***04 |  | 46100 | 18.9 | 34400 | 3.8 | 3.8417
205993184 | Ground Loop | TETCO | TBT060*2 | TAD060 | 61100 | 18.2 | 46800 | 3.8 | 5.0917
206199262 | Ground Loop | RHEEM | RPVV/H/D026D |  | 26000 | 19.9 | 20200 | 4.1 | 2.1667
206199264 | Ground Loop | RHEEM | RPVV/H/D049D |  | 49600 | 19.3 | 36400 | 4 | 4.1333
206199265 | Ground Loop | RHEEM | RPVV/H/D064D |  | 66200 | 18.8 | 48700 | 3.9 | 5.5167
10581111 | Ground Loop | 5 SERIES | NDP064H1*1 |  | 62500 | 18.2 | 46300 | 3.8 | 5.2083
10581113 | Ground Loop | YORK BY JOHNSON CONTROLS | YAPT026**1*1******H |  | 24800 | 17.9 | 19300 | 3.9 | 2.0667
10581114 | Ground Loop | YORK BY JOHNSON CONTROLS | YAPT038**1*(1,2)******H |  | 38200 | 19.7 | 28300 | 4.1 | 3.1833
10581115 | Ground Loop | YORK BY JOHNSON CONTROLS | YAPT049**1*1******H |  | 50400 | 19 | 38000 | 4 | 4.2
10581116 | Ground Loop | YORK BY JOHNSON CONTROLS | YAPT064**1*1******H |  | 62500 | 18.2 | 46300 | 3.8 | 5.2083
207200570 | Ground Loop | GeoSmart Energy | GS036**1*(0,3)*J |  | 32900 | 19.2 | 24400 | 3.8 | 2.7417
207200571 | Ground Loop | GeoSmart Energy | GS036**1*(1,2,4)*J |  | 33700 | 22 | 24400 | 4.2 | 2.8083
205993142 | Ground Loop | TETCO | TBT048 | TAD048 | 50300 | 19.5 | 41000 | 3.9 | 4.1917
205993143 | Ground Loop | GEOCOMFORT | GBT048*2 | GED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275
205993144 | Ground Loop | GEOCOMFORT | GBT048*2 | GAD048 | 50300 | 19.5 | 41000 | 3.9 | 4.1917
205993145 | Ground Loop | HYDRON MODULE | HBT048*2 | HED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275
205993146 | Ground Loop | HYDRON MODULE | HBT048*2 | HAD048 | 50300 | 19.5 | 41000 | 3.9 | 4.1917
205993147 | Ground Loop | TETCO | TBT048*2 | TED048 | 51300 | 19.3 | 40700 | 4.1 | 4.275
205993148 | Ground Loop | TETCO | TBT048*2 | TAD048 | 50300 | 19.5 | 41000 | 3.9 | 4.1917
5295970 | Ground Loop | TRANE | EXHF0481 |  | 47900 | 17.7 | 36300 | 3.76 | 3.9917
5295971 | Ground Loop | TRANE | EXHF0482 |  | 47900 | 17.7 | 36300 | 3.76 | 3.9917
5295972 | Ground Loop | TRANE | EXHF0483 |  | 47900 | 17.7 | 36300 | 3.76 | 3.9917
5295973 | Ground Loop | TRANE | EXHF0484 |  | 47900 | 17.7 | 36300 | 3.76 | 3.9917
5295974 | Ground Loop | TRANE | EXHF0488 |  | 47900 | 17.7 | 36300 | 3.76 | 3.9917
205993159 | Ground Loop | TETCO | TBT024 | TED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333
205993160 | Ground Loop | TETCO | TBT024 | TAD024 | 26300 | 20.4 | 18800 | 3.9 | 2.1917
205993161 | Ground Loop | GEOCOMFORT | GBT024*2 | GED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333
205993162 | Ground Loop | GEOCOMFORT | GBT024*2 | GAD024 | 26300 | 20.4 | 18800 | 3.9 | 2.1917
10443577 | Ground Loop | GEOCOMFORT | GBT024 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417
10443578 | Ground Loop | HYDRON MODULE | HBT024 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417
10443579 | Ground Loop | TETCO | TBT024 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417
10443580 | Ground Loop | GEOCOMFORT | GBT024*2 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417
10443581 | Ground Loop | HYDRON MODULE | HBT024*2 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417
10443582 | Ground Loop | TETCO | TBT024*2 | MCD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417
10443583 | Ground Loop | GEOCOMFORT | GBT024 | ACD024 | 24500 | 17.6 | 17800 | 3.6 | 2.0417
205993128 | Ground Loop | HYDRON MODULE | HBT036 | HAD036 | 36900 | 19.3 | 29000 | 3.9 | 3.075
205993129 | Ground Loop | TETCO | TBT036 | TED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333
205993130 | Ground Loop | TETCO | TBT036 | TAD036 | 36900 | 19.3 | 29000 | 3.9 | 3.075
205993131 | Ground Loop | GEOCOMFORT | GBT036*2 | GED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333
205993132 | Ground Loop | GEOCOMFORT | GBT036*2 | GAD036 | 36900 | 19.3 | 29000 | 3.9 | 3.075
205993133 | Ground Loop | HYDRON MODULE | HBT036*2 | HED036 | 37600 | 19.2 | 28800 | 3.8 | 3.1333
205993134 | Ground Loop | HYDRON MODULE | HBT036*2 | HAD036 | 36900 | 19.3 | 29000 | 3.9 | 3.075
10268233 | Ground Loop | GEOCOMFORT | GBT048 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917
10268234 | Ground Loop | HYDRON MODULE | HBT048 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917
10268235 | Ground Loop | TETCO | TBT048 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917
10268236 | Ground Loop | GEOCOMFORT | GBT048*2 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917
10268237 | Ground Loop | HYDRON MODULE | HBT048*2 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917
10268238 | Ground Loop | TETCO | TBT048*2 | MPD060 | 51500 | 19.9 | 37300 | 3.9 | 4.2917
10268244 | Ground Loop | GEOCOMFORT | GBT048 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333
10268140 | Ground Loop | HYDRON MODULE | HBT036*2 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333
10268141 | Ground Loop | TETCO | TBT036*2 | MPD036 | 35200 | 17.1 | 28700 | 3.8 | 2.9333
10268198 | Ground Loop | GEOCOMFORT | GBT036 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825
10268199 | Ground Loop | HYDRON MODULE | HBT036 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825
10268200 | Ground Loop | TETCO | TBT036 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825
10268201 | Ground Loop | GEOCOMFORT | GBT036*2 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825
10268202 | Ground Loop | HYDRON MODULE | HBT036*2 | MCD036 | 33900 | 17.4 | 27900 | 3.7 | 2.825
7499450 | Ground Loop | FHP | EP009-1HZ/VT |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167
7499451 | Ground Loop | FHP | EP009-2HZ/VT |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167
7499453 | Ground Loop | FHP | EP012-1HZ/VT |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
7499455 | Ground Loop | FHP | EP015-1HZ/VT |  | 16200 | 19.8 | 11000 | 3.63 | 1.35
7499456 | Ground Loop | FHP | EP015-2HZ/VT |  | 16200 | 19.8 | 11000 | 3.63 | 1.35
214855054 | Ground Loop | WHALEN | CASH*024AM**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
214855055 | Ground Loop | WHALEN | CASV*024AB**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
214855056 | Ground Loop | WHALEN | CASV*024AD**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
214855057 | Ground Loop | WHALEN | CASV*024AJ**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
214855058 | Ground Loop | WHALEN | CASV*024AM**B**(D,E) |  | 25000 | 18.5 | 17000 | 3.7 | 2.0833
214855059 | Ground Loop | WHALEN | CASH*030AB**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
214855060 | Ground Loop | WHALEN | CASH*030AD**B**(D,E) |  | 30000 | 17.5 | 23000 | 3.6 | 2.5
207200624 | Ground Loop | GeoSmart Energy | VI048**1*1 |  | 46000 | 21.7 | 43000 | 3.6 | 3.8333
5505441 | Ground Loop | BARD | GTC36S2-A | HE37942D175B2505AW/HE37942D210B2505AW | 38500 | 19.3 | 27000 | 4.1 | 3.2083
5612204 | Ground Loop | GeoSmart Energy | VI048**1*1 |  | 46000 | 21.7 | 43000 | 3.6 | 3.8333
203466716 | Ground Loop | 5 SERIES | NDV/NDH049J1*(1,2,4) |  | 50800 | 19.3 | 38200 | 4 | 4.2333
203470607 | Ground Loop | 5 SERIES | NSV/NSH048J1*(1,2,4) |  | 45900 | 18.8 | 36400 | 4 | 3.825
203490410 | Ground Loop | GeoSmart Energy | GT049**1*(1,2,4)*J |  | 50800 | 19.3 | 38200 | 4 | 4.2333
203490416 | Ground Loop | GeoSmart Energy | GS048**1*(1,2,4)*J |  | 45900 | 18.8 | 36400 | 4 | 3.825
203494005 | Ground Loop | GEOSTAR | 101/102J048**1*(1,2,4) |  | 45900 | 18.8 | 36400 | 4 | 3.825
3920503 | Ground Loop | AQUARIUS | EP070-1HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
3920504 | Ground Loop | AQUARIUS | EP070-3HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
3920505 | Ground Loop | AQUARIUS | EP070-4HZ/VT |  | 70500 | 17.56 | 56500 | 3.77 | 5.875
202391452 | Ground Loop | CARRIER | 50PSH012**C4/DA |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
6945298 | Ground Loop | BARD | GTC48S2-A | HE49948D210B2705AW | 51500 | 18.6 | 37000 | 3.9 | 4.2917
5343146 | Ground Loop | DAIKIN | WVFW1030*E***04 |  | 30600 | 19.3 | 22300 | 4 | 2.55
10445242 | Ground Loop | WaterFurnace | SDV049H1*(1,2) |  | 47700 | 18.2 | 38000 | 3.8 | 3.975
10445244 | Ground Loop | WaterFurnace | SDV072H1*1 |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083
10447649 | Ground Loop | RHEEM | RPVS/EC025 | RCFL-HM2417 | 24000 | 17.4 | 18800 | 3.9 | 2
5296247 | Ground Loop | TRANE | EXVF0241 |  | 25500 | 18.9 | 18200 | 3.8 | 2.125
5296248 | Ground Loop | TRANE | EXVF0242 |  | 25500 | 18.9 | 18200 | 3.8 | 2.125
5296249 | Ground Loop | TRANE | EXVF0247 |  | 25500 | 18.9 | 18200 | 3.8 | 2.125
205993149 | Ground Loop | GEOCOMFORT | GBT060 | GED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833
205993150 | Ground Loop | HYDRON MODULE | HBT060 | HED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833
205993151 | Ground Loop | TETCO | TBT060 | TED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833
205993152 | Ground Loop | GEOCOMFORT | GBT060*2 | GED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833
205993153 | Ground Loop | HYDRON MODULE | HBT060*2 | HED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833
205993154 | Ground Loop | TETCO | TBT060*2 | TED060 | 63400 | 17.8 | 48100 | 3.8 | 5.2833
205993155 | Ground Loop | GEOCOMFORT | GBT024 | GED024 | 26800 | 19.5 | 19200 | 4.1 | 2.2333
10443504 | Ground Loop | TETCO | TBS018*2 | ACD024 | 20100 | 18.6 | 14700 | 3.6 | 1.675
10443509 | Ground Loop | GEOCOMFORT | GBS018 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7
10443510 | Ground Loop | HYDRON MODULE | HBS018 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7
10443511 | Ground Loop | TETCO | TBS018 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7
10443512 | Ground Loop | GEOCOMFORT | GBS018*2 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7
10443513 | Ground Loop | HYDRON MODULE | HBS018*2 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7
10443514 | Ground Loop | TETCO | TBS018*2 | MPD024 | 20400 | 18.9 | 14600 | 3.6 | 1.7
5295950 | Ground Loop | TRANE | EXHF0301 |  | 29700 | 18.7 | 21100 | 3.7 | 2.475
5295951 | Ground Loop | TRANE | EXHF0302 |  | 29700 | 18.7 | 21100 | 3.7 | 2.475
5295952 | Ground Loop | TRANE | EXHF0307 |  | 29700 | 18.7 | 21100 | 3.7 | 2.475
5295953 | Ground Loop | TRANE | EXHF0361 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333
5295954 | Ground Loop | TRANE | EXHF0362 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333
5295955 | Ground Loop | TRANE | EXHF0367 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333
5295956 | Ground Loop | TRANE | EXHF0363 |  | 36400 | 19.1 | 26700 | 3.78 | 3.0333
10268245 | Ground Loop | HYDRON MODULE | HBT048 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333
10268246 | Ground Loop | TETCO | TBT048 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333
10268247 | Ground Loop | GEOCOMFORT | GBT048*2 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333
10268248 | Ground Loop | HYDRON MODULE | HBT048*2 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333
10268249 | Ground Loop | TETCO | TBT048*2 | ACD060 | 50800 | 19.2 | 37200 | 4 | 4.2333
10268250 | Ground Loop | GEOCOMFORT | GBT048 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333
10268251 | Ground Loop | HYDRON MODULE | HBT048 | MCD060 | 50800 | 19.2 | 37200 | 4 | 4.2333
3919848 | Ground Loop | AQUARIUS | EP009-1HZ/VT |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167
3919850 | Ground Loop | AQUARIUS | EP009-2HZ/VT |  | 9500 | 17.05 | 6800 | 3.6 | 0.79167
3919853 | Ground Loop | AQUARIUS | EP012-1HZ/VT |  | 12600 | 17.5 | 9300 | 3.6 | 1.05
3919854 | Ground Loop | AQUARIUS | EP015-1HZ/VT |  | 16200 | 19.8 | 11000 | 3.63 | 1.35
3919855 | Ground Loop | AQUARIUS | EP015-2HZ/VT |  | 16200 | 19.8 | 11000 | 3.63 | 1.35
3919884 | Ground Loop | AQUARIUS | EP024-1HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
3919931 | Ground Loop | AQUARIUS | EP024-2HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
202358913 | Ground Loop | DAIKIN | WCCW5019*E*04* |  | 20600 | 19 | 14000 | 3.7 | 1.7167
202358915 | Ground Loop | DAIKIN | WCCW5019*J*04* |  | 20600 | 19 | 14000 | 3.7 | 1.7167
8105933 | Ground Loop | TRANE | DXHF0703 |  | 70400 | 17.6 | 56800 | 3.8 | 5.8667
8105934 | Ground Loop | TRANE | DXHF0704 |  | 70400 | 17.6 | 56800 | 3.8 | 5.8667
8105935 | Ground Loop | TRANE | DXHF0708 |  | 70400 | 17.6 | 56800 | 3.8 | 5.8667
8105950 | Ground Loop | TRANE | DXVF0241 |  | 24948 | 17.41 | 19300 | 4 | 2.079
8105955 | Ground Loop | TRANE | DXVF0242 |  | 24948 | 17.41 | 19300 | 4 | 2.079
8105956 | Ground Loop | TRANE | DXVF0243 |  | 24948 | 17.41 | 19300 | 4 | 2.079
8105960 | Ground Loop | TRANE | DXVF0244 |  | 24948 | 17.41 | 19300 | 4 | 2.079
214813285 | Ground Loop | ARCADIAN | AVHP-03-G |  | 9900 | 17.22 | 7452 | 3.65 | 0.825
214813286 | Ground Loop | ARCADIAN | AVHP-04-G |  | 13040 | 17.32 | 10273 | 3.62 | 1.0867
214813287 | Ground Loop | ARCADIAN | AVHP-05-G |  | 15724 | 17.2 | 11705 | 3.61 | 1.3103
214813288 | Ground Loop | ARCADIAN | AVHP-06-G |  | 19621 | 17.3 | 15106 | 3.62 | 1.6351
214813289 | Ground Loop | ARCADIAN | AVHP-08-G |  | 26613 | 17.38 | 18707 | 3.61 | 2.2178
202330427 | Ground Loop | AAON, Inc. | WV-048-A-H-DCAC-C0-10-200-A |  | 49300 | 17.1 | 35210 | 3.7 | 4.1083
202330428 | Ground Loop | AAON, Inc. | WV-048-A-H-DCAC-C0-10-D00-A |  | 49800 | 17.5 | 44900 | 3.9 | 4.15
202330429 | Ground Loop | AAON, Inc. | WV-048-3-H-DCAC-C0-10-200-A |  | 49300 | 17.1 | 35210 | 3.7 | 4.1083
207334462 | Ground Loop | WaterFurnace | NDP064H1*1 |  | 62500 | 18.2 | 46300 | 3.8 | 5.2083
207337519 | Ground Loop | GEOSTAR | 103H060**1 | SAH060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
207337520 | Ground Loop | GEOSTAR | 103H060**1 | SRAA060* | 56300 | 17.7 | 44000 | 3.7 | 4.6917
207200572 | Ground Loop | GeoSmart Energy | GS042**1*(1,2,4)*J |  | 40700 | 21.7 | 28900 | 4 | 3.3917
207200574 | Ground Loop | GeoSmart Energy | GS048**1*(1,2,4)*J |  | 45900 | 18.8 | 36400 | 4 | 3.825
207200622 | Ground Loop | GeoSmart Energy | QT049**1*(1,2)* |  | 47700 | 18.2 | 38000 | 3.8 | 3.975
207200623 | Ground Loop | GeoSmart Energy | QT072**1*1* |  | 68500 | 17.1 | 54500 | 3.7 | 5.7083
5615049 | Ground Loop | DAIKIN | WCCW5036*K*04* |  | 38000 | 18.8 | 28700 | 3.8 | 3.1667
5615054 | Ground Loop | DAIKIN | WCCW5042*E*04* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675
5615055 | Ground Loop | DAIKIN | WCCW5042*F*04* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675
5615056 | Ground Loop | DAIKIN | WCCW5042*K*04* |  | 44100 | 17.9 | 34600 | 3.8 | 3.675
5615061 | Ground Loop | DAIKIN | WCCW5048*E*04* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167
5615062 | Ground Loop | DAIKIN | WCCW5048*F*04* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167
5615063 | Ground Loop | DAIKIN | WCCW5048*K*04* |  | 50600 | 18.2 | 39300 | 3.9 | 4.2167
207200563 | Ground Loop | GeoSmart Energy | GS030**1*(0,3)*H |  | 27900 | 21.1 | 20300 | 3.7 | 2.325
207200564 | Ground Loop | GeoSmart Energy | GS030**1*(1,4)*H |  | 28100 | 22 | 20500 | 3.9 | 2.3417
207200567 | Ground Loop | GeoSmart Energy | GS070**1*(1,4)*H |  | 69100 | 17.6 | 54000 | 3.7 | 5.7583
10268272 | Ground Loop | HYDRON MODULE | HBT060*2 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833
10268273 | Ground Loop | TETCO | TBT060*2 | ACD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833
10268274 | Ground Loop | GEOCOMFORT | GBT060 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833
10268275 | Ground Loop | HYDRON MODULE | HBT060 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833
10268276 | Ground Loop | TETCO | TBT060 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833
10268277 | Ground Loop | GEOCOMFORT | GBT060*2 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833
10268278 | Ground Loop | HYDRON MODULE | HBT060*2 | MCD060 | 61000 | 17.6 | 45500 | 3.7 | 5.0833
203113887 | Ground Loop | GEOSTAR | 101/102J042**1*(1,2,4)***** |  | 40700 | 21.7 | 28900 | 4 | 3.3917
202350524 | Ground Loop | AAON, Inc. | WV-048-1-H-DCAC-C0-10-200-A |  | 49300 | 17.1 | 35210 | 3.7 | 4.1083
202350526 | Ground Loop | AAON, Inc. | WV-048-2-H-DCAC-C0-10-200-A |  | 49300 | 17.1 | 35210 | 3.7 | 4.1083
6966789 | Ground Loop | TRANE | EXVF0127 |  | 13100 | 18.2 | 9400 | 3.74 | 1.0917
7076986 | Ground Loop | AQUARIUS | EP024-3HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
7076987 | Ground Loop | AQUARIUS | EP024-4HZ/VT |  | 26000 | 19.8 | 18000 | 3.7 | 2.1667
207334458 | Ground Loop | WaterFurnace | NDP026H1*1 |  | 24800 | 17.9 | 19300 | 3.9 | 2.0667
207334459 | Ground Loop | WaterFurnace | NDP038H1*(1,2) |  | 38200 | 19.7 | 28300 | 4.1 | 3.1833
207334460 | Ground Loop | WaterFurnace | NDP049H1*1 |  | 50400 | 19 | 38000 | 4 | 4.2
5317936 | Ground Loop | GEOCOMFORT | GRT060A | ACD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083
5317937 | Ground Loop | HYDRON MODULE | HRT060A | ACD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083
5317938 | Ground Loop | TETCO | TRT060A | ACD060 | 61300 | 17.1 | 45600 | 3.6 | 5.1083
205993114 | Ground Loop | GEOCOMFORT | GBS018 | GAD018 | 22200 | 22.2 | 14400 | 3.9 | 1.85
205993115 | Ground Loop | HYDRON MODULE | HBS018 | HED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417
205993116 | Ground Loop | HYDRON MODULE | HBS018 | HAD018 | 22200 | 22.2 | 14400 | 3.9 | 1.85
205993117 | Ground Loop | TETCO | TBS018 | TED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417
205993118 | Ground Loop | TETCO | TBS018 | TAD018 | 22200 | 22.2 | 14400 | 3.9 | 1.85
205993119 | Ground Loop | GEOCOMFORT | GBS018*2 | GED018 | 22100 | 21.7 | 14500 | 3.9 | 1.8417
205993120 | Ground Loop | GEOCOMFORT | GBS018*2 | GAD018 | 22200 | 22.2 | 14400 | 3.9 | 1.85
5296264 | Ground Loop | TRANE | EXVF0428 |  | 43200 | 18.5 | 31700 | 3.89 | 3.6
5296265 | Ground Loop | TRANE | EXVF0481 |  | 47900 | 18.5 | 36200 | 3.96 | 3.9917
5296266 | Ground Loop | TRANE | EXVF0482 |  | 47900 | 18.5 | 36200 | 3.96 | 3.9917
5296267 | Ground Loop | TRANE | EXVF0483 |  | 47900 | 18.5 | 36200 | 3.96 | 3.9917
5296268 | Ground Loop | TRANE | EXVF0484 |  | 47900 | 18.5 | 36200 | 3.96 | 3.9917
10581118 | Ground Loop | GEOSTAR | 107H026**1*1 |  | 24800 | 17.9 | 19300 | 3.9 | 2.0667
10581119 | Ground Loop | GEOSTAR | 107H038**1*(1,2) |  | 38200 | 19.7 | 28300 | 4.1 | 3.1833
10581120 | Ground Loop | GEOSTAR | 107H049**1*1 |  | 50400 | 19 | 38000 | 4 | 4.2

## Residential GSHP
[6 empty] | Water Loop Heat Pump |  |  |  |  | Ground Water Heat Pump |  |  |  |  | Ground Loop Heat Pump |  |  |  |  | Direct Geoexchange Heat Pump
AHRI Certified Reference Number | Brand Name | AHRI Type | Program Type | Outdoor Unit Model Number | Indoor Unit Model Number(s) | Full Load WLHP Cooling Capacity (Btuh) | Full Load WLHP Cooling EER (Btuh/watt) | Full Load WLHP Heating COP | Full Load WLHP Heating Capacity (Btuh) | WLHP Tonnage | Full Load GWHP Cooling Capacity (Btuh) | Full Load GWHP Cooling EER (Btuh/watt) | Full Load GWHP Heating COP | Full Load GWHP Heating Capacity (Btuh) | GWHP Tonnage | Full Load GLHP Cooling Capacity (Btuh) | Full Load GLHP Cooling EER (Btuh/watt) | Full Load GLHP Heating COP | Full Load GLHP Heating Capacity (Btuh) | GLHP Tonnage | Refrigerant Type | Full Load DGX Cooling Capacity (Btuh) | Full Load DGX Cooling EER (Btuh/watt) | Full Load DGX Heating COP | Full Load DGX Heating Capacity (Btuh) | DGX Tonnage
203105868 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-36C1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-410A | 38000 | 19.1 | 3.9 | 38000 | 3.1667
203105870 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-42C1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-410A | 44000 | 21 | 3.9 | 44000 | 3.6667
203105871 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-48C1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-410A | 51500 | 19.8 | 4 | 51500 | 4.2917
203105874 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-54C1-CP*-*-* | AH-054-*-*-* | [15 empty] | R-410A | 56000 | 19.1 | 3.8 | 56000 | 4.6667
203105877 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-60C1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-410A | 61500 | 19.1 | 3.6 | 61500 | 5.125
203470614 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AH-48C1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-410A | 33600 | 20.1 | 3.6 | 33600 | 2.8
203470620 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-24C1-CP*-*-* | AH-024-*-*-* | [15 empty] | R-410A | 25400 | 19.1 | 3.9 | 25400 | 2.1167
203470621 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-30C1-CP*-*-* | AH-030-*-*-* | [15 empty] | R-410A | 31600 | 20.1 | 3.9 | 31600 | 2.6333
204494956 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-36C1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-410A | 38000 | 19.1 | 3.9 | 38000 | 3.1667
204494957 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-42C1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-410A | 44000 | 19.1 | 3.9 | 44000 | 3.6667
204494958 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-48C1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-410A | 51500 | 19.8 | 4 | 51500 | 4.2917
204494959 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-54C1-CP*-*-* | AH-054-*-*-* | [15 empty] | R-410A | 56000 | 19.1 | 3.8 | 56000 | 4.6667
204494960 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-60C1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-410A | 61500 | 19.1 | 3.6 | 61500 | 5.125
216720848 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-24D1-CP*-*-* | AH-024-*-*-* | [15 empty] | R-454B | 24000 | 19.1 | 3.9 | 24000 | 2
216720849 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-30D1-CP*-*-* | AH-030-*-*-* | [15 empty] | R-454B | 31600 | 20.1 | 3.9 | 31600 | 2.6333
216720850 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-36D1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-454B | 38000 | 22 | 3.9 | 38000 | 3.1667
216720851 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-42D1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-454B | 44000 | 19.1 | 3.9 | 44000 | 3.6667
216720852 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-48D1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-454B | 51500 | 21 | 4.1 | 51500 | 4.2917
216720853 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-54D1-CP*-*-* | AH-054-*-*-* | [15 empty] | R-454B | 56000 | 19.1 | 3.8 | 56000 | 4.6667
216720854 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-60D1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-454B | 61500 | 19.1 | 4 | 61500 | 5.125
216720855 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-24D1-CP*-*-* | AH-024-*-*-* | [15 empty] | R-454B | 16100 | 20.1 | 4.3 | 16100 | 1.3417
216720856 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-30D1-CP*-*-* | AH-030-*-*-* | [15 empty] | R-454B | 20100 | 20.1 | 4.3 | 20100 | 1.675
216720857 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-36D1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-454B | 24100 | 30 | 4.1 | 24100 | 2.0083
216720858 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-48D1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-454B | 32200 | 30 | 4.5 | 32200 | 2.6833
216720859 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-60D1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-454B | 40200 | 25 | 4.6 | 40200 | 3.35
216720860 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-36D1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-454B | 24100 | 30 | 4.4 | 24100 | 2.0083
216720861 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-48D1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-454B | 32200 | 30 | 4.4 | 32200 | 2.6833
216720862 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-60D1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-454B | 40200 | 25 | 4.4 | 40200 | 3.35
216720863 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AH-36D1-CP*-*-* | AH-036-*-*-* | [15 empty] | R-454B | 24100 | 30 | 4.4 | 24100 | 2.0083
216720864 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AH-48D1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-454B | 32200 | 30 | 4.4 | 32200 | 2.6833
216720865 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AH-60D1-CP*-*-* | AH-060-*-*-* | [15 empty] | R-454B | 40200 | 25 | 4.6 | 40200 | 3.35
216720866 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-42D1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-454B | 28100 | 24 | 4.3 | 28100 | 2.3417
216720867 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-42D1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-454B | 28100 | 24 | 3.9 | 28100 | 2.3417
216720868 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AH-42D1-CP*-*-* | AH-042-*-*-* | [15 empty] | R-454B | 28100 | 24 | 3.9 | 28100 | 2.3417
8224172 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SC-018-1C | AVS-018-* | [15 empty] | R-410A | 18000 | 17.1 | 3.6 | 18000 | 1.5
8229033 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SD-018-1C | AVS-018-* | [15 empty] | R-410A | 18000 | 17.1 | 3.6 | 18000 | 1.5
8229034 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SDH-018-1C | AVS-018-* | [15 empty] | R-410A | 18000 | 17.1 | 3.6 | 18000 | 1.5
8229035 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SDH-024-1C | AVS-024-* | [15 empty] | R-410A | 24000 | 17.1 | 3.6 | 24000 | 2
8229036 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SD-024-1C | AVS-024-* | [15 empty] | R-410A | 24000 | 17.1 | 3.6 | 24000 | 2
8229037 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SC-024-1C | AVS-024-* | [15 empty] | R-410A | 24000 | 17.1 | 3.6 | 24000 | 2
8229041 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SDH-036-1C | AVS-036-* | [15 empty] | R-410A | 36000 | 17.1 | 3.6 | 36000 | 3
8229042 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SD-036-1C | AVS-036-* | [15 empty] | R-410A | 36000 | 17.1 | 3.6 | 36000 | 3
8229043 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SC-036-1C | AVS-036-* | [15 empty] | R-410A | 36000 | 17.1 | 3.6 | 36000 | 3
201841510 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | PSC-024-1C | AVS-024-* | [15 empty] | R-410A | 18000 | 25 | 4.3 | 18000 | 1.5
201841515 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-018-1C | HVA-018-* | [15 empty] | R-410A | 18000 | 16 | 3.6 | 18000 | 1.5
201841516 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-024-1C | HVA-024-* | [15 empty] | R-410A | 24000 | 16 | 3.6 | 24000 | 2
201841517 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-030-1C | HVA-030-* | [15 empty] | R-410A | 30000 | 16 | 3.6 | 30000 | 2.5
201841518 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-036-1C | HVA-036-* | [15 empty] | R-410A | 36000 | 16 | 3.6 | 36000 | 3
201841519 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-042-1C | HVA-042-* | [15 empty] | R-410A | 42000 | 16 | 3.6 | 42000 | 3.5
201841520 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-048-1C | HVA-048-* | [15 empty] | R-410A | 48000 | 16 | 3.6 | 48000 | 4
201841521 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-054-1C | HVA-054-* | [15 empty] | R-410A | 54000 | 16 | 3.6 | 54000 | 4.5
201841522 | EARTHLINKED | HRCU-DGX-CB | Direct Expansion Refrigerant | SCW-060-1C | HVA-060-* | [15 empty] | R-410A | 60000 | 16 | 3.6 | 60000 | 5
201902854 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-24C1-CP1-*-* | AH-024-*-*-* | [15 empty] | R-410A | 18000 | 25 | 4.3 | 18000 | 1.5
201902855 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-36C1-CP1-*-* | AH-036-*-*-* | [15 empty] | R-410A | 28000 | 23 | 4.1 | 28000 | 2.3333
201902856 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-48C1-CP1-*-* | AH-048-*-*-* | [15 empty] | R-410A | 40000 | 23 | 4.1 | 40000 | 3.3333
201902857 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2AD-60C1-CP1-*-* | AH-060-*-*-* | [15 empty] | R-410A | 49000 | 23 | 4.1 | 49000 | 4.0833
201902862 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-30C1-CP1-*-* | AH-030-*-*-* | [15 empty] | R-410A | 23000 | 25 | 4.3 | 23000 | 1.9167
201902863 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-36C1-CP1-*-* | AH-036-*-*-* | [15 empty] | R-410A | 28000 | 25 | 4.3 | 28000 | 2.3333
201902864 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG2A-48C1-CP1-*-* | AH-048-*-*-* | [15 empty] | R-410A | 40000 | 25 | 4.3 | 40000 | 3.3333
201902865 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-24C1-*-* | AH-024-*-*-* | [15 empty] | R-410A | 24000 | 21 | 3.6 | 24000 | 2
201902866 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-24C1-CP1-*-* | AH-024-*-*-* | [15 empty] | R-410A | 24000 | 20.9 | 4 | 24000 | 2
201902867 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-30C1-CP1-*-* | AH-030-*-*-* | [15 empty] | R-410A | 30000 | 21 | 4 | 30000 | 2.5
201902868 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-30C1-*-* | AH-030-*-*-* | [15 empty] | R-410A | 30000 | 19.1 | 3.6 | 30000 | 2.5
201902869 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-36C1-*-* | AH-036-*-*-* | [15 empty] | R-410A | 36000 | 19.1 | 3.6 | 36000 | 3
201902870 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-36C1-CP1-*-* | AH-036-*-*-* | [15 empty] | R-410A | 36000 | 20.9 | 4 | 36000 | 3
201902871 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-42C1-CP1-*-* | AH-042-*-*-* | [15 empty] | R-410A | 42000 | 21 | 4 | 42000 | 3.5
201902872 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-42C1-*-* | AH-042-*-*-* | [15 empty] | R-410A | 42000 | 19.1 | 3.6 | 42000 | 3.5
201902873 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-48C1-*-* | AH-048-*-*-* | [15 empty] | R-410A | 48000 | 19.1 | 3.6 | 48000 | 4
201902874 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-48C1-CP1-*-* | AH-048-*-*-* | [15 empty] | R-410A | 48000 | 20.9 | 4 | 48000 | 4
201902875 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-60C1-*-* | AH-060-*-*-* | [15 empty] | R-410A | 60000 | 19.1 | 3.6 | 60000 | 5
201902876 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-60C1-CP1-*-* | AH-060-*-*-* | [15 empty] | R-410A | 60000 | 20.9 | 4 | 60000 | 5
201977884 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-54C1-*-* | AH-054-*-*-* | [15 empty] | R-410A | 54000 | 19.1 | 3.6 | 54000 | 4.5
201977885 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1A-54C1-CP1-*-* | AH-054-*-*-* | [15 empty] | R-410A | 54000 | 21 | 4 | 54000 | 4.5
201978151 | Test Brand 01 | HRCU-DGX-C | Direct Expansion Refrigerant | TEST MODEL | TEST MODEL | [15 empty] | R-407C | 20000 | 24 | 5 | 20000 | 1.6667
203105865 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-24C1-CP*-*-* | AH-024-*-*-* | [15 empty] | R-410A | 24000 | 19.1 | 3.8 | 24000 | 2
203105866 | WATERLESS | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-30C1-CP*-*-* | AH-030-*-*-* | [15 empty] | R-410A | 30000 | 19.1 | 3.8 | 30000 | 2.5
203470619 | WATERLESS | HRCU-DGX-CW | Direct Expansion Refrigerant | WG1H-24C1-CP*-*-* | AH-048-*-*-* | [15 empty] | R-410A | 24000 | 19.1 | 3.6 | 24000 | 2
206374296 | Test Brand 01 | HRCU-DGX-C | Direct Expansion Refrigerant | TEST11922-1 | TEST MODEL | [15 empty] | R-32 | 20000 | 24 | 5 | 20000 | 1.6667
217607067 | BRAND_01 | HRCU-DGX-CB | Direct Expansion Refrigerant | MZ-TEST-ESPASS | AH-MZ-TEST-ESMIN | [15 empty] | R-454B | 24100 | 30 | 4.4 | 24100 | 2.0083
217730044 | BRAND_01 | HRCU-DGX-CB | Direct Expansion Refrigerant | WG1AH-36C1-CP*-*-* | S33-40LEWH-4500 | [15 empty] | R-410A | 38000 | 19.1 | 3.9 | 38000 | 3.1667
215224536 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF060-4CFN-*****A | [6 empty] | 63000 | 19 | 4 | 55500 | 5.25 | 59000 | 15.2 | 3.5 | 43500 | 4.9167
215224539 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF024-1VT/HZC-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224540 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF024-3VT/HZC-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224541 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF024-1VT/HZN-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224542 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF024-3VT/HZN-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224543 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF030-1VT/HZC-*****A | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224544 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF030-3VT/HZC-*****A | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224545 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF030-1VT/HZN-*****A | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224546 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF030-3VT/HZN-*****A | [6 empty] | 32000 | 21.5 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224547 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF036-1VT/HZC-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224548 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF036-3VT/HZC-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224549 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF036-1VT/HZN-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224550 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF036-3VT/HZN-*****A | [6 empty] | 40000 | 21 | 4.2 | 35400 | 3.3333 | 38000 | 16.5 | 3.7 | 28000 | 3.1667
215224551 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF042-1VT/HZC-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224552 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF042-3VT/HZC-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224553 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF042-1VT/HZN-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224554 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF042-3VT/HZN-*****A | [6 empty] | 45000 | 21 | 4.2 | 40000 | 3.75 | 43000 | 16.5 | 3.7 | 32000 | 3.5833
215224555 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF048-1VT/HZC-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224556 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF048-3VT/HZC-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224557 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF048-1VT/HZN-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
215224558 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CF048-3VT/HZN-*****A | [6 empty] | 52000 | 21 | 4.2 | 48000 | 4.3333 | 49000 | 16.5 | 3.7 | 38000 | 4.0833
216065302 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWS036* | [6 empty] | 35600 | 22.9 | 4.1 | 38300 | 2.9667 | 34900 | 17.7 | 3.3 | 31000 | 2.9083
216065303 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWS048* | [6 empty] | 52500 | 22.9 | 4.2 | 58700 | 4.375 | 50500 | 17.3 | 3.2 | 45200 | 4.2083
216065305 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT036* | [6 empty] | 42200 | 20.4 | 4.1 | 48000 | 3.5167 | 40200 | 15.4 | 3.3 | 38100 | 3.35
216065306 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT048* | [6 empty] | 52700 | 21.2 | 4.2 | 61100 | 4.3917 | 49500 | 16.3 | 3.5 | 49000 | 4.125
216065307 | GEOCOMFORT | WBWHP | Water-to-Water and Brine-to-Water | GWT060* | [6 empty] | 62700 | 20.4 | 3.9 | 67000 | 5.225 | 60600 | 16.2 | 3.1 | 52900 | 5.05
216128491 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5TV036BD1**2 |  | 36000 | 17.9 | 5.6 | 42300 | 3 | 41400 | 26.9 | 5.1 | 35700 | 3.45 | 38000 | 20.1 | 4.3 | 29300 | 3.1667
216128493 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5TV048BD1**2 | [6 empty] | 52500 | 24.5 | 4.7 | 47400 | 4.375 | 49100 | 18.5 | 4.1 | 38400 | 4.0917
216411469 | ClimateMaster | WBAHP-CB | Water-to-Air and Brine-to-Air | SJ/PN024A | SAN024A | [5 empty] | 24700 | 25.2 | 4.8 | 22500 | 2.0583 | 23900 | 19 | 4 | 17900 | 1.9917
216411470 | ClimateMaster | WBAHP-CB | Water-to-Air and Brine-to-Air | SJ/PN036A | SAN036A | 36400 | 17.3 | 5.3 | 39400 | 3.0333 | 41800 | 25 | 4.7 | 33700 | 3.4833 | 38300 | 18.4 | 4 | 26900 | 3.1917
216411471 | ClimateMaster | WBAHP-CB | Water-to-Air and Brine-to-Air | SJ/PN048A | SAN048A | [5 empty] | 51900 | 22.2 | 4.4 | 46000 | 4.325 | 49000 | 18.1 | 3.7 | 35500 | 4.0833
216419856 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)024A | [6 empty] | 27500 | 23.3 | 4.4 | 24200 | 2.2917 | 25600 | 17.3 | 3.6 | 19000 | 2.1333
216419857 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)024A*V | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
216419860 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)030A*V | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
216419863 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)036A*V | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
216419865 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)042A*V | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
216419867 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)048A | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
216419868 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)048A*V | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
216419879 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)015A | [6 empty] | 16700 | 23.5 | 4.3 | 13800 | 1.3917
216419880 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)015A*V | [6 empty] | 16900 | 26.2 | 4.5 | 13800 | 1.4083 | 15200 | 17.3 | 3.6 | 10700 | 1.2667
216419882 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)018A | [6 empty] | 20700 | 23 | 4.2 | 17900 | 1.725
216419883 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WC(L/R/B/P/T/K/F)018A*V | [6 empty] | 20900 | 25 | 4.4 | 17700 | 1.7417 | 19400 | 17.3 | 3.6 | 13800 | 1.6167
216419898 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)024A | [6 empty] | 27500 | 23.3 | 4.4 | 24200 | 2.2917 | 25600 | 17.3 | 3.6 | 19000 | 2.1333
216419899 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)024A*V | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
216419902 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)030A*V | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
216419904 | Whalen | WBAHP | Water-to-Air and Brine-to-Air | WR(L/R/B/P/T/K/F)036A*V | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
4219424 | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | R45HACW-P-1T-*-SDE** | [6 empty] | 38500 | 21.3 | 4.3 | 35700 | 3.2083 | 35100 | 16.3 | 3.6 | 27200 | 2.925
4219425 | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | R55HACW-P-1T-*-SDE** | [6 empty] | 50200 | 22.5 | 4.5 | 47200 | 4.1833 | 45400 | 17 | 3.8 | 35600 | 3.7833
4219426 | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | R65HACW-P-1T-*-SDE** | [6 empty] | 62600 | 21.5 | 4.5 | 58700 | 5.2167 | 57600 | 16.8 | 3.7 | 44000 | 4.8
4219429 | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | RH45HACW-P-1T-*-SDE** | [6 empty] | 37800 | 19.7 | 4.2 | 35000 | 3.15 | 35000 | 16.3 | 3.6 | 26600 | 2.9167
4219430 | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | RH55HACW-P-1T-*-SDE** | [6 empty] | 49200 | 20 | 4.4 | 46200 | 4.1 | 44400 | 17 | 3.6 | 34700 | 3.7
4219431 | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | RH65HACW-P-1T-*-SDE** | [6 empty] | 61400 | 19.4 | 4.3 | 57500 | 5.1167 | 56400 | 15 | 3.5 | 42800 | 4.7
4219433 | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | TF45HACW-P-1T-*-SDE** | [6 empty] | 39200 | 20.8 | 4.2 | 34300 | 3.2667 | 36200 | 16.2 | 3.6 | 25200 | 3.0167
4219434 | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | TF55HACW-P-1T-*-SDE** | [6 empty] | 51100 | 22.5 | 4.4 | 47100 | 4.2583 | 45400 | 17.1 | 3.8 | 35400 | 3.7833
4219435 | NORDIC | WBAHP | Water-to-Air and Brine-to-Air | TF65HACW-P-1T-*-SDE** | [6 empty] | 62500 | 20.9 | 4.3 | 58400 | 5.2083 | 57400 | 16.6 | 3.6 | 43800 | 4.7833
4219443 | NORDIC | WBAHP-CB | Water-to-Air and Brine-to-Air | RS45HACW-P-1T-* | AH-45-P-1-***** | [5 empty] | 38500 | 21.3 | 4.3 | 35700 | 3.2083 | 35100 | 16.3 | 3.6 | 27200 | 2.925
4219444 | NORDIC | WBAHP-CB | Water-to-Air and Brine-to-Air | RS55HACW-P-1T-* | AH-55-P-1-***** | [5 empty] | 50200 | 22.5 | 4.5 | 47200 | 4.1833 | 45400 | 17 | 3.8 | 35600 | 3.7833
4219445 | NORDIC | WBAHP-CB | Water-to-Air and Brine-to-Air | RS65HACW-P-1T-* | AH-65-P-1-***** | [5 empty] | 62600 | 21.5 | 4.5 | 58700 | 5.2167 | 57600 | 16.8 | 3.7 | 44000 | 4.8
4230301 | NORDIC | WBWHP | Water-to-Water and Brine-to-Water | W-25-HACW-P-1T-** | [6 empty] | 23200 | 21 | 3.8 | 22600 | 1.9333 | 21000 | 14.5 | 3.1 | 17300 | 1.75
4230302 | NORDIC | WBWHP | Water-to-Water and Brine-to-Water | W-45-HACW-P-1T-** | [6 empty] | 34000 | 20.4 | 3.9 | 32700 | 2.8333 | 30500 | 14.6 | 3.1 | 24400 | 2.5417
4230303 | NORDIC | WBWHP | Water-to-Water and Brine-to-Water | W-75-HACW-P-1T-** | [6 empty] | 62400 | 20.1 | 3.9 | 64500 | 5.2 | 55900 | 14.9 | 3.1 | 49000 | 4.6583
4230458 | NORDIC | WBWHP | Water-to-Water and Brine-to-Water | W55-HACW-P-1T-** | [6 empty] | 44700 | 20.5 | 3.7 | 45000 | 3.725 | 40300 | 15 | 3.1 | 34600 | 3.3583
4230459 | NORDIC | WBWHP | Water-to-Water and Brine-to-Water | W65-HACW-P-1T-** | [6 empty] | 54800 | 20.2 | 3.7 | 54900 | 4.5667 | 49600 | 15 | 3.1 | 42600 | 4.1333
4230749 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WCCW4024*E*01* | [6 empty] | 29600 | 22.8 | 4.2 | 23500 | 2.4667
4230751 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WCCW4024*F*01* | [6 empty] | 0 | 22.8 | 4.2 | 23500 | 0
4230753 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WCCW4024*J*01* | [6 empty] | 29600 | 22.8 | 4.2 | 23500 | 2.4667
4230922 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WCCW4024*K*01* | [6 empty] | 29600 | 22.8 | 4.2 | 23500 | 2.4667
214838955 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CL042-1HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214838956 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CL042-1VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214838957 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CL042-3HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214838958 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CL042-3VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214838959 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CL042-4HZC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
214838960 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CL042-4VTC****T/A*A | [6 empty] | 44500 | 21.5 | 4.6 | 36800 | 3.7083
205347302 | BOSCH-GEO | WBWHP | Water-to-Water and Brine-to-Water | TW025-1***-****CB | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
205349297 | CARRIER | WBWHP | Water-to-Water and Brine-to-Water | GW024W**D/G***1**2 | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
205349298 | BRYANT | WBWHP | Water-to-Water and Brine-to-Water | GW024W**D/G***1**2 | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
205349299 | HEIL | WBWHP | Water-to-Water and Brine-to-Water | HW024W**D/G***1**2 | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
205349300 | ARCOAIRE | WBWHP | Water-to-Water and Brine-to-Water | HW024W**D/G***1**2 | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
205349301 | KEEPRITE | WBWHP | Water-to-Water and Brine-to-Water | HW024W**D/G***1**2 | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
205349302 | TEMPSTAR | WBWHP | Water-to-Water and Brine-to-Water | HW024W**D/G***1**2 | [6 empty] | 25400 | 22.1 | 3.7 | 23800 | 2.1167 | 23400 | 16.9 | 3.05 | 18700 | 1.95
9100357 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH036**0*1 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
9100358 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH036**0*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
9100359 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH036**2*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
9100361 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH036**3*1 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
9100362 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH036**3*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
9100364 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH036**4*1 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
9100365 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH036**4*4 | [6 empty] | 37700 | 23 | 4.3 | 33000 | 3.1417 | 34500 | 17.3 | 3.6 | 26000 | 2.875
9100367 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH042**0*1 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
9100368 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH042**0*4 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
9100370 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH042**3*1 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
9100371 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH042**3*4 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
9100373 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH042**4*1 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
9100374 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH042**4*4 | [6 empty] | 45800 | 23.5 | 4.3 | 37000 | 3.8167 | 42300 | 18.5 | 3.7 | 29900 | 3.525
9100377 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH048**0*1 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
9100378 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH048**0*4 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
9100380 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH048**3*1 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
9100381 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH048**3*4 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
9100383 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH048**4*1 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
9100384 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YGSV/YGSH048**4*4 | [6 empty] | 52000 | 23.4 | 4.2 | 45900 | 4.3333 | 49500 | 18.1 | 3.6 | 36900 | 4.125
217897421 | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)036A*V | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
217897422 | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)036A*V | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
217897425 | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)042A*V | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
217897426 | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)042A*V | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
217897427 | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)048A | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
217897428 | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)048A | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
217897429 | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)048A*V | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
217897430 | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)048A*V | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
217897447 | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)015A | [6 empty] | 16700 | 23.5 | 4.3 | 13800 | 1.3917
217897448 | COMFORT-AIRE | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)015A | [6 empty] | 16700 | 23.5 | 4.3 | 13800 | 1.3917
217897449 | CENTURY | WBAHP | Water-to-Air and Brine-to-Air | MR(L/R/B/P/T/K/F)015A*V | [6 empty] | 16900 | 26.2 | 4.5 | 13800 | 1.4083 | 15200 | 17.3 | 3.6 | 10700 | 1.2667
214776161 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK009 | [6 empty] | 9500 | 23.6 | 4.13 | 8600 | 0.79167
214776167 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0091-5 | [6 empty] | 9700 | 27 | 4.44 | 8400 | 0.80833
202146983 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS030*2***1 | [6 empty] | 30900 | 24.6 | 4.7 | 26300 | 2.575 | 29000 | 18.8 | 3.8 | 21700 | 2.4167
202146984 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS030 | [6 empty] | 31800 | 23.4 | 4.5 | 27900 | 2.65 | 29700 | 17.7 | 3.6 | 22900 | 2.475
202146985 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS030*2 | [6 empty] | 31800 | 23.4 | 4.5 | 27900 | 2.65 | 29700 | 17.7 | 3.6 | 22900 | 2.475
202146986 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS030*3 | [6 empty] | 31800 | 23.4 | 4.5 | 27900 | 2.65 | 29700 | 17.7 | 3.6 | 22900 | 2.475
202146987 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS030*4 | [6 empty] | 31800 | 23.4 | 4.5 | 27900 | 2.65 | 29700 | 17.7 | 3.6 | 22900 | 2.475
202146988 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS030*A | [6 empty] | 31800 | 23.4 | 4.5 | 27900 | 2.65 | 29700 | 17.7 | 3.6 | 22900 | 2.475
202146989 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS030*****1 | [6 empty] | 30900 | 24.6 | 4.7 | 26300 | 2.575 | 29000 | 18.8 | 3.8 | 21700 | 2.4167
202146990 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS030*2***1 | [6 empty] | 30900 | 24.6 | 4.7 | 26300 | 2.575 | 29000 | 18.8 | 3.8 | 21700 | 2.4167
202146991 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS036 | [6 empty] | 39500 | 24.1 | 4.4 | 34800 | 3.2917 | 36600 | 17.9 | 3.7 | 28300 | 3.05
202146992 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS036*2 | [6 empty] | 39500 | 24.1 | 4.4 | 34800 | 3.2917 | 36600 | 17.9 | 3.7 | 28300 | 3.05
202146993 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS036*3 | [6 empty] | 39500 | 24.1 | 4.4 | 34800 | 3.2917 | 36600 | 17.9 | 3.7 | 28300 | 3.05
202146994 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS036*4 | [6 empty] | 39500 | 24.1 | 4.4 | 34800 | 3.2917 | 36600 | 17.9 | 3.7 | 28300 | 3.05
202146995 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS036*A | [6 empty] | 39500 | 24.1 | 4.4 | 34800 | 3.2917 | 36600 | 17.9 | 3.7 | 28300 | 3.05
202146996 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS036*****1 | [6 empty] | 39500 | 24.7 | 4.6 | 33600 | 3.2917 | 37200 | 18.8 | 3.9 | 27500 | 3.1
202146997 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS036*2***1 | [6 empty] | 39500 | 24.7 | 4.6 | 33600 | 3.2917 | 37200 | 18.8 | 3.9 | 27500 | 3.1
202146998 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS036*3***1 | [6 empty] | 39500 | 24.7 | 4.6 | 33600 | 3.2917 | 37200 | 18.8 | 3.9 | 27500 | 3.1
202146999 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS036*A***1 | [6 empty] | 39500 | 24.7 | 4.6 | 33600 | 3.2917 | 37200 | 18.8 | 3.9 | 27500 | 3.1
202147000 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS036 | [6 empty] | 39500 | 24.1 | 4.4 | 34800 | 3.2917 | 36600 | 17.9 | 3.7 | 28300 | 3.05
202147001 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS036*2 | [6 empty] | 39500 | 24.1 | 4.4 | 34800 | 3.2917 | 36600 | 17.9 | 3.7 | 28300 | 3.05
202147002 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS036*3 | [6 empty] | 39500 | 24.1 | 4.4 | 34800 | 3.2917 | 36600 | 17.9 | 3.7 | 28300 | 3.05
202147003 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS036*4 | [6 empty] | 39500 | 24.1 | 4.4 | 34800 | 3.2917 | 36600 | 17.9 | 3.7 | 28300 | 3.05
202147004 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS036*A | [6 empty] | 39500 | 24.1 | 4.4 | 34800 | 3.2917 | 36600 | 17.9 | 3.7 | 28300 | 3.05
202147005 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS036*****1 | [6 empty] | 39500 | 24.7 | 4.6 | 33600 | 3.2917 | 37200 | 18.8 | 3.9 | 27500 | 3.1
202147006 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS036*2***1 | [6 empty] | 39500 | 24.7 | 4.6 | 33600 | 3.2917 | 37200 | 18.8 | 3.9 | 27500 | 3.1
202147007 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS036*3***1 | [6 empty] | 39500 | 24.7 | 4.6 | 33600 | 3.2917 | 37200 | 18.8 | 3.9 | 27500 | 3.1
202147008 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS036*A***1 | [6 empty] | 39500 | 24.7 | 4.6 | 33600 | 3.2917 | 37200 | 18.8 | 3.9 | 27500 | 3.1
202147009 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS036 | [6 empty] | 39500 | 24.1 | 4.4 | 34800 | 3.2917 | 36600 | 17.9 | 3.7 | 28300 | 3.05
214823486 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)048BD1**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
216621309 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)009*R0**6 | [6 empty] | 12000 | 23.1 | 4.1 | 10000 | 1
216621310 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)012*R0**6 | [6 empty] | 14000 | 26 | 4.3 | 12400 | 1.1667 | 13000 | 18 | 3.6 | 9500 | 1.0833
216621311 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)015*R0**1 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
216621312 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)018*R0**1 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
216621313 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*S0**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
216621314 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*S0**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
216621315 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*S0**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
216621316 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042*S0**1 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
216621317 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048*S0**1 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
216621323 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)018*D0**1 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
216621324 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)018*D0**4 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
216621325 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D0**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621326 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D2**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621327 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D3**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621328 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D4**1 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621329 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D0**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621330 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D2**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621331 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D3**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621332 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024*D4**4 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
216621333 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*D0**1 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216621334 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*D3**1 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216621335 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*D0**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216621336 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030*D3**4 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
216621337 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D0**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
216621338 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036*D3**1 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
217754425 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024F1*B*T |  | 24400 | 17.91 | 5.79 | 28000 | 2.0333
217754428 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024F1*B*C |  | 24400 | 17.91 | 5.79 | 28000 | 2.0333
217754431 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030F1*B*T |  | 29200 | 18.78 | 5.91 | 34500 | 2.4333
217754434 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030F1*B*C |  | 29200 | 18.78 | 5.91 | 34500 | 2.4333
217754437 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV036F1*B*T |  | 39000 | 18.4 | 5.34 | 44100 | 3.25
217754440 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV036F1*B*C |  | 39000 | 18.4 | 5.34 | 44100 | 3.25
217754443 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042F1*B*T |  | 42140 | 17.99 | 5.32 | 46648 | 3.5117
217754446 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042F1*B*C |  | 42140 | 17.99 | 5.32 | 46648 | 3.5117
217754449 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048F1*B*T |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
9009366 | FHP | WBAHP | Water-to-Air and Brine-to-Air | ES025-2CF/HZ/VT*-*****A | [6 empty] | 29000 | 23.2 | 4.5 | 23400 | 2.4167 | 27500 | 17.7 | 3.6 | 18600 | 2.2917
9009369 | FHP | WBAHP | Water-to-Air and Brine-to-Air | ES035-1CF/HZ/VT*-*****A | [6 empty] | 42000 | 21.25 | 4.2 | 36000 | 3.5 | 38000 | 15.7 | 3.6 | 28000 | 3.1667
9009382 | FHP | WBAHP | Water-to-Air and Brine-to-Air | ES035-3CF/HZ/VT*-*****A | [6 empty] | 42000 | 21.25 | 4.2 | 36000 | 3.5 | 38000 | 15.7 | 3.6 | 28000 | 3.1667
9009391 | FHP | WBAHP | Water-to-Air and Brine-to-Air | ES035-4CF/HZ/VT*-*****A | [6 empty] | 42000 | 21.25 | 4.2 | 36000 | 3.5 | 38000 | 15.7 | 3.6 | 28000 | 3.1667
9009394 | FHP | WBAHP | Water-to-Air and Brine-to-Air | ES049-1CF/HZ/VT*-*****A | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
9009404 | FHP | WBAHP | Water-to-Air and Brine-to-Air | ES049-3CF/HZ/VT*-*****A | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
9009406 | FHP | WBAHP | Water-to-Air and Brine-to-Air | ES049-4CF/HZ/VT*-*****A | [6 empty] | 54000 | 19 | 4.2 | 48000 | 4.5 | 49000 | 15.5 | 3.6 | 38000 | 4.0833
9011292 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH018**0*1 | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
9032337 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | HRCC09*-2 | [6 empty] | 11500 | 23.9 | 4.1 | 8800 | 0.95833
9032648 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | HRCX18*-6 | [6 empty] | 20000 | 22.5 | 4.1 | 16000 | 1.6667 | 18000 | 17.1 | 3.6 | 13000 | 1.5
9033424 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | HRCX09*-6 | [6 empty] | 11500 | 26.5 | 4.5 | 8800 | 0.95833 | 10000 | 19 | 3.6 | 6800 | 0.83333
9033758 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | HRCX24*-6 | [6 empty] | 26000 | 26.5 | 4.4 | 22000 | 2.1667 | 24000 | 19 | 3.6 | 17000 | 2
9033759 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | HRCX12*-6 | [6 empty] | 13000 | 25 | 4.1 | 10500 | 1.0833 | 11800 | 18 | 3.6 | 8000 | 0.98333
9035993 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT024******B |  | 25600 | 17 | 5.5 | 30000 | 2.1333 | [5 empty] | 26800 | 19.8 | 4 | 18100 | 2.2333
9035994 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT024******B |  | 25600 | 17 | 5.5 | 30000 | 2.1333 | [5 empty] | 26800 | 19.8 | 4 | 18100 | 2.2333
9035995 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT024******B |  | 25600 | 17 | 5.5 | 30000 | 2.1333 | [5 empty] | 26800 | 19.8 | 4 | 18100 | 2.2333
9035996 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT024*2****B |  | 25600 | 17 | 5.5 | 30000 | 2.1333 | [5 empty] | 26800 | 19.8 | 4 | 18100 | 2.2333
9035997 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT024*2****B |  | 25600 | 17 | 5.5 | 30000 | 2.1333 | [5 empty] | 26800 | 19.8 | 4 | 18100 | 2.2333
9035998 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT024*2****B |  | 25600 | 17 | 5.5 | 30000 | 2.1333 | [5 empty] | 26800 | 19.8 | 4 | 18100 | 2.2333
9035999 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT024*3****B |  | 25600 | 17 | 5.5 | 30000 | 2.1333 | [5 empty] | 26800 | 19.8 | 4 | 18100 | 2.2333
9036000 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT024*3****B |  | 25600 | 17 | 5.5 | 30000 | 2.1333 | [5 empty] | 26800 | 19.8 | 4 | 18100 | 2.2333
9036001 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT024*3****B |  | 25600 | 17 | 5.5 | 30000 | 2.1333 | [5 empty] | 26800 | 19.8 | 4 | 18100 | 2.2333
9036002 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT024*A****B |  | 25600 | 17 | 5.5 | 30000 | 2.1333 | [5 empty] | 26800 | 19.8 | 4 | 18100 | 2.2333
9036003 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT024*A****B |  | 25600 | 17 | 5.5 | 30000 | 2.1333 | [5 empty] | 26800 | 19.8 | 4 | 18100 | 2.2333
9036004 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT024*A****B |  | 25600 | 17 | 5.5 | 30000 | 2.1333 | [5 empty] | 26800 | 19.8 | 4 | 18100 | 2.2333
9036975 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT036******B |  | 36500 | 17 | 5.3 | 43300 | 3.0417 | [5 empty] | 38200 | 19.9 | 4.1 | 27600 | 3.1833
9036998 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT036******B |  | 36500 | 17 | 5.3 | 43300 | 3.0417 | [5 empty] | 38200 | 19.9 | 4.1 | 27600 | 3.1833
9037017 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT036******B |  | 36500 | 17 | 5.3 | 43300 | 3.0417 | [5 empty] | 38200 | 19.9 | 4.1 | 27600 | 3.1833
9037062 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT036*2****B |  | 36500 | 17 | 5.3 | 43300 | 3.0417 | [5 empty] | 38200 | 19.9 | 4.1 | 27600 | 3.1833
9037081 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT036*2****B |  | 36500 | 17 | 5.3 | 43300 | 3.0417 | [5 empty] | 38200 | 19.9 | 4.1 | 27600 | 3.1833
9037097 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT036*2****B |  | 36500 | 17 | 5.3 | 43300 | 3.0417 | [5 empty] | 38200 | 19.9 | 4.1 | 27600 | 3.1833
9037137 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT036*3****B |  | 36500 | 17 | 5.3 | 43300 | 3.0417 | [5 empty] | 38200 | 19.9 | 4.1 | 27600 | 3.1833
9037158 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT036*3****B |  | 36500 | 17 | 5.3 | 43300 | 3.0417 | [5 empty] | 38200 | 19.9 | 4.1 | 27600 | 3.1833
9037175 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT036*3****B |  | 36500 | 17 | 5.3 | 43300 | 3.0417 | [5 empty] | 38200 | 19.9 | 4.1 | 27600 | 3.1833
9037215 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZT036*A****B |  | 36500 | 17 | 5.3 | 43300 | 3.0417 | [5 empty] | 38200 | 19.9 | 4.1 | 27600 | 3.1833
9037240 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZT036*A****B |  | 36500 | 17 | 5.3 | 43300 | 3.0417 | [5 empty] | 38200 | 19.9 | 4.1 | 27600 | 3.1833
9037275 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZT036*A****B |  | 36500 | 17 | 5.3 | 43300 | 3.0417 | [5 empty] | 38200 | 19.9 | 4.1 | 27600 | 3.1833
208136396 | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | 166D066A*1 | [6 empty] | 57000 | 20.1 | 3.7 | 70000 | 4.75 | 54000 | 16.1 | 3.2 | 56500 | 4.5
208136397 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | HE066*1******D | [6 empty] | 57000 | 20.1 | 3.7 | 70000 | 4.75 | 54000 | 16.1 | 3.2 | 56500 | 4.5
208429479 | YORK BY JOHNSON CONTROLS | WBWHP | Water-to-Water and Brine-to-Water | YAWE066**1*****D | [6 empty] | 57000 | 20.1 | 3.7 | 70000 | 4.75 | 54000 | 16.1 | 3.2 | 56500 | 4.5
208450079 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | HRCX18*-6 | [6 empty] | 20000 | 22.5 | 4.1 | 16000 | 1.6667 | 18000 | 17.1 | 3.6 | 13000 | 1.5
208450080 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | HRCX09*-6 | [6 empty] | 11500 | 26.5 | 4.5 | 8800 | 0.95833 | 10000 | 19 | 3.6 | 6800 | 0.83333
208450081 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | HRCX24*-6 | [6 empty] | 26000 | 26.5 | 4.4 | 22000 | 2.1667 | 24000 | 19 | 3.6 | 17000 | 2
208450082 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | HRCX12*-6 | [6 empty] | 13000 | 25 | 4.1 | 10500 | 1.0833 | 11800 | 18 | 3.6 | 8000 | 0.98333
208450083 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | HRCX30*-6 | [6 empty] | 30000 | 23.5 | 4.1 | 25000 | 2.5 | 28000 | 18 | 3.6 | 20000 | 2.3333
208450084 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | HRCX36*-6 | [6 empty] | 35500 | 21.6 | 4.1 | 31500 | 2.9583 | 34100 | 17.1 | 3.6 | 25000 | 2.8417
215400209 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV042F3*B*C |  | 42140 | 17.99 | 5.32 | 46648 | 3.5117
215400212 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048E1*B*T |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
215400213 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048F3*B*T |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
215400216 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048E1*B*C |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
215400217 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048F3*B*C |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
215400220 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060E1*B*T |  | 64000 | 17.4 | 5.3 | 78000 | 5.3333
215400221 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060F3*B*T |  | 64000 | 17.23 | 5.25 | 78000 | 5.3333
215400222 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060E1*B*C |  | 64000 | 17.4 | 5.3 | 78000 | 5.3333
215400223 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060F3*B*C |  | 64000 | 17.23 | 5.25 | 78000 | 5.3333
215402546 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV007E1*B*T |  | 7100 | 17.99 | 5.49 | 8100 | 0.59167
215402548 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV009E1*B*T |  | 9200 | 17.49 | 4.98 | 11000 | 0.76667
215402550 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024E1*B*T |  | 24400 | 18.37 | 5.79 | 28000 | 2.0333
215402551 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024F3*B*T |  | 24400 | 17.91 | 5.79 | 28000 | 2.0333
215402554 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024E1*B*C |  | 24400 | 18.37 | 5.79 | 28000 | 2.0333
215402555 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV024F3*B*C |  | 24400 | 17.91 | 5.79 | 28000 | 2.0333
215402558 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030E1*B*T |  | 29200 | 19.17 | 5.67 | 34500 | 2.4333
215402559 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030F3*B*T |  | 29200 | 18.78 | 5.91 | 34500 | 2.4333
215402562 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030E1*B*C |  | 29200 | 19.17 | 5.67 | 34500 | 2.4333
215402563 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV030F3*B*C |  | 29200 | 18.78 | 5.91 | 34500 | 2.4333
215402566 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV036E1*B*T |  | 39000 | 19.02 | 5.35 | 44100 | 3.25
215402567 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV036F3*B*T |  | 39000 | 18.4 | 5.34 | 44100 | 3.25
9910450 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS018*****1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
9910451 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS018*****1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
9910452 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS018*A***1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
9910453 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS018*A***1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
9910454 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS018*A***1B |  | 19900 | 17.3 | 5.4 | 22600 | 1.6583 | [5 empty] | 20800 | 20.5 | 3.8 | 14200 | 1.7333
9910548 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS024*****1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910549 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS024*****1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910550 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS024*****1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910551 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS024*2***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910552 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS024*2***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910553 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS024*2***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910554 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS024*3***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910555 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS024*3***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910556 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS024*3***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910557 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS024*A***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910558 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS024*A***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910559 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS024*A***1B |  | 25000 | 17.9 | 5.6 | 29300 | 2.0833 | [5 empty] | 26100 | 21.5 | 3.9 | 18600 | 2.175
9910584 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS030*****1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910585 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS030*****1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910586 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS030*****1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910587 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS030*2***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910588 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS030*2***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910589 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS030*2***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910590 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS030*3***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910591 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS030*3***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910592 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS030*3***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910593 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS030*A***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910594 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS030*A***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
9910595 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS030*A***1B |  | 29500 | 17.5 | 5.7 | 33000 | 2.4583 | [5 empty] | 30700 | 20.7 | 4 | 21500 | 2.5583
215852874 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV036E1*C/S*C |  | 38100 | 18.45 | 5.18 | 41100 | 3.175
215852875 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV036F3*C/S*C |  | 38100 | 18.08 | 5.08 | 41100 | 3.175
215852878 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV042E1*C/S*C |  | 43500 | 17.3 | 5.06 | 50000 | 3.625
215852879 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV042F3*C/S*C |  | 43500 | 16.95 | 4.96 | 50000 | 3.625
215852882 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV048E1*C/S*C |  | 50800 | 17.62 | 5.52 | 58500 | 4.2333
215852883 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV048F3*C/S*C |  | 50800 | 17.27 | 5.41 | 58500 | 4.2333
215852884 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV060E1*C/S*C |  | 60500 | 17.3 | 5.5 | 74700 | 5.0417
215852885 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV060F3*C/S*C |  | 60500 | 16.95 | 5.39 | 74700 | 5.0417
217212057 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP024-4HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
217212059 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP024-4HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
217212060 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP024-4VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
217212061 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP024-4VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
217212062 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP036-1VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
217212064 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP036-1VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
217212065 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP036-2VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
217212066 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP036-2VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
217212067 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP036-3VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
217212068 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP036-3VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
217212070 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP036-4VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
217212071 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP036-4VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
217212072 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP048-1VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
217212073 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP048-1VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
217212074 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP048-3VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
217212076 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP048-3VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
217212077 | FHP | WBAHP | Water-to-Air and Brine-to-Air | CP048-4VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
202667081 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | BP042-1VT*******B | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202679205 | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSC-*****B | SM036-1AH*-*****B | [5 empty] | 40900 | 22.2 | 4.5 | 35200 | 3.4083 | 37900 | 17.15 | 3.8 | 27400 | 3.1583
202679208 | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSC-*****B | SM036-1AH*-*****B | [5 empty] | 40900 | 22.2 | 4.5 | 35200 | 3.4083 | 37900 | 17.15 | 3.8 | 27400 | 3.1583
202729320 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB048V******1**1 | [6 empty] | 51100 | 24 | 4.3 | 40500 | 4.2583 | 46800 | 17.75 | 3.7 | 33400 | 3.9
202729321 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB048V******1**1 | [6 empty] | 51100 | 24 | 4.3 | 40500 | 4.2583 | 46800 | 17.75 | 3.7 | 33400 | 3.9
202729322 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB048V******1**1 | [6 empty] | 51100 | 24 | 4.3 | 40500 | 4.2583 | 46800 | 17.75 | 3.7 | 33400 | 3.9
202729323 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB048V******1**1 | [6 empty] | 51100 | 24 | 4.3 | 40500 | 4.2583 | 46800 | 17.75 | 3.7 | 33400 | 3.9
202729324 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB048V******1**1 | [6 empty] | 51100 | 24 | 4.3 | 40500 | 4.2583 | 46800 | 17.75 | 3.7 | 33400 | 3.9
202729325 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB048V******1**1 | [6 empty] | 51100 | 24 | 4.3 | 40500 | 4.2583 | 46800 | 17.75 | 3.7 | 33400 | 3.9
202729332 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202729333 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202729334 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202729335 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202729336 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202729337 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB018V******1**2 | [6 empty] | 21300 | 25.3 | 4.4 | 17700 | 1.775 | 20500 | 18.5 | 3.7 | 14800 | 1.7083
202732300 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP042-1VT*******B | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732301 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732302 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732303 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732304 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732305 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732306 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732307 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732308 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB042V******1**1 | [6 empty] | 44100 | 25.6 | 4.65 | 35000 | 3.675 | 40600 | 19.4 | 3.7 | 26800 | 3.3833
202732913 | BOSCH-GEO | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSN-*****B | SM036-1AH*-*****B | [5 empty] | 40900 | 22.2 | 4.5 | 35200 | 3.4083 | 37900 | 16.95 | 3.8 | 27400 | 3.1583
202732914 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | BP018-1HZ*******C | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732915 | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | SM036-1CSN-*****B | SM036-1AH*-*****B | [5 empty] | 40900 | 22.2 | 4.5 | 35200 | 3.4083 | 37900 | 16.95 | 3.8 | 27400 | 3.1583
202732916 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP018-1HZ*******C | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732917 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732918 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732919 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732920 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732921 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732922 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732923 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732924 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB018H******1**2 | [6 empty] | 21300 | 24.7 | 4.4 | 17700 | 1.775 | 20500 | 17.9 | 3.65 | 14800 | 1.7083
202732931 | 5 SERIES | WBWHP | Water-to-Water and Brine-to-Water | NEW040*1* | [6 empty] | 33000 | 20.1 | 4 | 40000 | 2.75 | 30600 | 16.1 | 3.3 | 34000 | 2.55
202732932 | 5 SERIES | WBWHP | Water-to-Water and Brine-to-Water | NEW050*1* | [6 empty] | 47000 | 20.1 | 3.9 | 54900 | 3.9167 | 44500 | 16.1 | 3.3 | 45000 | 3.7083
202732934 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC036H3 | [6 empty] | 46200 | 23.29 | 4.12 | 38800 | 3.85
202732935 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC036H4 | [6 empty] | 46200 | 23.29 | 4.12 | 38800 | 3.85
202732936 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC036HW | [6 empty] | 46200 | 23.29 | 4.12 | 38800 | 3.85
202732937 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC048H3 | [6 empty] | 59700 | 25.72 | 4.56 | 50000 | 4.975 | 55100 | 19.28 | 3.77 | 39000 | 4.5917
202732938 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC048H4 | [6 empty] | 59700 | 25.72 | 4.56 | 50000 | 4.975 | 55100 | 19.28 | 3.77 | 39000 | 4.5917
202732939 | TRANE | WBAHP | Water-to-Air and Brine-to-Air | GWSC048HW | [6 empty] | 59700 | 25.72 | 4.56 | 50000 | 4.975 | 55100 | 19.28 | 3.77 | 39000 | 4.5917
207348828 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW050*3 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
207348829 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW050*4 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
207348830 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW050*5 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
207348831 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW060*0 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
207348832 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW060*3 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
207348833 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW060*4 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
207348834 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW060*5 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
207337462 | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | 105G060**1 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
207337463 | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | 165G060**1 | [6 empty] | 62500 | 20.6 | 3.8 | 63200 | 5.2083 | 58000 | 16.1 | 3.1 | 50100 | 4.8333
207337466 | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | 166D040**1 | [6 empty] | 33000 | 20.1 | 4 | 40000 | 2.75 | 30600 | 16.1 | 3.3 | 34000 | 2.55
207337467 | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | 166D050**1 | [6 empty] | 47000 | 20.1 | 3.9 | 54900 | 3.9167 | 44500 | 16.1 | 3.3 | 45000 | 3.7083
207337468 | GEOSTAR | WBWHP | Water-to-Water and Brine-to-Water | 166D066**1 | [6 empty] | 57000 | 20.1 | 3.7 | 70000 | 4.75 | 54000 | 16.1 | 3.2 | 56500 | 4.5
207337469 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103H026**1 | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207337470 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103H026**1 | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207337471 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 163H026**1 | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207337472 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 163H026**1 | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207337473 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 104H026**1 | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207337474 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 104H026**1 | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207337475 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 164H026**1 | SAH026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207337476 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 164H026**1 | SRAA026* | [5 empty] | 25800 | 23 | 4.6 | 23300 | 2.15 | 23400 | 17.5 | 3.7 | 18400 | 1.95
207337477 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J038**1 | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207337478 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103J038**1 | SRAA036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207337479 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 163J038**1 | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207337480 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 163J038**1 | SRAA036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207337481 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 104J038**1 | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207337482 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 104J038**1 | SRAA036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207337483 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 164J038**1 | SAH036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207337484 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 164J038**1 | SRAA036* | 34400 | 16.3 | 5.2 | 41600 | 2.8667 | 38200 | 24.2 | 4.7 | 35100 | 3.1833 | 36000 | 19 | 4 | 27900 | 3
207337485 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J049**1 | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337486 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103J049**1 | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337487 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 163J049**1 | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337488 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 163J049**1 | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337489 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 104H049**1 | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337490 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 104H049**1 | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337491 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 164H049**1 | SAH048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337492 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 164H049**1 | SRAA048* | [5 empty] | 51000 | 24.2 | 4.6 | 47100 | 4.25 | 46300 | 18 | 3.9 | 37700 | 3.8583
207337493 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J064**1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207337494 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103J064**1 | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207337495 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 163J064**1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207337496 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 163J064**1 | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207337497 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 104H064**1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207337498 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 104H064**1 | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207337499 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 164H064**1 | SAH060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207337500 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 164H064**1 | SRAA060* | [5 empty] | 63200 | 22.5 | 4.4 | 56000 | 5.2667 | 57400 | 17 | 3.7 | 45200 | 4.7833
207337509 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103H022**1 | SAH022* | [5 empty] | 20400 | 26.5 | 4.8 | 18100 | 1.7 | 18700 | 19.1 | 3.8 | 14000 | 1.5583
207337510 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103H022**1 | SRAA026* | [5 empty] | 20400 | 26.5 | 4.8 | 18100 | 1.7 | 18700 | 19.1 | 3.8 | 14000 | 1.5583
207337511 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103H030**1 | SAH030* | [5 empty] | 26900 | 25.6 | 4.8 | 24900 | 2.2417 | 24600 | 18.9 | 3.9 | 19800 | 2.05
207337512 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103H030**1 | SRAA026* | [5 empty] | 26900 | 25.6 | 4.8 | 24900 | 2.2417 | 24600 | 18.9 | 3.9 | 19800 | 2.05
207337513 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J036**1 | SAH036* | 29100 | 17.4 | 5.8 | 35600 | 2.425 | 33200 | 27.4 | 4.9 | 29600 | 2.7667 | 30600 | 20.4 | 4 | 23100 | 2.55
207337514 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103J036**1 | SRAA036* | 29100 | 17.4 | 5.8 | 35600 | 2.425 | 33200 | 27.4 | 4.9 | 29600 | 2.7667 | 30600 | 20.4 | 4 | 23100 | 2.55
207337515 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103J042**1 | SAH042* | [5 empty] | 41300 | 25.6 | 4.8 | 36000 | 3.4417 | 37800 | 19.5 | 3.9 | 27400 | 3.15
207337516 | GEOSTAR | WBAHP-C | Water-to-Air and Brine-to-Air | 103J042**1 | SRAA048* | [5 empty] | 41300 | 25.6 | 4.8 | 36000 | 3.4417 | 37800 | 19.5 | 3.9 | 27400 | 3.15
207337517 | GEOSTAR | WBAHP-CB | Water-to-Air and Brine-to-Air | 103H048**1 | SAH048* | [5 empty] | 46900 | 25.5 | 4.7 | 41900 | 3.9083 | 42500 | 18.7 | 4 | 33400 | 3.5417
6501947 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH038**3*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
6501948 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH038**4*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
6501949 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH038**4*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
6501950 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**0*0 | [6 empty] | 42300 | 23.3 | 4.3 | 36000 | 3.525
215224027 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF007-1VT/HZC-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
215224028 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF007-1VT/HZN-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
215224029 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF009-1VT/HZC-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
215224030 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF009-1VT/HZN-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
215224031 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF012-1VT/HZC-*****A | [6 empty] | 13500 | 23 | 4.3 | 12000 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224032 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF012-1VT/HZN-*****A | [6 empty] | 13500 | 23 | 4.3 | 11700 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224033 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF015-1VT/HZC-*****A | [6 empty] | 16700 | 24 | 4.3 | 14000 | 1.3917 | 15700 | 18 | 3.6 | 11000 | 1.3083
215224034 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF015-1VT/HZN-*****A | [6 empty] | 16700 | 23.5 | 4.3 | 14000 | 1.3917 | 15500 | 17.5 | 3.6 | 11000 | 1.2917
215224035 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF018-1VT/HZC-*****A | [6 empty] | 21300 | 24 | 4.4 | 18000 | 1.775 | 20000 | 18 | 3.6 | 14200 | 1.6667
215224036 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF018-1VT/HZN-*****A | [6 empty] | 21000 | 24 | 4.4 | 17700 | 1.75 | 19700 | 18 | 3.6 | 14200 | 1.6417
215224037 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF007-2VT/HZC-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
215224038 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF007-2VT/HZN-*****A | [6 empty] | 8000 | 24 | 4.7 | 7000 | 0.66667 | 7400 | 18.5 | 3.6 | 5000 | 0.61667
215224039 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF009-2VT/HZC-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
215224040 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF009-2VT/HZN-*****A | [6 empty] | 9800 | 23 | 4.5 | 8400 | 0.81667 | 9200 | 17.5 | 3.6 | 6500 | 0.76667
215224041 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF012-2VT/HZC-*****A | [6 empty] | 13500 | 23 | 4.3 | 12000 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224042 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF012-2VT/HZN-*****A | [6 empty] | 13500 | 23 | 4.3 | 11700 | 1.125 | 12500 | 17.5 | 3.6 | 9000 | 1.0417
215224043 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF015-2VT/HZC-*****A | [6 empty] | 16700 | 24 | 4.3 | 14000 | 1.3917 | 15700 | 18 | 3.6 | 11000 | 1.3083
215224044 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF015-2VT/HZN-*****A | [6 empty] | 16700 | 23.5 | 4.3 | 14000 | 1.3917 | 15500 | 17.5 | 3.6 | 11000 | 1.2917
215224045 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF018-2VT/HZC-*****A | [6 empty] | 21300 | 24 | 4.4 | 18000 | 1.775 | 20000 | 18 | 3.6 | 14200 | 1.6667
215224046 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF018-2VT/HZN-*****A | [6 empty] | 21000 | 24 | 4.4 | 17700 | 1.75 | 19700 | 18 | 3.6 | 14200 | 1.6417
215224047 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-2VT/HZC-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224048 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-4VT/HZC-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224049 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-2VT/HZN-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224050 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF024-4VT/HZN-*****A | [6 empty] | 26000 | 23 | 4 | 23000 | 2.1667 | 25000 | 17 | 3.7 | 18000 | 2.0833
215224051 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-2VT/HZC-*****A | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
215224052 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CF030-4VT/HZC-*****A | [6 empty] | 32000 | 22 | 4 | 28000 | 2.6667 | 31000 | 16.5 | 3.7 | 23400 | 2.5833
216743648 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP048-1VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216743649 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP048-3VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216743650 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP048-4VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216743651 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RP048-1VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216743652 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP048-1VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216743653 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP048-3VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216743654 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP048-4VT/HZN-*****A | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216743655 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RP060-1VT/HZC-*****A |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216743656 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP060-1VT/HZC-*****A |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216743657 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP060-3VT/HZC-*****A |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216743658 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP060-4VT/HZC-*****A |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216743659 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RP060-1VT/HZN-*****A |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216743660 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP060-1VT/HZN-*****A |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216743661 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP060-3VT/HZN-*****A |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216743662 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP060-4VT/HZN-*****A |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216759673 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W7SZ030BV1**F | W7BM030BN1**2 | 31600 | 15.1 | 5.1 | 48300 | 2.6333 | 35800 | 27.8 | 4.5 | 40700 | 2.9833 | 32400 | 18.1 | 3.4 | 31700 | 2.7
216759674 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W7SZ042BV1**F | W7BM042BN1**2 | 38100 | 15.6 | 4.9 | 55900 | 3.175 | 44400 | 28.8 | 4.4 | 51300 | 3.7 | 41600 | 19.3 | 3.8 | 41400 | 3.4667
216759675 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W7SZ048BV1**F | W7BM048BN1**2 | [5 empty] | 56600 | 21 | 3.8 | 69600 | 4.7167 | 48000 | 14 | 3.2 | 53500 | 4
216759816 | WaterFurnace | WBAHP-C | Water-to-Air and Brine-to-Air | W5SS024BD1 | A5D(C/U)024B* | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
205312006 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | ZBV/ZBH042**0*1 | [6 empty] | 47000 | 22 | 4.5 | 41400 | 3.9167
214067547 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**3*0 | [6 empty] | 28100 | 24 | 4.3 | 23900 | 2.3417 | 26000 | 19.2 | 3.7 | 18900 | 2.1667
214067548 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**3*1 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
214067549 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**3*4 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
214067550 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**4*0 | [6 empty] | 28100 | 24 | 4.3 | 23900 | 2.3417 | 26000 | 19.2 | 3.7 | 18900 | 2.1667
214067551 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**4*1 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
214067552 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH024**4*4 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
214067553 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**3*1 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
214067554 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**3*4 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
214067555 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**4*1 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
214067556 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH026**4*4 |  | 24900 | 16.8 | 5.5 | 30100 | 2.075 | 27700 | 24 | 4.8 | 23900 | 2.3083 | 26400 | 19.6 | 4 | 19500 | 2.2
214067557 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**3*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
214067558 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**3*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
214067559 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**3*4 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
214067560 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**4*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
214067561 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**4*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
214067562 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH030**4*4 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
214067563 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**3*0 | [6 empty] | 35100 | 24.4 | 4.5 | 29200 | 2.925 | 32900 | 19.2 | 3.8 | 24400 | 2.7417
214067564 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**3*1 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
214067565 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**3*4 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
214067566 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**4*0 | [6 empty] | 35100 | 24.4 | 4.5 | 29200 | 2.925 | 32900 | 19.2 | 3.8 | 24400 | 2.7417
214067567 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**4*1 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
214067568 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH036**4*4 |  | 32300 | 18.8 | 5.7 | 36500 | 2.6917 | 36800 | 28.8 | 4.9 | 29200 | 3.0667 | 33700 | 22 | 4.2 | 24400 | 2.8083
214067569 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH038**3*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
214067570 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH038**3*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
214067571 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH038**4*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
214067572 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH038**4*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
214067573 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**3*0 | [6 empty] | 42300 | 23.3 | 4.3 | 36000 | 3.525
214067574 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**3*1 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
214067575 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**3*4 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
214067576 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**4*0 | [6 empty] | 42300 | 23.3 | 4.3 | 36000 | 3.525
214067577 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**4*1 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
214067578 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**4*4 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
214067579 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH042**5*0 | [6 empty] | 42300 | 23.3 | 4.3 | 36000 | 3.525
214067580 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH048**4*0 | [6 empty] | 48900 | 22.3 | 4.2 | 44700 | 4.075
214067581 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH048**4*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
214067582 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH048**4*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
214067583 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH048**5*0 | [6 empty] | 48900 | 22.3 | 4.2 | 44700 | 4.075
214067584 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH049**3*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
214067585 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH049**3*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
214067586 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH049**4*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
214067587 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH049**4*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
214067595 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH064**3*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
214067596 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH064**3*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
214067597 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH064**4*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
214067598 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | GBV/GBH064**4*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
215837810 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH024F3*C/S*T |  | 24500 | 17.65 | 5.68 | 28000 | 2.0417
215837811 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH024J1*C/S*T |  | 24500 | 17.65 | 5.68 | 28000 | 2.0417
215837813 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH024K3*C/S*T |  | 24500 | 17.65 | 5.68 | 28000 | 2.0417
215837818 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH024F3*C/S*C |  | 24500 | 17.65 | 5.68 | 28000 | 2.0417
215837820 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH024J1*C/S*C |  | 24500 | 17.65 | 5.68 | 28000 | 2.0417
215837821 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSH024K3*C/S*C |  | 24500 | 17.65 | 5.68 | 28000 | 2.0417
7519567 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS030*3 | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519568 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS030*3 | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519569 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS030*3 | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519570 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS030*4 | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519571 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS030*4 | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519572 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS030*4 | [6 empty] | 31000 | 23.4 | 4.7 | 28700 | 2.5833 | 30100 | 18.5 | 3.9 | 22300 | 2.5083
7519573 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*A | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519574 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*A | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519575 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*A | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519576 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*2 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519577 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*2 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519578 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*2 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519579 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*3 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519580 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*3 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519581 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*3 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519582 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*4 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519583 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*4 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519584 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*4 | [6 empty] | 40500 | 23.5 | 4.6 | 37600 | 3.375 | 37800 | 18 | 3.9 | 30200 | 3.15
7519727 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS024*****1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519748 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS024*****1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519756 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS024*****1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519769 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS024*A***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519770 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS024*A***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519771 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS024*A***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519772 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS024*2***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519773 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS024*2***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519774 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS024*2***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519775 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS024*3***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519776 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS024*3***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7519777 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS024*3***1 |  | 25900 | 18.4 | 5.9 | 29800 | 2.1583 | 29400 | 29.5 | 5.1 | 24000 | 2.45 | 27000 | 21.6 | 4.2 | 19300 | 2.25
7520238 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS030*****1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520239 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS030*****1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520240 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS030*****1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520241 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS030*2***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520242 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS030*2***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520243 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS030*2***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520244 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS030*3***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520245 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS030*3***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520246 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS030*A***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520247 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS030*A***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520248 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS030*A***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520249 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS030*3***1 |  | 30100 | 17.6 | 5.9 | 36200 | 2.5083 | 34000 | 27.5 | 5.1 | 29200 | 2.8333 | 31400 | 20.4 | 4.2 | 23200 | 2.6167
7520250 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*****1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520251 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*****1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520252 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*****1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520253 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*2***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520254 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*2***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520255 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*2***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520256 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*3***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520257 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*3***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520258 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*3***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520259 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS036*A***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520260 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS036*A***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7520261 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TVS036*A***1 | [6 empty] | 41600 | 25.5 | 4.8 | 36900 | 3.4667 | 38800 | 19.2 | 3.9 | 29600 | 3.2333
7523956 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GVS018*****1 |  | 20700 | 18.8 | 6.2 | 23700 | 1.725 | 23200 | 30.5 | 5.3 | 19600 | 1.9333 | 21700 | 22.2 | 4 | 15400 | 1.8083
7523957 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HVS018*****1 |  | 20700 | 18.8 | 6.2 | 23700 | 1.725 | 23200 | 30.5 | 5.3 | 19600 | 1.9333 | 21700 | 22.2 | 4 | 15400 | 1.8083
203254607 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GB042H******1**1 |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203254608 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB042H******1**1 |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203254609 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB042H******1**1 |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203254610 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB042H******1**1 |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203254611 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB042H******1**1 |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203254612 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB042H******1**1 |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203254614 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB042H******1**1 |  | 38400 | 17.15 | 5.8 | 42400 | 3.2 | 44100 | 27.2 | 5 | 35000 | 3.675 | 40600 | 19.5 | 4 | 26800 | 3.3833
203254620 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GC024V/C**N***1*X1 | [6 empty] | 29000 | 23.7 | 4.6 | 23500 | 2.4167 | 26600 | 18.2 | 3.7 | 18000 | 2.2167
203254624 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GC024H**C***1*X1 |  | 25500 | 16.6 | 5.6 | 29200 | 2.125 | 29000 | 25.75 | 5 | 23500 | 2.4167 | 26600 | 19.9 | 3.7 | 18000 | 2.2167
203254626 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GC024H**N***1*X1 | [6 empty] | 29000 | 24.1 | 5 | 23500 | 2.4167 | 26600 | 18.3 | 3.7 | 18000 | 2.2167
203254744 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GC024V/C**N***1**1 | [6 empty] | 29000 | 23.7 | 4.6 | 23500 | 2.4167 | 26600 | 18.2 | 3.7 | 18000 | 2.2167
203254748 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GC024H**C***1**1 |  | 25500 | 16.6 | 5.6 | 29200 | 2.125 | 29000 | 25.75 | 5 | 23500 | 2.4167 | 26600 | 19.9 | 3.7 | 18000 | 2.2167
203254752 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GC024H**N***1**1 | [6 empty] | 29000 | 24.1 | 5 | 23500 | 2.4167 | 26600 | 18.3 | 3.7 | 18000 | 2.2167
203260718 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | SM024-1VT/CFC******A | [6 empty] | 29000 | 24.7 | 4.3 | 23500 | 2.4167 | 26600 | 18.9 | 3.7 | 18000 | 2.2167
203260866 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GC024V/C**C***1**1 + UI | [6 empty] | 29000 | 24.7 | 4.3 | 23500 | 2.4167 | 26600 | 18.9 | 3.7 | 18000 | 2.2167
203260867 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GC024V/C**C***1*X1 + UI | [6 empty] | 29000 | 24.7 | 4.3 | 23500 | 2.4167 | 26600 | 18.9 | 3.7 | 18000 | 2.2167
215268677 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)015*R0**4 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
215268678 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)015*R2**4 | [6 empty] | 17000 | 28 | 4.9 | 16000 | 1.4167 | 15500 | 19.5 | 4.1 | 12000 | 1.2917
215268679 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)018*R2**1 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
215268680 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)018*R0**4 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
215268681 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)018*R2**4 | [6 empty] | 20600 | 25 | 4.6 | 18500 | 1.7167 | 18500 | 18.3 | 4 | 14500 | 1.5417
215268682 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*S2**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
215268683 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*S3**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
215268684 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*S4**1 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
215268685 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*S0**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
215268686 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*S2**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
215268687 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*S3**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
215268688 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)024*S4**4 |  | 24500 | 17.5 | 5.4 | 30000 | 2.0417 | 28000 | 28 | 4.7 | 24000 | 2.3333 | 26000 | 20.6 | 4 | 19000 | 2.1667
215268689 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)030*S3**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
215268690 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)030*S0**4 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
215268691 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)030*S3**4 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
215268692 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S3**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268693 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S0**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268694 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S3**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268695 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S0**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268696 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S3**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268697 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*S3**1 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
215268698 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*S0**2 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
215268699 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*S3**2 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
215268700 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*S0**4 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
215268701 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*S3**4 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
215268702 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*S3**1 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
215268703 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*S0**2 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
215268704 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*S3**2 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
215268705 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*S0**4 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
215268706 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*S3**4 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
215268713 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)030*S2**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
215268714 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)030*S4**1 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
215268715 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)030*S2**4 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
215268716 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)030*S4**4 |  | 30000 | 17.5 | 5.3 | 36000 | 2.5 | 33000 | 28 | 4.5 | 30000 | 2.75 | 30000 | 21 | 3.9 | 23000 | 2.5
215268717 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S4**1 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268718 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S2**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268719 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S4**2 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268720 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S2**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268721 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)036*S4**4 |  | 36000 | 18.8 | 5.8 | 39000 | 3 | 39000 | 29 | 5 | 32000 | 3.25 | 37500 | 21.5 | 4.2 | 26000 | 3.125
215268722 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*S4**1 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
215268723 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*S2**2 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
215268724 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*S4**2 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
215268725 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)042*S4**4 |  | 42000 | 18.4 | 6 | 49000 | 3.5 | 45000 | 27 | 5.2 | 39000 | 3.75 | 42000 | 21.2 | 4.2 | 32000 | 3.5
215268726 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*S4**1 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
215268727 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*S2**2 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
215268728 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*S4**2 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
215268729 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | V5A(V/H)048*S4**4 | [6 empty] | 53500 | 26 | 4.8 | 48000 | 4.4583 | 51000 | 19 | 4.2 | 38500 | 4.25
217351675 | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP048-1CSC-*****A | BIVA-48RCB-M20X | [5 empty] | 53000 | 23.1 | 4.8 | 47000 | 4.4167 | 50600 | 18.1 | 4.2 | 38000 | 4.2167
217351676 | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP048-1CSN-*****A | BIVA-48RCB-M20X | [5 empty] | 53000 | 23.9 | 4.9 | 45200 | 4.4167 | 50200 | 18.7 | 4.1 | 35400 | 4.1833
217351677 | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP060-1CSC-*****A | BIVA-60RCB-M20X | [5 empty] | 64200 | 21.8 | 4.6 | 62200 | 5.35 | 60800 | 17.7 | 4 | 50000 | 5.0667
217351678 | BOSCH | WBAHP-CB | Water-to-Air and Brine-to-Air | RP060-1CSN-*****A | BIVA-60RCB-M20X | [5 empty] | 64000 | 22.2 | 4.8 | 62400 | 5.3333 | 60600 | 17.5 | 4.2 | 51200 | 5.05
217351679 | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP024-1CSC-*****A | BMAC2430BBTA | [5 empty] | 27400 | 23.2 | 5 | 23800 | 2.2833 | 25400 | 18.1 | 4.1 | 18800 | 2.1167
217351680 | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP024-1CSN-*****A | BMAC2430BBTA | [5 empty] | 27600 | 24.3 | 5.1 | 23800 | 2.3 | 26000 | 18.3 | 4.3 | 18800 | 2.1667
217351681 | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP036-1CSC-*****A | BMAC3036BBTA | [5 empty] | 39600 | 21.5 | 4.8 | 37800 | 3.3 | 37000 | 16.4 | 4.1 | 29800 | 3.0833
217351682 | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP036-1CSN-*****A | BMAC3036BBTA | [5 empty] | 40200 | 22.2 | 5 | 38800 | 3.35 | 38200 | 17.2 | 4.2 | 30800 | 3.1833
217351683 | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP048-1CSC-*****A | BMAC4248CBTA | [5 empty] | 52000 | 21.6 | 4.5 | 45400 | 4.3333 | 50200 | 17.5 | 3.9 | 37200 | 4.1833
217351684 | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP048-1CSN-*****A | BMAC4248CBTA | [5 empty] | 53400 | 22.5 | 4.7 | 46600 | 4.45 | 51600 | 17.8 | 4.1 | 38200 | 4.3
217351685 | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP060-1CSC-*****A | BMAC4860CBTA | [5 empty] | 63400 | 20.5 | 4.4 | 58600 | 5.2833 | 60200 | 16.9 | 3.8 | 47600 | 5.0167
217351686 | BOSCH | WBAHP-C | Water-to-Air and Brine-to-Air | RP060-1CSN-*****A | BMAC4860CBTA | [5 empty] | 63200 | 21.1 | 4.5 | 59400 | 5.2667 | 60000 | 16.8 | 4 | 49800 | 5
217351687 | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | TW025-1***-*****C |  | 22600 | 15.8 | 5.09 | 31400 | 1.8833 | 24400 | 24.4 | 4.25 | 25600 | 2.0333 | 23600 | 18.7 | 3.26 | 19800 | 1.9667
217351688 | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | TW035-1***-*****C | [6 empty] | 34600 | 21.5 | 3.96 | 37200 | 2.8833 | 33000 | 16.5 | 3.16 | 28800 | 2.75
217351689 | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | TW049-1***-*****C | [6 empty] | 44000 | 21.5 | 4.25 | 50000 | 3.6667 | 42500 | 16.9 | 3.46 | 39500 | 3.5417
217351690 | BOSCH | WBWHP | Water-to-Water and Brine-to-Water | TW061-1***-*****C | [6 empty] | 55000 | 20.7 | 3.96 | 59500 | 4.5833 | 51500 | 15.9 | 3.16 | 47500 | 4.2917
217351692 | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | CP024-1CSC-*****A | BIVA-24RCB-M20X | [5 empty] | 27400 | 24.3 | 4.8 | 23200 | 2.2833 | 26000 | 18.3 | 4 | 18400 | 2.1667
217351693 | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | CP024-1CSN-*****A | BIVA-24RCB-M20X | [5 empty] | 27200 | 25.2 | 4.9 | 23200 | 2.2667 | 26000 | 18.8 | 4.1 | 18200 | 2.1667
217351694 | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | CP036-1CSC-*****A | BIVA-36RCB-M20X | [5 empty] | 40200 | 23.4 | 4.7 | 36400 | 3.35 | 38200 | 17.6 | 4 | 29200 | 3.1833
217351695 | FHP | WBAHP-CB | Water-to-Air and Brine-to-Air | CP036-1CSN-*****A | BIVA-36RCB-M20X | [5 empty] | 41400 | 24.1 | 4.8 | 37000 | 3.45 | 39200 | 18.6 | 4.1 | 29800 | 3.2667
214776192 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0187-5 | [6 empty] | 19400 | 21.6 | 4.47 | 19000 | 1.6167
214776193 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0242-5 | [6 empty] | 26300 | 24 | 4.56 | 24700 | 2.1917 | 25200 | 18.5 | 3.82 | 20100 | 2.1
214776194 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0247-5 | [6 empty] | 26300 | 24 | 4.56 | 24700 | 2.1917 | 25200 | 18.5 | 3.82 | 20100 | 2.1
214776195 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0362-5 | [6 empty] | 41700 | 22.6 | 4.26 | 37200 | 3.475
214776196 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GETK0367-5 | [6 empty] | 41700 | 22.6 | 4.26 | 37200 | 3.475
214796343 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W5A(V/H)024BD1**2 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
214796344 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W5A(V/H)030BD1**2 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
214796345 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W5A(V/H)036BD1**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
214796346 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W5A(V/H)042BD1**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
214796347 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W5A(V/H)048BD1**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
214796667 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | W5A(V/H)018BD1**2 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
214810491 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)018BD1**2 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
214810492 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)024BD1**2 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
214810493 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)030BD1**2 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
214810494 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)036BD1**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
214810495 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)042BD1**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
214810496 | GEOSTAR | WBAHP | Water-to-Air and Brine-to-Air | G5A(V/H)048BD1**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
214823444 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)018BD1**2 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
214823445 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)024BD1**2 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
214823446 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)030BD1**2 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
214823447 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)036BD1**2 |  | 36400 | 17.9 | 6.1 | 43300 | 3.0333 | 41800 | 28.4 | 5.3 | 36000 | 3.4833 | 38500 | 20.8 | 4.5 | 29600 | 3.2083
214823448 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)042BD1**2 | [6 empty] | 46200 | 26.6 | 5.2 | 41700 | 3.85 | 41700 | 19.2 | 4.4 | 33700 | 3.475
214823449 | GeoSmart Energy | WBAHP | Water-to-Air and Brine-to-Air | S5A(V/H)048BD1**2 | [6 empty] | 53100 | 24.9 | 5.1 | 49300 | 4.425 | 50500 | 18.9 | 4.4 | 40100 | 4.2083
214823480 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)018BD1**2 | [6 empty] | 20800 | 27 | 5 | 18900 | 1.7333 | 18700 | 19.8 | 4.2 | 14700 | 1.5583
214823481 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)024BD1**2 |  | 23800 | 16.1 | 5.7 | 28000 | 1.9833 | 26400 | 25.2 | 4.9 | 23300 | 2.2 | 25000 | 19.2 | 4.1 | 19400 | 2.0833
214823482 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | Y5A(V/H)030BD1**2 |  | 30800 | 17.3 | 5.6 | 38600 | 2.5667 | 35200 | 27.5 | 4.8 | 31100 | 2.9333 | 32300 | 20.3 | 4 | 24600 | 2.6917
215742630 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 31630/U | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
215742631 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 31640/U | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
215742632 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 21630/U | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
215742633 | Ecoforest | WBWHP | Water-to-Water and Brine-to-Water | 21640/U | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
215743134 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK006 | [6 empty] | 9300 | 21.7 | 4.5 | 8100 | 0.775
215743135 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK009 | [6 empty] | 9500 | 23 | 4.5 | 8400 | 0.79167
215743136 | TRANE | WBAHP-O | Water-to-Air and Brine-to-Air | GECK012 | [6 empty] | 13300 | 23.2 | 4.3 | 11600 | 1.1083
216739881 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV036E1*C/S*C |  | 35600 | 16.5 | 4.9 | 39100 | 2.9667
216739882 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV036F3*C/S*C |  | 35600 | 16.2 | 4.8 | 39100 | 2.9667
216739883 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV036J1*C/S*C |  | 35600 | 16.2 | 4.8 | 39100 | 2.9667
216739884 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV036K3*C/S*C |  | 35600 | 16 | 4.8 | 39100 | 2.9667
216739895 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV048E1*C/S*C |  | 49200 | 16.9 | 5 | 58000 | 4.1
216739896 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV048F3*C/S*C |  | 49200 | 16.5 | 4.9 | 58000 | 4.1
216739897 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSDV048K3*C/S*C |  | 49200 | 16.5 | 4.9 | 58000 | 4.1
216739910 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH024E1*C/S*C |  | 24400 | 16.9 | 5.1 | 29500 | 2.0333
216739911 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH024F3*C/S*C |  | 24400 | 16.6 | 5 | 29500 | 2.0333
216739912 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH024J1*C/S*C |  | 24400 | 16.6 | 5 | 29500 | 2.0333
216739913 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSNH024K3*C/S*C |  | 24400 | 16.4 | 5 | 29500 | 2.0333
215832292 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6012D* | [6 empty] | 13000 | 23 | 4.6 | 11000 | 1.0833 | 12000 | 17.9 | 3.8 | 8500 | 1
215832293 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6018D* | [6 empty] | 20400 | 25 | 4.3 | 16000 | 1.7 | 19000 | 18 | 3.6 | 12000 | 1.5833
215832294 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6024D* | [6 empty] | 28000 | 25 | 4.3 | 21400 | 2.3333 | 26000 | 18.4 | 3.6 | 17500 | 2.1667
215832295 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6030D* | [6 empty] | 32400 | 24 | 4.2 | 26000 | 2.7 | 30000 | 18.4 | 3.6 | 21000 | 2.5
215832296 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6036D* | [6 empty] | 39000 | 23.2 | 4.1 | 35000 | 3.25 | 36400 | 18 | 3.6 | 28000 | 3.0333
215832297 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6042D* | [6 empty] | 45500 | 23.3 | 4.3 | 38000 | 3.7917 | 43500 | 18.5 | 3.8 | 31000 | 3.625
215832298 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6048D* | [6 empty] | 52500 | 23.6 | 4.2 | 45500 | 4.375 | 49500 | 18 | 3.6 | 36000 | 4.125
215832299 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSH6060D* | [6 empty] | 64000 | 23.5 | 4.3 | 51000 | 5.3333 | 60000 | 18.1 | 3.6 | 41000 | 5
202921913 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP036-3HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921914 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | EP036-4HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921915 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | BP036-1HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921952 | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-1HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921953 | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-3HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921954 | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-4HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921956 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP036-1HZ*-*****B | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202921957 | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-1VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202921958 | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-3VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202921959 | FHP | WBAHP | Water-to-Air and Brine-to-Air | EP036-4VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202921960 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP036-1VT*-*****B |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922686 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH036***3/CA | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922689 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH036***5/EA | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922692 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSH036***6/FA | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922695 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922697 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922700 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922703 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922706 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922708 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922711 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922714 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB036H******1**1 | [6 empty] | 40200 | 24.3 | 4.7 | 34400 | 3.35 | 37500 | 18.7 | 3.9 | 26000 | 3.125
202922716 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSV036***3/CA |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922719 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSV036***5/EA |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922722 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50PSV036***6/FA |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922725 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922728 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922731 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922734 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922737 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922740 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922742 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
202922745 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HB036V******1**1 |  | 36000 | 17.1 | 5.5 | 41000 | 3 | 40200 | 25.9 | 4.9 | 34400 | 3.35 | 37500 | 19.7 | 3.9 | 26000 | 3.125
7418803 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH042**4*0 | [6 empty] | 42300 | 23.3 | 4.3 | 36000 | 3.525
7418887 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH042**4*1 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
7418965 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH042**4*4 |  | 39000 | 18.6 | 5.8 | 45600 | 3.25 | 43900 | 28.1 | 4.9 | 36100 | 3.6583 | 40700 | 21.7 | 4 | 28900 | 3.3917
7419110 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH042**5*0 | [6 empty] | 42300 | 23.3 | 4.3 | 36000 | 3.525
7419218 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**0*0 | [6 empty] | 48900 | 22.3 | 4.2 | 44700 | 4.075
7419321 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**0*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
7419403 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**0*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
7419473 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**3*0 | [6 empty] | 48900 | 22.3 | 4.2 | 44700 | 4.075
7419527 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**3*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
7419618 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**3*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
7419681 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**4*0 | [6 empty] | 48900 | 22.3 | 4.2 | 44700 | 4.075
7419733 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**4*1 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
7419797 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**4*4 | [6 empty] | 50300 | 25.9 | 4.7 | 44700 | 4.1917 | 45900 | 18.8 | 4 | 36400 | 3.825
7420917 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKSV/YKSH048**5*0 | [6 empty] | 48900 | 22.3 | 4.2 | 44700 | 4.075
7421327 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH049**0*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
7421397 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH049**0*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
7421438 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH049**3*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
7421969 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH049**4*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
7421970 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH049**4*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
7422020 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH064**0*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
7422043 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH064**0*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
7422058 | YORK BY JOHNSON CONTROLS | WBAHP | Water-to-Air and Brine-to-Air | YKTV/YKTH064**3*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
215399772 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV015A1*C/S*T |  | 15500 | 17.51 | 5.09 | 17000 | 1.2917
215399776 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV015A1*C/S*C |  | 15500 | 17.51 | 5.09 | 17000 | 1.2917
215399790 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSMV024J1*C/S*T |  | 24700 | 17.58 | 5.12 | 28600 | 2.0583
217465611 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO22KB2CWRB | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
217465612 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO22KB2CWBB | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
217465613 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO22KB2BWRB | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
217465614 | GeoSmart Energy | WBWHP | Water-to-Water and Brine-to-Water | NETZERO22KB2BWBB | [6 empty] | 46387 | 18.71 | 3.4 | 85577 | 3.8656 | 42788 | 15.07 | 2.92 | 69881 | 3.5657
217531660 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)006A | [6 empty] | 7600 | 30 | 4.8 | 6200 | 0.63333 | 6700 | 20 | 3.6 | 4600 | 0.55833
217531661 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)009A | [6 empty] | 10500 | 28 | 4.6 | 9000 | 0.875 | 9700 | 19 | 3.7 | 7000 | 0.80833
217531662 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)012A | [6 empty] | 13700 | 28.3 | 4.3 | 12200 | 1.1417 | 12400 | 19.5 | 3.6 | 9200 | 1.0333
217531663 | ClimateMaster | WBAHP | Water-to-Air and Brine-to-Air | SE(L/R/B/P/D/N/T/K)018A | [6 empty] | 22000 | 28.1 | 4.9 | 18900 | 1.8333 | 20100 | 19.5 | 4.1 | 14500 | 1.675
215223342 | WaterFurnace | WBAHP-O | Water-to-Air and Brine-to-Air | V5C(C/W/S)015**0**1 | [6 empty] | 15500 | 22 | 4.1 | 14000 | 1.2917
216743615 | BOSCH | WBAHP-O | Water-to-Air and Brine-to-Air | CA009-1***-******E | [6 empty] | 9500 | 22.35 | 4.45 | 8150 | 0.79167
216743616 | BOSCH | WBAHP-O | Water-to-Air and Brine-to-Air | CA009-2***-******E | [6 empty] | 9500 | 22.35 | 4.45 | 8150 | 0.79167
216743617 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RP024-1VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216743618 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-1VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216743619 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-2VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216743620 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-3VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216743621 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-4VTC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216743622 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RP024-1VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216743623 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-1VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216743624 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-2VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216743625 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-3VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216743626 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-4VTN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216743627 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RP024-1HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216743628 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-1HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216743629 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-2HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216743630 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-3HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216743631 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-4HZC-*****A |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216743632 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RP024-1HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216743633 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-1HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216743634 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-2HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216743635 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-3HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216743636 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP024-4HZN-*****A |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216743637 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RP036-1VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216743638 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP036-1VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216743639 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP036-2VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216743640 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP036-3VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216743641 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP036-4VT/HZC-*****A | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216743642 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RP036-1VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216743643 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP036-1VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216743644 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP036-2VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216743645 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP036-3VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216743646 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | CP036-4VT/HZN-*****A | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216743647 | BOSCH-GEO | WBAHP | Water-to-Air and Brine-to-Air | RP048-1VT/HZC-*****A | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
5295966 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH018**2*4 | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
5295968 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH018**0*4 | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
5295969 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH018**0*1 | [6 empty] | 20600 | 26 | 4.6 | 18700 | 1.7167 | 18500 | 18.3 | 3.8 | 14500 | 1.5417
5295980 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH024**0*0 | [6 empty] | 28100 | 24 | 4.3 | 23900 | 2.3417 | 26000 | 19.2 | 3.7 | 18900 | 2.1667
5295981 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH024**3*0 | [6 empty] | 28100 | 24 | 4.3 | 23900 | 2.3417 | 26000 | 19.2 | 3.7 | 18900 | 2.1667
5295982 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH024**4*0 | [6 empty] | 28100 | 24 | 4.3 | 23900 | 2.3417 | 26000 | 19.2 | 3.7 | 18900 | 2.1667
5295983 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH024**2*0 | [6 empty] | 28100 | 24 | 4.3 | 23900 | 2.3417 | 26000 | 19.2 | 3.7 | 18900 | 2.1667
5295984 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH024**0*1 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
5295985 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH024**3*1 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
5295986 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH024**2*1 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
5295987 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH024**4*1 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
5295988 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH024**4*4 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
5295989 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH024**3*4 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
5295990 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH024**0*4 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
5295991 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH024**2*4 | [6 empty] | 28100 | 27.5 | 4.6 | 24600 | 2.3417 | 26000 | 19.6 | 3.8 | 19000 | 2.1667
5295992 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH030**0*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
5295993 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH030**3*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
5295994 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH030**4*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
5295995 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH030**2*0 |  | 26800 | 17.9 | 5.3 | 32900 | 2.2333 | 30800 | 27.1 | 4.7 | 26000 | 2.5667 | 27900 | 21.1 | 3.7 | 20300 | 2.325
5295996 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH030**0*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
5295997 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | NBV/NBH030**2*1 |  | 27000 | 18.9 | 5.6 | 32900 | 2.25 | 31200 | 29.5 | 4.8 | 26000 | 2.6 | 28100 | 22 | 3.9 | 20500 | 2.3417
207348707 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*0*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348708 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*0*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348709 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*0*5 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348710 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*3*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348711 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*3*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348712 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*3*5 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348713 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*4*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348714 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*4*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348715 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*4*5 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
207348716 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*0*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348717 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*0*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348718 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*0*5 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348719 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*3*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348720 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*3*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348721 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*3*5 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348722 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*4*1 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348723 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*4*4 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348724 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD049*4*5 |  | 49100 | 17.2 | 5.5 | 59000 | 4.0917 | 54100 | 24.5 | 4.6 | 47200 | 4.5083 | 50800 | 19.3 | 4 | 38200 | 4.2333
207348725 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*0*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348726 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*0*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348727 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*0*5 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348728 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*3*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348729 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*3*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348730 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*3*5 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348731 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*4*1 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348732 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*4*4 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348733 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD064*4*5 |  | 62300 | 16.4 | 5.2 | 73900 | 5.1917
207348818 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW018*0 | [6 empty] | 18800 | 22.9 | 3.7 | 18500 | 1.5667 | 17300 | 16.6 | 3.1 | 14700 | 1.4417
207348819 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW025*0 | [6 empty] | 26700 | 21.2 | 3.8 | 27100 | 2.225 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
207348820 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW025*2 | [6 empty] | 26700 | 21.2 | 3.8 | 27100 | 2.225 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
207348821 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW025*4 | [6 empty] | 26700 | 21.2 | 3.8 | 27100 | 2.225 | 24700 | 16.1 | 3.1 | 22000 | 2.0583
207348822 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW040*0 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
207348823 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW040*3 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
207348824 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW040*4 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
207348825 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW040*5 | [6 empty] | 40900 | 23.4 | 3.9 | 39100 | 3.4083 | 37700 | 17.5 | 3.1 | 30500 | 3.1417
207348826 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW050*0 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
207348827 | WaterFurnace | WBWHP | Water-to-Water and Brine-to-Water | NSW050*2 | [6 empty] | 55600 | 21.6 | 3.7 | 54200 | 4.6333 | 51500 | 16.4 | 3.1 | 44200 | 4.2917
215811946 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6009D* | [6 empty] | 11000 | 26 | 4.3 | 8800 | 0.91667 | 9800 | 19 | 3.7 | 6800 | 0.81667
215811947 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6009D* | [6 empty] | 11000 | 26 | 4.3 | 8800 | 0.91667 | 9800 | 19 | 3.7 | 6800 | 0.81667
215811948 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6012D* | [6 empty] | 13500 | 26 | 4.1 | 11000 | 1.125 | 12500 | 19 | 3.6 | 9000 | 1.0417
215811950 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6012D* | [6 empty] | 13500 | 26 | 4.1 | 11000 | 1.125 | 12500 | 19 | 3.6 | 9000 | 1.0417
215811951 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6018D* | [6 empty] | 20000 | 21.1 | 4.1 | 16000 | 1.6667 | 18000 | 17.2 | 3.6 | 13000 | 1.5
215811952 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6018D* | [6 empty] | 20000 | 21.1 | 4.1 | 16000 | 1.6667 | 18000 | 17.2 | 3.6 | 13000 | 1.5
215811953 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6024D* | [6 empty] | 24000 | 23 | 4.1 | 22000 | 2 | 23000 | 18 | 3.6 | 17500 | 1.9167
215811954 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6024D* | [6 empty] | 24000 | 23 | 4.1 | 22000 | 2 | 23000 | 18 | 3.6 | 17500 | 1.9167
215811955 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6030D* | [6 empty] | 30000 | 22.5 | 4.1 | 24000 | 2.5 | 28000 | 17.5 | 3.6 | 19900 | 2.3333
215811957 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6030D* | [6 empty] | 30000 | 22.5 | 4.1 | 24000 | 2.5 | 28000 | 17.5 | 3.6 | 19900 | 2.3333
215811958 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6036D* | [6 empty] | 39000 | 22 | 4.1 | 35000 | 3.25 | 37000 | 18 | 3.6 | 28000 | 3.0833
215811959 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6036D* | [6 empty] | 39000 | 22 | 4.1 | 35000 | 3.25 | 37000 | 18 | 3.6 | 28000 | 3.0833
215811960 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6042D* | [6 empty] | 44000 | 24 | 4.3 | 37000 | 3.6667 | 42000 | 18 | 3.6 | 30000 | 3.5
215811961 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6042D* | [6 empty] | 44000 | 24 | 4.3 | 37000 | 3.6667 | 42000 | 18 | 3.6 | 30000 | 3.5
215811962 | HYDROTECH | WBAHP | Water-to-Air and Brine-to-Air | WSV6048D* | [6 empty] | 55000 | 23 | 4.1 | 38000 | 4.5833
215811964 | AE Air | WBAHP | Water-to-Air and Brine-to-Air | WSV6048D* | [6 empty] | 55000 | 23 | 4.1 | 38000 | 4.5833
215415780 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)024A*VB | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
215415781 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)024A*VC | [6 empty] | 27800 | 24 | 4.5 | 24000 | 2.3167 | 25800 | 18 | 3.7 | 19000 | 2.15
215415784 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)030A*VB | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
215415785 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)030A*VC | [6 empty] | 32800 | 23.5 | 4.3 | 28800 | 2.7333 | 30500 | 17.3 | 3.6 | 23000 | 2.5417
215415788 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)036A*VB | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
215415789 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)036A*VC | [6 empty] | 39200 | 25.2 | 4.2 | 35800 | 3.2667 | 36400 | 17.4 | 3.6 | 27900 | 3.0333
215415792 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)042A*VB | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
215415793 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)042A*VC | [6 empty] | 46000 | 22.9 | 4.3 | 39900 | 3.8333
215415794 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)048A*B | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
215415795 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)048A*C | [6 empty] | 53000 | 21.5 | 4.1 | 48000 | 4.4167
215415796 | Johnson Controls | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)048A*VB | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
215415797 | SKYMARK | WBAHP | Water-to-Air and Brine-to-Air | BR(L/R/B/P/T/K/F)048A*VC | [6 empty] | 53500 | 22.8 | 4.2 | 47700 | 4.4583
217754453 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV048F1*B*C |  | 50600 | 17.57 | 5.74 | 59100 | 4.2167
217754457 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060F1*B*T |  | 64000 | 17.23 | 5.25 | 78000 | 5.3333
217754461 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSSV060F1*B*C |  | 64000 | 17.23 | 5.25 | 78000 | 5.3333
217754473 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH024E1*B*C |  | 24500 | 17.53 | 5.29 | 26100 | 2.0417
217754474 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH024F1*B*C |  | 24500 | 17.18 | 5.19 | 26100 | 2.0417
217754477 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH030E1*B*C |  | 31400 | 17.12 | 5.36 | 34900 | 2.6167
217754478 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH030F1*B*C |  | 31400 | 16.78 | 5.26 | 34900 | 2.6167
217754481 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH036E1*B*C |  | 38000 | 18.43 | 5.36 | 42900 | 3.1667
217754482 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH036F1*B*C |  | 38000 | 18.06 | 5.25 | 42900 | 3.1667
217754485 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH042E1*B*C |  | 44000 | 17.59 | 5.12 | 50300 | 3.6667
217754486 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH042F1*B*C |  | 44000 | 17.24 | 5.02 | 50300 | 3.6667
217754489 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH048E1*B*C |  | 48200 | 17.34 | 5.08 | 56900 | 4.0167
217754490 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH048F1*B*C |  | 48200 | 16.99 | 4.98 | 56900 | 4.0167
217754493 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH060E1*B*C |  | 60000 | 16.8 | 4.9 | 68600 | 5
217754494 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTH060F1*B*C |  | 60000 | 16.46 | 4.8 | 68600 | 5
217754501 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV024E1*B*C |  | 24300 | 17.59 | 5.81 | 28000 | 2.025
217754502 | DAIKIN | WBAHP | Water-to-Air and Brine-to-Air | WSTV024F1*B*C |  | 24300 | 17.24 | 5.7 | 28000 | 2.025
217037791 | YORK BY JOHNSON CONTROLS | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SS024BD1 | Y5BM024BN1**2 | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
217037792 | YORK BY JOHNSON CONTROLS | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SS036BD1 | Y5BM036BN1**2 | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
217037793 | YORK BY JOHNSON CONTROLS | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SS048BD1 | Y5BM048BN1**2 | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
217037794 | YORK BY JOHNSON CONTROLS | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SS060BD1 | Y5BM060BN1**2 | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
217037796 | YORK BY JOHNSON CONTROLS | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SZ024BD1 | Y5BM024BN1**2 | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
217037797 | YORK BY JOHNSON CONTROLS | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SZ036BD1 | Y5BM036BN1**2 | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
217037798 | YORK BY JOHNSON CONTROLS | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SZ048BD1 | Y5BM048BN1**2 | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
217037799 | YORK BY JOHNSON CONTROLS | WBAHP-CB | Water-to-Air and Brine-to-Air | Y5SZ060BD1 | Y5BM060BN1**2 | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
217037801 | YORK BY JOHNSON CONTROLS | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SS024BD1 | A5D(C/U)024B* | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
217037802 | YORK BY JOHNSON CONTROLS | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
217037803 | YORK BY JOHNSON CONTROLS | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SS048BD1 | A5D(C/U)048B* | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
217037804 | YORK BY JOHNSON CONTROLS | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SS060BD1 | A5D(C/U)060B* | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
217037806 | YORK BY JOHNSON CONTROLS | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SZ024BD1 | A5D(C/U)024B* | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
217037807 | YORK BY JOHNSON CONTROLS | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SZ036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
217037808 | YORK BY JOHNSON CONTROLS | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SZ048BD1 | A5D(C/U)048B* | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
217037809 | YORK BY JOHNSON CONTROLS | WBAHP-C | Water-to-Air and Brine-to-Air | Y5SZ060BD1 | A5D(C/U)060B* | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
217037811 | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | S5SS024BD1 | S5BM024BN1**2 | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
217037812 | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | S5SS036BD1 | S5BM036BN1**2 | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
217037813 | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | S5SS048BD1 | S5BM048BN1**2 | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
217037814 | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | S5SS060BD1 | S5BM060BN1**2 | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
217037816 | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | S5SZ024BD1 | S5BM024BN1**2 | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
217037817 | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | S5SZ036BD1 | S5BM036BN1**2 | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
217037818 | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | S5SZ048BD1 | S5BM048BN1**2 | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
217037819 | GeoSmart Energy | WBAHP-CB | Water-to-Air and Brine-to-Air | S5SZ060BD1 | S5BM060BN1**2 | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
217037821 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | S5SS024BD1 | A5D(C/U)024B* | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
217037822 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | S5SS036BD1 | A5D(C/U)036B* | 35300 | 17.1 | 5.6 | 41800 | 2.9417 | 38100 | 25.2 | 5 | 35000 | 3.175 | 37000 | 19.8 | 4.2 | 28400 | 3.0833
217037823 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | S5SS048BD1 | A5D(C/U)048B* | [5 empty] | 50900 | 24.3 | 4.8 | 47300 | 4.2417 | 47100 | 18.2 | 4.2 | 37900 | 3.925
217037824 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | S5SS060BD1 | A5D(C/U)060B* | [5 empty] | 63900 | 23.7 | 4.4 | 55700 | 5.325 | 59900 | 18.2 | 3.9 | 46700 | 4.9917
217037826 | GeoSmart Energy | WBAHP-C | Water-to-Air and Brine-to-Air | S5SZ024BD1 | A5D(C/U)024B* | [5 empty] | 25800 | 23.8 | 4.6 | 22700 | 2.15 | 23800 | 18.4 | 3.9 | 18800 | 1.9833
216802011 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*048***6*(A-H)** | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216802012 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*048***6*(J-R)** | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216802013 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*060***3*(A-H)** |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216802014 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*060***3*(J-R)** |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216802015 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*060***5*(A-H)** |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216802016 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*060***5*(J-R)** |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216802017 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*060***6*(A-H)** |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216802018 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | 50WT*060***6*(J-R)** |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216979809 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979810 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979811 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979812 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979813 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979814 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979815 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979816 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA24H**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 27000 | 24 | 4.8 | 22500 | 2.25 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979817 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216979818 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA36V/H**C******1 | [6 empty] | 40500 | 24 | 5 | 37000 | 3.375 | 39000 | 18.5 | 4 | 28000 | 3.25
216979819 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA36V/H**N******1 | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216979820 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA36V/H**N******1 | [6 empty] | 40000 | 23.5 | 5 | 36500 | 3.3333 | 38500 | 18.3 | 4 | 27500 | 3.2083
216979821 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA48V/H**C******1 | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216979822 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA48V/H**C******1 | [6 empty] | 53500 | 23 | 5 | 48000 | 4.4583 | 51000 | 18 | 4 | 38000 | 4.25
216979823 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA48V/H**N******1 | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216979824 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA48V/H**N******1 | [6 empty] | 53000 | 22.5 | 5 | 47500 | 4.4167 | 50500 | 17.5 | 4 | 37500 | 4.2083
216979825 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA60V/H**C******1 |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216979826 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA60V/H**C******1 |  | 61500 | 16 | 5.6 | 75000 | 5.125 | [5 empty] | 63000 | 18 | 4 | 48000 | 5.25
216979827 | CARRIER | WBAHP | Water-to-Air and Brine-to-Air | GCA60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216979828 | BRYANT | WBAHP | Water-to-Air and Brine-to-Air | GCA60V/H**N******1 |  | 61000 | 16 | 5.6 | 75000 | 5.0833 | [5 empty] | 62500 | 18 | 4 | 47500 | 5.2083
216979837 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979838 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979839 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979840 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979841 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979842 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979843 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979844 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979845 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979846 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979847 | COMFORTMAKER | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979848 | DAY & NIGHT | WBAHP | Water-to-Air and Brine-to-Air | HCR24V**N******1 |  | 24500 | 16.5 | 5.6 | 28000 | 2.0417 | 26500 | 24 | 4.8 | 22500 | 2.2083 | 25000 | 18.5 | 4 | 17500 | 2.0833
216979849 | HEIL | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979850 | ARCOAIRE | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979851 | KEEPRITE | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
216979852 | TEMPSTAR | WBAHP | Water-to-Air and Brine-to-Air | HCR24H**C******1 |  | 25000 | 16.5 | 5.6 | 28500 | 2.0833 | 27000 | 24 | 4.8 | 23000 | 2.25 | 25500 | 18.5 | 4 | 18000 | 2.125
1483426 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP012-1HZ/VT | [6 empty] | 14200 | 22.7 | 4.3 | 12000 | 1.1833 | 12600 | 17.5 | 3.6 | 9300 | 1.05
1483428 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP024-1HZ/VT | [6 empty] | 28400 | 27.35 | 4.5 | 23700 | 2.3667 | 26000 | 19.8 | 3.7 | 18000 | 2.1667
1483429 | BOSCH | WBAHP | Water-to-Air and Brine-to-Air | BP030-1HZ/VT | [6 empty] | 31000 | 27 | 4.95 | 25000 | 2.5833 | 28500 | 19.4 | 3.95 | 20300 | 2.375
3059231 | WaterFurnace | WBAHP-O | Water-to-Air and Brine-to-Air | NCC/NCW/NCS/NCE15*2 | [6 empty] | 16200 | 22 | 4.1 | 14000 | 1.35
3059237 | WaterFurnace | WBAHP-O | Water-to-Air and Brine-to-Air | NCC/NCW/NCS/NCE15*0 | [6 empty] | 16200 | 22 | 4.1 | 14000 | 1.35
3627926 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH015**0*0 | [6 empty] | 16000 | 24 | 4.1 | 15000 | 1.3333
3627927 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | USV/USH015**2*0 | [6 empty] | 16000 | 24 | 4.1 | 15000 | 1.3333
202147710 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS042*3***1 | [6 empty] | 43700 | 25.6 | 4.5 | 37500 | 3.6417 | 40700 | 19.2 | 3.8 | 30200 | 3.3917
202147711 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS042*3***1 | [6 empty] | 43700 | 25.6 | 4.5 | 37500 | 3.6417 | 40700 | 19.2 | 3.8 | 30200 | 3.3917
202147712 | GEOCOMFORT | WBAHP | Water-to-Air and Brine-to-Air | GZS060*3***1 | [6 empty] | 60500 | 22.3 | 4.3 | 58600 | 5.0417 | 57000 | 17.5 | 3.6 | 46200 | 4.75
202147713 | HYDRON MODULE | WBAHP | Water-to-Air and Brine-to-Air | HZS060*3***1 | [6 empty] | 60500 | 22.3 | 4.3 | 58600 | 5.0417 | 57000 | 17.5 | 3.6 | 46200 | 4.75
202147714 | TETCO | WBAHP | Water-to-Air and Brine-to-Air | TZS060*3***1 | [6 empty] | 60500 | 22.3 | 4.3 | 58600 | 5.0417 | 57000 | 17.5 | 3.6 | 46200 | 4.75
202211042 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*0*1 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
202211043 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*0*4 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833
202211044 | WaterFurnace | WBAHP | Water-to-Air and Brine-to-Air | URD038*0*5 |  | 36500 | 17 | 5.5 | 43300 | 3.0417 | 40000 | 24.4 | 4.9 | 35000 | 3.3333 | 38200 | 19.7 | 4.2 | 28500 | 3.1833