Massachusetts Residential IECC Energy Performance Testing Certificate

## House Address:	Permit #:	Date: 	 Permit holder:	Phone:

- Building Envelope Air Leakage (mandatory):

## Blower door test (Mandatory)

Testing company:	Phone:

#### Tester Name (print): ______________________________ Signature: _________________________________ Date: ______________

#### BPI or HERS Rater certification number:     BPI no: _________________         HERS Rater no: ________________

Test Result:

Fan Flow at 50 Pascals = 	CFM50		Total Conditioned Volume = 	ft3

ACH50 = CFM50 x 60 / Volume =   		ACH50 (must be ≤ 3.0 ACH50)

## Visual Inspection (Mandatory)

- Air Barrier and Insulation Installation checklist completed, signed and included with this certificate.

# Heating and Cooling System Duct Leakage

# All portions of the ducts are located entirely within the building thermal envelope. Testing is not required*.

Duct leakage test

Testing company:	Phone:

#### Tester Name (print): ______________________________ Signature: _________________________________ Date: ______________

BPI or HERS Rater certification number:     BPI no: _______________         HERS Rater no: _________________

Total duct leakage test (choose 1):

- Rough-in w/ air handler (must be ≤ 4.0 CFM/100 ft2)

- Post construction (must be ≤ 4.0 CFM/100 ft2)

- Rough-in w/o air handler (must be ≤ 3.0 CFM/100 ft2)

Test Result:

System 1:

Fan Flow at 25 Pascals (CFM25) ________ CFM 	 Conditioned Floor Area (CFA) served by system = _________ft2

CFM25 / CFA x 100 = __________ CFM/100 ft2

System 2 (if present):

Fan Flow at 25 Pascals (CFM25) ________ CFM 	 Conditioned Floor Area (CFA) served by system = _________ft2

CFM25 / CFA x 100 = __________ CFM/100 ft2

*Note: 	When following the Energy Rating Index (ERI) path, a leakage to outdoors test is required per RESNET standards.

# Whole-house Ventilation System Airflow Test

Verifier:

Testing company:	Phone:  ______________________

#### Tester Name (print): ______________________________ Signature: _________________________________ Date: _____________

BPI or HERS Rater certification number:     BPI no: _________________         HERS Rater no: ________________

Infiltration credit portion of equation is optional

Required airflow (Q):

Required inputs:

CFA = 	Conditioned Floor Area = __________ ft2

Nbr = 	Number of bedrooms = ________

Optional inputs:

Q50 =   Blower door test result = ________ CFM50

S = 	Building height factor = _______

WSF = Weather and shielding factor = ________

| Stories above grade plane | 1 | 2 | 3 |
| --- | --- | --- | --- |
| S | 1.00 | 1.32 | 1.55 |

| County | WSF |
| --- | --- |
| Barnstable | 0.60 |
| Berkshire | 0.52 |
| Bristol | 0.54 |
| Dukes | 0.59 |
| Essex | 0.58 |
| Franklin | 0.52 |
| Hampden | 0.49 |
| Hampshire | 0.59 |
| Middlesex | 0.55 |
| Nantucket | 0.61 |
| Norfolk | 0.52 |
| Plymouth | 0.53 |
| Suffolk | 0.66 |
| Worcester | 0.59 |

Required airflow (Q) = ____________ CFM

Tested airflow = _____________ CFM

(must be ≥ required airflow)

- Fan controlled to operate continuously

Fan efficacy:

- In-line fan (max 2.8 CFM/W)

- Bathroom/utility room fan: 10-89 CFM (max 1.4 CFM/W)

- Bathroom/utility room fan: 90+ CFM (max 2.8 CFM/W)

HVI-Rated fan efficacy = _________ CFM/W

# Qualified Performance Testing Providers:

Find qualified performance testers at:

http://nehers.org/find-hers-rater

http://www.resnet.us/directory/search

https://bpi.org/locator-tool/find-a-contractor